{"text_format":"3","workbook":"xls","n_sheets":4,"sheets":["Technical Schedule XLPE Cable","Deviation Schedule","Drwg & Type Tests","Sheet1"],"not_rendered":{"external_links":1,"defined_names":20},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Technical Schedule XLPE Cable","index":0,"n_rows":126,"n_cols":63,"rows_kept":126,"merged":[[0,1,0,7],[1,1,1,7],[2,1,2,7],[3,6,3,7],[4,1,4,7],[5,1,5,7],[8,3,8,4],[9,3,9,4],[18,3,18,4],[69,1,69,4],[72,1,72,2],[73,1,73,2],[78,1,78,2]],"flags":["formulas_cached_only"]}
[null,"TECHNICAL SCHEDULES A & B FOR MV XLPE CABLES "]
[]
[null,"SAP: 171351   CABLE 11kV 1C 630SQ. CU EUX1XCQ"]
[]
[null,"Schedule A:  Purchasers specific requirements"]
[null,"Schedule B: Guarantees and technical particulars of equipment offered"]
[]
[null,1,2,null,3,null,4,5]
[null,"Item ","240-56063792 Rev 3","Description",null,null,"Schedule A","Schedule B"]
[null,1,null,"Item and system description"]
[{"$nulls":4},"CABLE 11kV 1C 630SQ. CU EUX1XCQ"]
[null,1.1,null,null,"SAP No",null,{"v":171351,"d":"0171351"},"xxxxxxxxxx"]
[null,1.2,null,null,"Buyers Guide Drawing",null,"D-DT-8001 ","xxxxxxxxxx"]
[null,"1.3",null,null,"Symmetrical fault level rating","kA","xxxxxxxxxx","xxxxxxxxxx"]
[null,"1.4",null,null,"Nominal system voltage","kV",11,"xxxxxxxxxx"]
[null,"1.5",null,null,"Earth fault level rating","kA","xxxxxxxxxx","xxxxxxxxxx"]
[]
[]
[null,2,null,"Ratings"]
[null,2.1,"3.1.1",null,"Rated voltage (Ur)","kV",11,"____________"]
[null,null,"3.1.2",null,"Conductor Size","mmsq",630,"____________"]
[null,2.3,"3.1.2",null,"Number of cores (1- Core or 3- Cores)",null,1,"____________"]
[null,null,"3.1.4.8",null,"Screening of cables",null,"Individually screened","____________"]
[null,null,"3.1.4.2",null,"Semiconducting core screen",null,"Strippable","____________"]
[null,null,"3.1.4.3",null,"Core identification",null,"Yes","____________"]
[null,null,"3.1.4.4",null,"Bedding under armouring",null,"MDPE","____________"]
[null,null,"3.1.4.8",null,"Armouring",null,"AWA","____________"]
[null,2.5,"3.2.6i)",null,"Rated frequency (fr)","Hz",50,"____________"]
[null,2.7,"3.1.4.8.2 & 3.1.4.8.4",null,"Type of outer sheath ",null,"Black PE type S2","____________"]
[null,null,"3.1.4.8",null,"Does outer sheath sheath comply with the requirements specified in 3.1.4.5, 3.1.4.8.2 and or 3.1.4.8.4",null,"Yes","____________"]
[null,2.8,"3.1.4.6",null,"Is the PVC outer or PE sheath fire retardant?",null,"Yes","____________"]
[null,2.9,"3.1.4.7",null,"Does the cable meet the longitudinal water blocking requirements for conductor and cable?",null,"Yes","____________"]
[null,null,"3.1.4.7",null,"Method used to achieve water blocking requirements",null,"xxxxxxxxxx","____________"]
[null,null,"3.1.4.7",null,"Instruction provided for water blocking removal in conductor when jointing or termination (If applicable) ?",null,"Yes / NA","____________"]
[null,null,"3.2.1b)",null,"Hole for woodern drums for a spindle if not 80mm (minimum). ","mm","80mm (min)","____________"]
[null,"2.10","3.2.1c)",null,"Drum length required as per 3.2.1c?","m",500,"____________"]
[null,2.11,"3.2.2",null,"Is the conductor marking system details supplied with tender?",null,"Yes","____________"]
[null,2.12,"3.2.2",null,"Does the conductor marking comply with the requirements of 3.2.2?",null,"Yes","____________"]
[null,2.14,"3.2.2",null,"What magnification factor is required to read font size for conductor marking characters?","Factor","xxxxxxxxxx","____________"]
[null,2.15,"3.2.3",null,"Is marking of cable identification system details submitted with tender?",null,"Yes","____________"]
[null,2.17,null,null,"Does the cable marking system comply with the requirements of 3.2.3?",null,"Yes","____________"]
[null,2.19,"3.2.3a)",null,"Where is the cable identification system located (in which layer of the cable)?",null,"xxxxxxxxxx","____________"]
[null,"2.20","3.2.3c)",null,"Does the cable identification system comply with the requirements as stated in 3.2.3c)","mm","Yes","____________"]
[null,null,"3.2.4",null,"Does the marking of cable outer sheath comply to 3.2.4?",null,"xxxxxxxxxx","____________"]
[null,"2.21","3.2.5",null,"Does the marking of the drum comply with clause 3.2.5?",null,"Yes","____________"]
[null,"2.22","3.2.6",null,"Does the catalogue/ drawing  have all the required technical information?",null,"Yes","____________"]
[null,"2.23","3.3.1.3",null,"Are copies of type tests reports submitted with tender documentation?",null,"Yes","____________"]
[null,null,"3.3.1",null,"Are all applicable documents submitted i.e type test reports, test schedules, deviation schedule (if any), cable construction drawings, list of all type tested material used in the construction of the cable?",null,"Yes","____________"]
[null,"3.24","3.3.1.2",null,"Cable dimentional data drawing submitted?",null,"Yes","____________"]
[null,"3.25","3.2.6e)",null,"Maximum sustained current rating at 90deg Celcius conductor temperature installed in:","A"]
[{"$nulls":4},"a) Ground?",null,"xxxxxxxxxx","____________"]
[{"$nulls":4},"b) Air?",null,"xxxxxxxxxx","____________"]
[{"$nulls":4},"c) Ducts?",null,"xxxxxxxxxx","____________"]
[null,"3.26","3.2.6e)",null,"Maximum sustained current rating 70deg Celcius conductor temperature installe in:","A"]
[{"$nulls":4},"a) Ground?",null,"xxxxxxxxxx","____________"]
[{"$nulls":4},"b) Air?",null,"xxxxxxxxxx","____________"]
[{"$nulls":4},"c) Ducts?",null,"xxxxxxxxxx","____________"]
[null,"3.27","3.2.6c)",null,"Short circuit rating?","kA","xxxxxxxxxx","____________"]
[null,null,"3.2.6g)",null,"Cable mass?","kg/m","xxxxxxxxxx","____________"]
[null,null,"3.2.6h)",null,"Gross mass per standard drum length?","kg ","xxxxxxxxxx","____________"]
[null,null,"3.2.6i)",null,"Resistance at max conductor temperature?","°C","xxxxxxxxxx","____________"]
[null,null,"3.2.6j)",null,"Reatance per phase?","Ω/m","xxxxxxxxxx","____________"]
[null,null,"3.2.6k)",null,"Capacitance per phase?","nF/m","xxxxxxxxxx","____________"]
[null,null,"3.2.6l)",null,"Zero sequence impedance and capacitance per phase?","Ω/m","xxxxxxxxxx","____________"]
[null,null,"3.2.6m)",null,"Cable termal time constant?","Seconds","xxxxxxxxxx","____________"]
[null,null,"3.2.6 n)",null,"A copy of the relevant SABS mark scheme permit submitted?",null,"xxxxxxxxxx","____________"]
[null,"3.28","3.3",null,"Testing of cable is done in accordance with SANS 1339?",null,"Yes","____________"]
[]
[]
[null,"SIGNATURES"]
[]
[]
[{"$nulls":4},"         "]
[null,"Factory",null,null,"Name (Print)",null,"Sign","Date"]
[]
[]
[{"$nulls":4},"         "]
[]
[null,"Eskom",null,null,"Name (Print)",null,"Sign","Date"]
[]
[]
[]
[]
[]
[{"$nulls":12},"Description","Buyer's Guide Drawing","SAP No","Rated Voltage","Number of cores","Conductor Size","Screening","Semi conducting core screen","Core identification","Bedding under armouring","Armouring","Type of Outer Sheath","Water blocking requirements","Hole spindle diameter","Drum Length","Marking of conductor","Marking of cable","Marking of cable outer sheath","All documentation submitted","All tests performed and reports and where applicable certificates submitted","Font size for conductor marking","Magnification factor","Location of cable ID ","Does cable ID system comply with 5.3","Font size of cable ID","Availability of catalogue","Max sustained current rating and calculations","Symmetrical Fault rating (kA)","Earth Fault ","Testing of cable in accordance with"]
[{"$nulls":12},1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30]
[{"$nulls":12},"Select item from list . . .","__________","__________","__________","__________","__________","__________",null,"__________","__________","__________","__________","__________","__________",null,"__________","__________","__________",null,null,"__________","__________","__________","__________","__________","__________",{"$nulls":10},"__________","__________","__________","__________","__________",null,"-","-","-","-","-","-","-","-","-"]
[{"$nulls":12},"CABLE,ELECT:GUX1XCQ 33KV 1C;CU;630 MM2","D-DT-8001 ",577440,33,1,630,"Individually screened","Strippable","Yes","MDPE","AWA","Black PE type S2","Yes","80mm (min)",500,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE,ELECT:GUX3MAQ 33KV 3C;AL;50 MM2","D-DT-8001 ",578946,33,3,50,"Individually screened","Strippable","Yes","PVC Type B1","SWA","Black PE type S2","Yes","80mm (min)",300,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE,ELECT:GUX3MCQ 33KV 3C;CU;50 MM2","D-DT-8001 ",578948,33,3,50,"Individually screened","Strippable","Yes","PVC Type B1","SWA","Black PE type S2","Yes","80mm (min)",300,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE,ELECT:GUX3PAQ 33KV 3C;AL;95 MM2","D-DT-8001 ",578951,33,3,95,"Individually screened","Strippable","Yes","PVC Type B1","SWA","Black PE type S2","Yes","80mm (min)",300,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE,ELECT:GUX3PCQ 33KV 3C;CU;95 MM2","D-DT-8001 ",578949,33,3,95,"Individually screened","Strippable","Yes","PVC Type B1","SWA","Black PE type S2","Yes","80mm (min)",300,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE,ELECT:GUX3SAQ 33KV 3C;AL;185 MM2","D-DT-8001 ",578947,33,3,185,"Individually screened","Strippable","Yes","PVC Type B1","SWA","Black PE type S2","Yes","80mm (min)",300,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE,ELECT:GUX3SCQ 33KV 3C;CU;185 MM2","D-DT-8001 ",578953,33,3,185,"Individually screened","Strippable","Yes","PVC Type B1","SWA","Black PE type S2","Yes","80mm (min)",300,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE,ELECT:GUX3UAQ 33KV 3C;AL;300 MM2","D-DT-8001 ",578952,33,3,300,"Individually screened","Strippable","Yes","PVC Type B1","SWA","Black PE type S2","Yes","80mm (min)",300,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE,ELECT:GUX3UCQ 33KV 3C;CU;300 MM2","D-DT-8001 ",578954,33,3,300,"Individually screened","Strippable","Yes","PVC Type B1","SWA","Black PE type S2","Yes","80mm (min)",300,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE 11kV 1C 630SQ. CU EUX1XCQ","D-DT-8001 ",171351,11,1,630,"Individually screened","Strippable","Yes","MDPE","AWA","Black PE type S2","Yes","80mm (min)",500,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE 22kV 1C 630SQ. CU FUX1XCQ","D-DT-8001 ",182545,22,1,630,"Individually screened","Strippable","Yes","MDPE","AWA","Black PE type S2","Yes","80mm (min)",500,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE,ELECT:EUX1MCQ 11KV 1C;CU;50 MM2","D-DT-8001 ",577428,11,1,50,"Individually screened","Strippable","Yes","MDPE","AWA","Black PE type S2","Yes","80mm (min)",500,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE,ELECT:EUX1PCQ 11KV 1C;CU;95 MM2","D-DT-8001 ",577429,11,1,95,"Individually screened","Strippable","Yes","MDPE","AWA","Black PE type S2","Yes","80mm (min)",500,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE,ELECT:EUX1SCQ 11KV 1C;CU;185 MM2","D-DT-8001 ",577430,11,1,185,"Individually screened","Strippable","Yes","MDPE","AWA","Black PE type S2","Yes","80mm (min)",500,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE,ELECT:EUX1UCQ 11KV 1C;CU;300 MM2","D-DT-8001 ",577431,11,1,300,"Individually screened","Strippable","Yes","MDPE","AWA","Black PE type S2","Yes","80mm (min)",500,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE,ELECT:EUX3PAQ 11KV 3C;AL;95 MM2","D-DT-8001 ",578940,11,3,95,"Individually screened","Strippable","Yes","PVC Type B1","SWA","Black PE type S2","Yes","80mm (min)",300,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE,ELECT:EUX3SAQ 11KV 3C;AL;185 MM2","D-DT-8001 ",578941,11,3,185,"Individually screened","Strippable","Yes","PVC Type B1","SWA","Black PE type S2","Yes","80mm (min)",300,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE,ELECT:EUX3UAQ 11KV 3C;AL;300 MM2","D-DT-8001 ",578950,11,3,300,"Individually screened","Strippable","Yes","PVC Type B1","SWA","Black PE type S2","Yes","80mm (min)",300,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE,ELECT:FUX1MCQ 22KV 1C;CU;50 MM2","D-DT-8001 ",577432,22,1,50,"Individually screened","Strippable","Yes","MDPE","AWA","Black PE type S2","Yes","80mm (min)",500,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE,ELECT:FUX1PCQ 22KV 1C;CU;95 MM2","D-DT-8001 ",577433,22,1,95,"Individually screened","Strippable","Yes","MDPE","AWA","Black PE type S2","Yes","80mm (min)",500,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE,ELECT:FUX1SCQ 22KV 1C;CU;185 MM2","D-DT-8001 ",577434,22,1,185,"Individually screened","Strippable","Yes","MDPE","AWA","Black PE type S2","Yes","80mm (min)",500,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE,ELECT:FUX1UCQ 22KV 1C;CU;300 MM2","D-DT-8001 ",577435,22,1,300,"Individually screened","Strippable","Yes","MDPE","AWA","Black PE type S2","Yes","80mm (min)",500,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE,ELECT:FUX3MAQ 22KV 3C;AL;50 MM2","D-DT-8001 ",578942,22,3,50,"Individually screened","Strippable","Yes","PVC Type B1","SWA","Black PE type S2","Yes","80mm (min)",300,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE,ELECT:FUX3PAQ 22KV 3C;AL;95 MM2","D-DT-8001 ",578943,22,3,95,"Individually screened","Strippable","Yes","PVC Type B1","SWA","Black PE type S2","Yes","80mm (min)",300,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE,ELECT:FUX3SAQ 22KV 3C;AL;185 MM2","D-DT-8001 ",578944,22,3,185,"Individually screened","Strippable","Yes","PVC Type B1","SWA","Black PE type S2","Yes","80mm (min)",300,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE,ELECT:FUX3UAQ 22KV 3C;AL;300 MM2","D-DT-8001 ",578945,22,3,300,"Individually screened","Strippable","Yes","PVC Type B1","SWA","Black PE type S2","Yes","80mm (min)",300,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE,ELECT:GUX1MCQ 33KV 1C;CU;50 MM2","D-DT-8001 ",577436,33,1,50,"Individually screened","Strippable","Yes","MDPE","AWA","Black PE type S2","Yes","80mm (min)",500,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE,ELECT:GUX1PCQ 33KV 1C;CU;95 MM2","D-DT-8001 ",577437,33,1,95,"Individually screened","Strippable","Yes","MDPE","AWA","Black PE type S2","Yes","80mm (min)",500,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE,ELECT:GUX1SCQ 33KV 1C;CU;185 MM2","D-DT-8001 ",577438,33,1,185,"Individually screened","Strippable","Yes","MDPE","AWA","Black PE type S2","Yes","80mm (min)",500,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE,ELECT:GUX1UCQ 33KV 1C;CU;300 MM2","D-DT-8001 ",577439,33,1,300,"Individually screened","Strippable","Yes","MDPE","AWA","Black PE type S2","Yes","80mm (min)",500,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE,ELECT:EUX3KCQ 11KV 3C;CU;25 MM2","D_DT_8001",171388,11,3,25,"Individually screened","Strippable","Yes","PVC Type B1","SWA","Black PE type S2","Longitudinally water blocking","80mm (min)",300,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE 22kV 3C 25SQ. CU FUX3KCQ","D-DT-8001 ",182546,22,3,25,"Individually screened","Strippable","Yes","PVC Type B1","SWA","Black PE type S2","Longitudinally water blocking","80mm (min)",300,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE 11kV 3C 50SQ. CU EUX3MCQ","D-DT-8001 ",171386,11,3,50,"Individually screened","Strippable","Yes","PVC Type B1","SWA","Black PE type S2","Longitudinally water blocking","80mm (min)",300,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE 22kV 3C 50SQ. CU FUX3MCQ","D-DT-8001 ",171384,22,3,50,"Individually screened","Strippable","Yes","PVC Type B1","SWA","Black PE type S2","Longitudinally water blocking","80mm (min)",300,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE 11kV 3C 95SQ. CU EUX3PCV","D-DT-8001 ",403148,11,3,95,"Individually screened","Strippable","Yes","PVC Type B1","SWA","Black PE type S2","Longitudinally water blocking","80mm (min)",300,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE 22kV 3C 95SQ. CU FUX3PCQ","D-DT-8001 ",171204,22,3,95,"Individually screened","Strippable","Yes","PVC Type B1","SWA","Black PE type S2","Longitudinally water blocking","80mm (min)",300,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE 11kV 3C 185SQ. CU EUX3SCQ","D-DT-8001 ",171352,11,3,185,"Individually screened","Strippable","Yes","PVC Type B1","SWA","Black PE type S2","Longitudinally water blocking","80mm (min)",300,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE 22kV 3C 185SQ. CU FUX3SCQ","D-DT-8001 ",175763,22,3,185,"Individually screened","Strippable","Yes","PVC Type B1","SWA","Black PE type S2","Longitudinally water blocking","80mm (min)",300,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]
[{"$nulls":12},"CABLE 11kV 3C 300SQ. CU EUX3UCQ","D-DT-8001 ",184296,11,3,300,"Individually screened","Strippable","Yes","PVC Type B1","SWA","Black PE type S2","Longitudinally water blocking","80mm (min)",300,"Yes","Yes","Yes","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","xxxxxxxxxx","Yes","Yes","xxxxxxxxxx","xxxxxxxxxx","SANS 1339"]

{"sheet":"Deviation Schedule","index":1,"n_rows":6,"n_cols":3,"rows_kept":6,"merged":[[0,0,0,2],[2,0,2,2]],"flags":["formulas_cached_only"]}
["Deviation schedule"]
[null,null,"CABLE 11kV 1C 630SQ. CU EUX1XCQ"]
["Any deviations offered to this specification shall be listed below with reasons for deviation.  In addition, evidence shall be provided that the proposed deviation will at least be more cost-effective that that specified by Eskom."]
["Item","Clause","Proposed deviation"]
[]
[null,null,"NO DEVIATIONS TO SPECIFICATION"]

{"sheet":"Drwg & Type Tests","index":2,"n_rows":59,"n_cols":10,"rows_kept":59,"merged":[[0,1,0,9],[1,1,1,9],[2,1,2,9],[5,1,5,4],[6,2,6,4],[7,2,7,4],[8,2,8,4],[9,2,9,4],[10,2,10,4],[11,1,11,4],[26,1,26,4],[36,1,36,4],[39,1,40,1],[41,1,43,1],[44,1,46,1],[49,1,51,1],[52,1,53,1],[54,1,55,1],[56,1,57,1]],"flags":["formulas_cached_only"]}
[null,"Drawing and Type Test Report Schedule for MV XLPE Cables"]
[]
[null,"SAP: 171351   CABLE 11kV 1C 630SQ. CU EUX1XCQ"]
[]
[null,1,2,3,4,5,6,7,8,9]
[null,"Drawings",{"$nulls":3},"Drawing/ Instruction number ","Revision number","Unique product model/ type/ code offered","Product rating / size offered ","Manufacturing location (Name, Address and Country)"]
[null,"1","Cable cross sectional area drawing"]
[null,"2","Cable embossing drawing"]
[null,"3","Cable drum and drum labelling"]
[null,"4","Cable water blocking removal instructions"]
[null,"5","Conductor and cable marking detail"]
[null,"Type Test Reports and certificates as required in SANS 1339",{"$nulls":3},"Report Number","Test facility and date tested","Unique product model/type type tested","Product rating offered ","Manufacturing location of type tested unit (Name, Address and Country)"]
[null,"Component","Test property","Test method","Requirement"]
[null,"Fillers and binders","Acid gas emission","SANS 60754-2","4.5.3"]
[null,"Bedding","Acid gas emission","SANS 60754-2","4.5.3"]
[null,"Outer sheath","Acid gas emission","SANS 60754-2","4.5.3"]
[null,"Finished cable","Fire propagation","SANS 60332-3-24","4.5.1"]
[null,null,"Smoke emission","SANS 61034-2","4.5.2"]
[null,"Type approval test","Bending test","SANS 6284-3","4.6.2.1"]
[null,null,"Partial discharge test","SANS 6291","4.6.2.3"]
[null,null,"Load cycling test","SANS 6284-3","4.6.2.2"]
[null,null,"Impulse voltage withstand","SANS 6284-3","4.6.2.4"]
[null,null,"Four hour high voltage withstand","SANS 6284-3","4.6.2.5"]
[null,"Ageing test","50 Hz, 2 year test or","SANS 6284-5","4.7.2"]
[null,"(One of the two tests 50Hz or 500Hz will be sufficient)","500 Hz, 3 000 h test","SANS 6284-5","4.7.3"]
[null,"Water penetration test","Longitudinal water penetration test","Annex F of IEC 60502-2:2014","4.3.14"]
[null,"Routine Test reports and certificates generic copies as required in SANS 1339",{"$nulls":3},"Report Number","Test facility and date tested","Unique product model/type type tested","Product rating offered ","Manufacturing location of type tested unit (Name, Address and Country)"]
[null,"Component","Test property","Test method","Requirement"]
[null,"Metallic core screen","Assembly","SANS 1339: 2017 (Visual examination)","4.3.7.1"]
[null,"Core(s)","Identification","SANS 1339: 2017 (Visual examination)","4.3.6"]
[null,null,"Laying up","SANS 1339: 2017 (Visual examination)","4.3.8.1"]
[null,"Finished cable","Marking","SANS 1339: 2017 (Visual examination)","7.2.1"]
[null,null,"Conductor resistance","SANS 6282-1","4.4.1"]
[null,null,"Voltage withstand","SANS 6284-3","4.4.2"]
[null,null,"Partial discharge test","SANS 6291","4.4.3"]
[null,null,"DC voltage test on outer sheath","SANS 6286","4.4.4"]
[null,"Sample Test reports and certificates generic copies as required in SANS 1339",{"$nulls":3},"Report Number","Test facility and date tested","Unique product model/type type tested","Product rating offered ","Manufacturing location of type tested unit (Name, Address and Country)"]
[null,"Component","Test property","Test method","Requirement"]
[null,"Conductor","Construction","SANS 1411-1","4.3.1"]
[null,"Conductor screen","Thickness","SANS 6284-2","4.3.2.3"]
[null,null,"Measurement of insulation\ninterface protrusions and\nvoids","SANS 6284-1","4.3.2.2"]
[null,"XLPE insulation","Composition","SANS 1411-4","4.3.3.1"]
[null,null,"Thickness","SANS 6284-1","4.3.3.2"]
[null,null,"Measurement of voids and contaminants","SANS 6284-1","4.3.3.1"]
[null,"Core screen","Adhesion","SANS 6284-2","4.3.4.2"]
[null,null,"Thickness","SANS 6284-2","4.3.4.3"]
[null,null,"Measurement of insulation\ninterface protrusions and\nvoids","SANS 6284-1","4.3.4.2"]
[null,"Metallic core screen","Wire size (Where applicable)","By Measurement","4.3.7.3"]
[null,"Core(s)","Identification","Visual examination","4.3.6"]
[null,"Lead or lead alloy sheath (where applicable)","Composition","SANS 6281 -2","4.3.10.2"]
[null,null,"Malleability","SANS 6281 -2","4.3.10.2"]
[null,null,"Thickness","SANS 6281 -2","4.3.10.4"]
[null,"Bedding","Physical properties","SANS 1411-2 or 1411- 5","4.3.11.1"]
[null,null,"Thickness","SANS 60811-201","4.3.11.2"]
[null,"Armour","Properties","SANS 1411-6","4.3.12.1"]
[null,null,"Wire diameter","SANS 6283","4.3.12.2"]
[null,"Outer sheath","Physical properties","SANS 1411-2, SANS1411-5 or SANS1411-7","4.3.13.1"]
[null,null,"Thickness","SANS 60811-1-1","4.3.13.2"]
[null,"Finished cable","Resistivity of semiconducting screens","SANS 6284-2","4.3.2.4"]

{"sheet":"Sheet1","index":3,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}