{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["Summary","Preliminaries","BOQ"],"not_rendered":{"external_links":1,"defined_names":2},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Summary","index":0,"n_rows":19,"n_cols":5,"rows_kept":19,"merged":[[2,0,2,4],[3,0,3,3],[4,0,4,3],[5,0,5,3],[6,0,6,3],[7,0,7,3],[8,0,8,3],[9,0,9,3]],"flags":["formulas_cached_only"]}
[]
[]
["SUMMARY"]
[]
["PRELIMINARY & GENERAL ITEMS",{"$nulls":3},0]
["FIRE PROTECTION SYSTEM",{"$nulls":3},0]
["FIRE DETECTION INSTALLATION",{"$nulls":3},0]
[]
[]
["TOTAL (excl. 15% VAT)",{"$nulls":3},0]
[]
[]
["………………………………………"]
["SIGNED"]
[]
[]
[]
["………………………………………"]
["NAME"]

{"sheet":"Preliminaries","index":1,"n_rows":26,"n_cols":6,"rows_kept":26,"merged":[[9,0,9,3],[11,1,11,5],[17,0,17,3],[21,1,21,7],[22,1,22,7],[23,1,23,7],[24,1,24,7],[25,1,25,7]],"flags":["formulas_cached_only"]}
[]
[]
[]
["No","Description","Unit","Qty","Rate","Total"]
[1,"PRELIMINARY & GENERAL ITEMS"]
[1.1,"OVERHEAD FOR PROJECT (This includes Site Establishment Overhead Costs, Office Overheads, Administration Costs etc.)","Sum",1]
[1.2,"SHEQ Management, OHSA appointments, PPE etc. ","Sum",1]
[1.3,"Supervisor","Day",132]
[1.4,"Safety Officer","Day",132]
["Sub-Total (carried over to Summary)"]
[]
[null,"Transport"]
[]
[1,"Transport ","Unit","QTY","Rate","Amount"]
[1.1,"LDV","km",13200]
[1.2,"Personnel Transport for Staff","km",13200]
[]
["Sub-Total (carried over to Summary)"]
[]
[]
[null,"Notes to Tenderer:"]
[1,"The estimated quantities are subject to re-measure."]
[2,"Tenderer to provide detailed breakdown for the lump sum items as and when requested."]
[3,"Transport will be assessed based on log book verified  by Supervisor and approved by the Project Manager. "]
[4,"The tenderer needs to read scope of works together with the price schedule to ensure they price comprehensively."]
[5,"The Tenderers to ensure that materials used for pricing are SANS or SABS approved. Specification will be requested. "]

{"sheet":"BOQ","index":2,"n_rows":127,"n_cols":4,"rows_kept":127,"merged":[[0,0,0,5],[68,0,69,0],[68,1,69,4],[68,5,69,5],[99,0,99,3]],"flags":["formulas_cached_only"]}
["ROSHERVILLE SUPERSTORE FIRE PROTECTION _ BILL OF QUANTITIES"]
[]
[]
[2,"FIRE PROTECTION INSTALLATION"]
[]
[null,"Design, manufacture, works testing, supply and delivery to site, moving into position, erection, connecting up,  site testing, witness testing, proving to the inspectors, demonstrating to the engineer and maintenance team of the complete installation as per conditions of contract , the specification in the bills and on drawings."]
[2.1,"Fire Hydrants & Hose Reels Pump skid mounted set consisting electric duty and standby diesel pumps duty 2400 LPM  @ 600kPa  Jockey pump duty 1.0 Litres/sec @ 800kPa. Pump set to be complete with triple pump start test arrangement, control panel with status indicators specified, 2 hours diesel day tank with bund container for spilt fuel, batteries, isolating and strainer valves, pressure switches, pressure gauges horn & flashing beacons and other accessories to make a complete installation. Assembly to have 200 litres surge pressure vessel. Pumps to a have ASIB test certificate.","Item",1]
[2.2,"Black mild victaulic grooved jointed steel pipework for fire hydrants and hose reel to SANS 62 with one coat rust inhibitor and two coats firemen's red code A11 paint. Pipework to include supports, bends, reducers, flanges and all pipe accessories to make a complete installation."]
["i","25 mm ","m",250]
["ii","50 mm","m",50]
["iii","80 mm","m",120]
["iv","100 mm","m",750]
["v","150 mm","m",130]
["vi","250 mm","m",25]
[]
[2.3,"Black mild steel pipework for sprinkler system to SANS 62 with one coat rust inhibitor and two coats firemen's red code A11 paint. Pipework to include supports, bends, reducers, flanges and all pipe accessories to make a complete installation."]
["i","32 mm ","m",160]
["ii","40 mm ","m",160]
["iii","50 mm","m",200]
["iv","80 mm","m",96]
["v","100 mm","m",110]
["vii","150 mm","m",60]
["viii","Drain cock as 20mm NB isolating ball valve at 80mm dropper base","No.",24]
[2.4,"ESFR FM approved pendent sprinkler heads complete with stainless steel guards, K=24.2, Temp.= 68deg C, NB=20mm","No.",400]
[2.5,"PN16 Valves for fire protection use shall be ASIB, UL or FM approved brand with tracable part number and nominal bore as stated in the bills all painted fireman's red code A11"]
["i","25 mm NB complete with ball float valve for incoming cold water supply  ","No.",2]
["ii","100 mm NB gear operated isolating test pipe valve","No.",2]
["iii","250 mm NB gear operated butterfly isolating valve","No.",2]
["v","25 mm NB ball type isolating drain valves","No.",18]
["vii","50 mm NB ball type isolating valve","No.",3]
[2.6,"2400 LPM flow test metering device to be fitted on the pump to tank test pipework","No.",1]
[2.7,"65 mm outlet fire hydrant with handwheel opening mechanism. Hydrant to have a horizontal screwed connection to the 80mm dropper.","No.",17]
[2.8,"Swing Type Fire Hose Reel to  comply with SANS 543  complete with 25 mm chrome plated isolating valve.\nFire hose reels shall be fitted with a 30m long reinforced red rubber hose of internal diameter of 20mm nominal bore, with a 4.8mm internal diameter aluminium nozzle and chrome plated brass isolating valve.Fire hose reel pipes above ground shall be colour coded signal red A11.\n ","No.",2]
[2.9,"Wall  Type Fire Hose Reel to  comply with SANS 543 complete with 25 mm chrome plated isolating valve.\nFire hose reels shall be fitted with a 30m long reinforced red rubber hose of internal diameter of 20mm nominal bore, with a 4.8mm internal diameter aluminium nozzle and chrome plated brass isolating valve.Fire hose reel pipes above ground shall be colour coded signal red A11.\n ","No.",34]
[{"v":2.1,"d":"2.10"},"2kg CO2  fire extinguisher complying with the requirements of SANS 1567. Extinguishers to hung at position as shown on the drawings complete with meranti backing board.","No.",2]
[2.11,"9 kg Dry Chemical powder fire extinguisher complying with the requirements of SANS 1910. Extinguishers to hung at position as shown on the drawings complete with meranti backing board.","No.",68]
[1.12,"14,640 x 4,880 x 2,440 mm  high galvanised mild steel sectional tank effective capacity 144m3 complete with subdivision step ladders, level indicators , 2 No. 250dia flanged vortex inhibitors, outlets, overflows as shown on the drawings and as necessary to have a complete assembly.","Item",1]
[2.13,"Fire brigade breeching double inlet complete with storz suction hydrant adaptor valve, non return valve, isolating valves, gauge and fittings as detailed on the drawing","Item",1]
[2.14,"Fire signage as indicated on the drawings. Marking and signposting shall be of the photoluminescent type and shall comply with the relevant sections of SANS 1186. "]
[]
["i","Framed 290 mm Type E1/E2 back to back","No.",9]
["ii","Framed 290mm  Type E3","No.",12]
["iii","Framed 190mm  Type E3","No.",3]
["iv","Framed 290 mm Type F1","No.",17]
["v","Framed 290mm Type F4","No.",17]
["vi","Framed 190mm Type F5","No.",2]
["vii","Framed 190mm Type F6","No.",2]
["viii","Framed 190mm Type F4","No.",2]
["ix","Framed 290mm Type F18/21 back to back","No.",1]
["x","Framed 290 mm Type F15","No.",1]
["xi","Type F45-FIRE EXIT/KEEP CLEAR","No.",10]
["xii","Framed weather proof 290mm Type F49/F38 on 1800mm high gms support","No.",1]
["xiii","Framed weather proof 600 x 600 mm TYPE GA 26-ASSEMBLY POINT on 1800mm high gms support","No.",2]
[]
[null,"Sprinkler Fire Water Storage Tank"]
[]
[2.15,"Strip out old 265kl existing fire water tank and remove from site as directed by client","Item",1]
[2.16,"The Supplier must prepare ground/ area for installation of new tank on existing foot print 4m radius.","Item",1]
[2.17,"Design 265kl  galvanized cylindrical water storage tank 4m radius.","Item",1]
[2.18,"Supply new 265kl galvanized cylindrical  water storage tank 4 m radius.","Item",1]
[2.19,"Install new 265kl galvanized cylindrical water storage tank.","Item",1]
[{"v":2.2,"d":"2.20"},"Reconnect new water tank with existing water inlet and outlet pipework. Also supply necessary gate valves (drainage, inlet), inlet valve (ball valve) and gaskets required.","Item",1]
[2.21,"Paint new connections with signal red SANS 1091 compliance","Item",1]
[2.22,"Test new installation for leaks and commission. ","Item",1]
[2.22,"Testing and commissioning to the satisfaction of the engineer","Item",1]
[2.24,"Preparation of Operating manuals/all technical drawings(as built drawings) and Maintenance Manuals","Item",1]
[2.25,"Allow for training of user client staff","Item",1]
[]
[null,"Sub-Total (carried over to Summary)"]
[]
[]
[3,"FIRE DETECTION INSTALLATION"]
["*","Supply, install and connect inclusive of all fixing materials, wastage and sundries. CLASS A wiring method. Equipment to be Ziton type or similar and equal approved. NB: inclusive of all necessary equipment such as cherry picker, scaffolding, etc"]
["*","Installation to comply in full with SANS10139 and applicable standards"]
["*","Standby Battery supplies for any part of the system shall be capable of maintaining the system in normal operation for at least 24 h,after which there shall be sufficient capacity to operate all sounders in evacuation mode for at least 30 min. "]
[3.1,"4-loop Adressable firepanel, incl. batery back-up, network card, auto dialer, local sounder, logbook and holder.","No",1]
[3.2,"Addressable Fire Panel Accessory - Network Printed Circuit Board","No",1]
[3.3,"Addressable Fire Panel Repeater Small Cabinet English","No",3]
[3.4,"Addressable Fire Panel ACC - LED IND - 24 Z","No",6]
[3.5,"Battery 12 V 7.2 Ah (for 2010-1/-2 fire panels only, use\nBS127N-A for all other applications)","No",4]
[3.6,"Ceiling : Optical sensor [ZP730-2] c/w surface mounting sensor base [ZP7-SB1]","No",40]
[3.7,"Void : Optical sensor [ZP730-2] c/w surface mounting sensor base [ZP7-SB1]","No",40]
[3.8,"Manual Call point (RED), surface base, resettable element, LED indication - Fire Exits","No",30]
[3.9,"Manual Call point (GREEN), surface base, resettable element, LED indication","No",1]
[{"v":3.1,"d":"3.10"},"Combination beacon / sounder, recessed base","No",30]
[3.11,"Loop Isolators, CLASS A wiring method","No",3]
[3.12,"Line Relays - Interface to Mechanical System","No",3]
[3.13,"Line Relays - Interface to Automated sliding doors, smoke curtain, access controlled doors, etc","No",1]
[3.14,"Line Interface units","No",2]
[3.15,"Beam detector (transmitter) and Reflector (receiver) installed 1200mm above the top of the crane. Range from 50 – 110 m. Video-based type","No",26]
[3.16,"Supply and Installation of loop PH30 Fire Resistant Cable 2 Core, 1.5mm wiring and cable trunking (P8000 with covers and hangers) - 200m roll","No",5]
[3.17,"P8000 cable trunking (WxH: 76 x 76mm); hangers  c/w nuts and bolts, bends, tees etc.","No",300]
[3.18,"25mm PVC conduiting c/w hangers, saddles, screws,  nuts and bolts, bends, tees etc.","No",600]
[3.19,"25mm bosal conduiting c/w hangers, saddles, screws,  nuts and bolts, bends, tees etc.","No",800]
[{"v":3.2,"d":"3.20"},"Allow for inspection(s), testing and commissioning of the complete fire detection installation","Sum",1]
[3.21,"Other - Contractor to specify","Sum",1]
[]
[4,"DECOMMISSIONING OF EXISTING SERVICES"]
[4.1,"Allow for decommissioning of existing services and removal of rubble from site. ","Sum",1]
["Sub-Total (carried over to Summary)"]
{"$rows_empty":25}
["…………………………………………………………………………………………………………………………………."]
["TENDERER"]