{"text_format":"3","workbook":"xls","n_sheets":5,"sheets":["LV Cables Technical Schedules","Deviation Schedule","Tools, Spares,Drwg & Type Tests","Sheet1","Sheet2"],"not_rendered":{"external_links":1,"defined_names":20},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"LV Cables Technical Schedules","index":0,"n_rows":106,"n_cols":22,"rows_kept":106,"merged":[[0,1,0,7],[1,1,1,7],[2,1,2,7],[3,6,3,7],[4,1,4,7],[5,1,5,7],[8,3,8,4],[9,3,9,4],[53,1,53,4],[56,1,56,2],[57,1,57,2],[62,1,62,2],[63,1,63,2]],"flags":["formulas_cached_only"]}
[null,"TECHNICAL SCHEDULES A & B FOR LV CABLES "]
[]
[null,"SAP: 0400642   CABLE,ELECT:BVX4PCV 1,0KV 4C;CU;95 MM2"]
[]
[null,"Schedule A:  Purchasers specific requirements"]
[null,"Schedule B: Guarantees and technical particulars of equipment offered"]
[]
[null,1,2,null,3,null,4,5]
[null,"Item ","240-56063805 or SANS 1507:3","Description",null,null,"Schedule A","Schedule B"]
[null,1,null,"Item and system description"]
[{"$nulls":4},"CABLE,ELECT:BVX4PCV 1,0KV 4C;CU;95 MM2"]
[null,1.1,null,"·","SAP No",null,"0400642","xxxxxxxxxx"]
[null,1.2,null,"·","Buyers Guide Drawing",null,"D-DT-2128","xxxxxxxxxx"]
[null,"1.3",null,"·","Symmetrical fault level rating","kA","xxxxxxxxxx","____________"]
[null,"1.4","240-56063805 Rev 3, clause 3.1","·","Nominal system voltage","kV",1,"xxxxxxxxxx"]
[null,"1.5",null,"·","Earth fault level rating","kA","xxxxxxxxxx","____________"]
[]
[null,2.1,"240-56063805 Rev 3,  clause 3.1","·","Rated voltage (Ur)","kV",1,"xxxxxxxxxx"]
[null,null,"240-56063805 Rev 3,  clause 3.2.2","·","Insulation material",null,"PVC","xxxxxxxxxx"]
[null,null,"240-56063805 Rev 3,  clause 3.2.1","·","Conductor material",null,"Cu","xxxxxxxxxx"]
[null,null,"D-DT 2128 & D-DT 3128","·","Conductor Size",null,{"v":95,"d":"95.0"},"xxxxxxxxxx"]
[null,2.3," 240-56063805 Rev 3, clause 3.2.3","·","Number of cores",null,4,"xxxxxxxxxx"]
[null,null,"240-56063805 Rev 3, clause 3.2.3b), Table 1","·","Are colours of phases as per clause 3.2.3?",null,"Yes","xxxxxxxxxx"]
[null,null,"240-56063805 Rev 3, clause 3.2.4","·","Bedding under armouring",null,"PVC","xxxxxxxxxx"]
[null,2.9,"240-56063805 Rev 3, clause 3.2.5","·","Armour ",null,"Galvanized steel wire armour","xxxxxxxxxx"]
[null,"2.10","240-56063805 Rev 3,  clause 3.2.6","·","The cable shall have PCV outer sheathing, and shall be UV radiation stabilized.",null,"Yes","xxxxxxxxxx"]
[null,"2.11","240-56063805 Rev 3,  clause 3.2.7","·","Does the cable  meet the fire perfomance requirements as per 3.2.7?",null,"Yes","____________"]
[null,"2.13","SANS 1507-3, clause 5.2.2","·","Rated frequency (fr)","Hz",50,"xxxxxxxxxx"]
[null,"3.1","240-56063805 Rev 3,  clause 3.3.1","·","Does the supplied woodern drum meet the minimum requirements as per clause 3.3.1?",null,"Yes","____________"]
[null,"3.2","240-56063805 Rev 3,  clause 3.3.1b)","·","Drum length required if other than that specified in 3.3.1b)","m",300,"____________"]
[null,"3.3","240-56063805 Rev 3,  clause 3.3.2","·","Is conductor marking system details supplied with tender?",null,"Yes","____________"]
[null,"3.4","240-56063805 Rev 3,  clause 3.3.2","·","Font size for conductor marking characters","mm","xxxxxxxxxx","____________"]
[null,"3.5","240-56063805 Rev 3,  clause 3.3.2d)","·","Is marking of cable identification system details supplied with tender?","Yes","Yes","____________"]
[null,"3.6","240-56063805 Rev 3,  clause 3.3.3","·","Cable identification system location?",null,"xxxxxxxxxx","____________"]
[null,"3.7","240-56063805 Rev 3,  clause 3.3.3","·","Font size for the cable identification system characters","mm","xxxxxxxxxx"]
[null,"3.8","240-56063805 Rev 3,  clause 3.3.4","·","Does the marking of cable outer sheath comply to 3.6?",null,"Yes","____________"]
[null,"3.9","240-56063805 Rev 3,  clause 3.4","·","Are all relevant documents submitted?",null,"Yes","____________"]
[null,"3.10","240-56063805 Rev 3,  clause 3.4.4","·","Copy of type tests report and where applicable certificates to be provided with tender documentation ",null,"Yes","____________"]
[null,"3.11","240-56063805 Rev 3,  clause 3.4.1","·","Dimentions of cable submitted",null,"Yes","____________"]
[null,"3.12","240-56063805 Rev 3,  clause 3.4.2",null,"Maximum sustained current rating at a conductor temperature of 70dec Celcius installed in:"]
[{"$nulls":4},"1) Ground?","A","xxxxxxxxxx","____________"]
[{"$nulls":4},"2) Air?","A","xxxxxxxxxx","____________"]
[{"$nulls":4},"3) Ducts?","A","xxxxxxxxxx","____________"]
[null,"3.13","240-56063805 Rev 3,  clause 3.4.2b)",null,"Short circuit rating?","kA","xxxxxxxxxx","____________"]
[null,"3.14","240-56063805 Rev 3,  clause 3.4.2c)",null,"Cable mass?","kg/m","xxxxxxxxxx","____________"]
[null,"3.15","240-56063805 Rev 3,  clause 3.4.2d)",null,"Gross mass per standard drum length?","kg ","xxxxxxxxxx","____________"]
[null,"3.16","240-56063805 Rev 3,  clause 3.4.2e)",null,"Resistance at max conductor temperature?","Ω/m","xxxxxxxxxx","____________"]
[null,"3.17","240-56063805 Rev 3,  clause 3.4.2f)",null,"Reatance per phase?","Ω/m","xxxxxxxxxx","____________"]
[null,"3.18","240-56063805 Rev 3,  clause 3.8.2g)",null,"Capacitance per phase?","nF/m","xxxxxxxxxx","____________"]
[null,"3.19","240-56063805 Rev 3,  clause 3.4.2h)",null,"Zero sequence impedance and capacitance per phase?","Ω/m","xxxxxxxxxx","____________"]
[null,"3.20","240-56063805 Rev 3,  clause 3.4.4",null,"Testing of cable is done in accordance with SANS 1507?",null,"Yes","____________"]
[]
[]
[null,"SIGNATURES"]
[]
[]
[{"$nulls":4},"         "]
[null,"Factory",null,null,"Name (Print)",null,"Sign","Date"]
[]
[]
[]
[]
[{"$nulls":4},"         "]
[null,"Eskom",null,null,"Name (Print)",null,"Sign","Date"]
[]
[]
[]
[]
[{"$nulls":15},4.2,4.3,4.3,"4.4.5","5.1.3"]
[{"$nulls":12},"Description","Buyer's Guide Drawing","SAP No","Rated Voltage","Number of cores","Conductor Size","Armouring","Drum Length","Symmetrical fault level (kA)","Earth Fault Level A"]
[{"$nulls":12},1,2,3,4,5,6,7,8,9,10]
[{"$nulls":12},"Select item from list . . .","__________","__________","__________","__________","__________","_______________________","__________","__________","__________"]
[{"$nulls":12},"CABLE,ELECT:BVX2HCV 1,0KV 2C;CU;16 MM2","D-DT-3128","0014474",1000,2,16,"Galvanized steel wire armour",500,20]
[{"$nulls":12},"CABLE,ELECT:BVX4HCV 1,0KV 4C;CU;16 MM2","D-DT-3128","0404766",1000,4,16,"Galvanized steel wire armour",500,20]
[{"$nulls":12},"CABLE,ELECT:BVX4KCV 1,0KV 4C;CU;25 MM2","D-DT-3128","0404767",1000,4,25,"Galvanized steel wire armour",300,20]
[{"$nulls":12},"CABLE,ELECT:BVX4LCV 1,0KV 4C;CU;35 MM2","D-DT-3128","0400639",1000,4,35,"Galvanized steel wire armour",300,20]
[{"$nulls":12},"CABLE,ELECT:BVX4NCV 1,0KV 4C;CU;70 MM2","D-DT-3128","0400641",1000,4,70,"Galvanized steel wire armour",300,20]
[{"$nulls":12},"CABLE,ELECT:BVX4QCV 1,0KV 4C;CU;120 MM2","D-DT-3128","0403090",1000,4,120,"Galvanized steel wire armour",300,20]
[{"$nulls":12},"CABLE,ELECT:BVX4RCV 1,0KV 4C;CU;150 MM2","D-DT-3128","0404119",1000,4,150,"Galvanized steel wire armour",300,20]
[{"$nulls":12},"CABLE,ELECT:BVX4SCV 1,0KV 4C;CU;185 MM2","D-DT-3128","0403094",1000,4,185,"Galvanized steel wire armour",300,20]
[{"$nulls":12},"CABLE,ELECT:BVX3HVC 1,0KV 3C;CU;16 MM2","D-DT-3128","0404103",1000,3,16,"Galvanized steel wire armour",500,20]
[{"$nulls":12},"CABLE,ELECT:BVV1WCV 1,0KV 1C;CU;500 MM2","D-DT-3128","0403113",1000,1,500,"Aluminium wire armour",300,20]
[{"$nulls":12},"CABLE,ELECT:BVV1TCV 1,0KV 1C;CU;240 MM2","D-DT-3128","0403351",1000,1,240,"Aluminium wire armour",300,20]
[{"$nulls":12},"CABLE,ELECT:BVX4MCV 1,0KV 4C;CU;50 MM2","D-DT-3128","0403353",1000,4,50,"Galvanized steel wire armour",300,20]
[{"$nulls":12},"CABLE,ELECT:BVX2KCV 1,0KV 2C;CU;25 MM2","D-DT-3128","0403473",1000,2,25,"Galvanized steel wire armour",300,20]
[{"$nulls":12},"CABLE,ELECT:BVX2LCV 1,0KV 2C;CU;35 MM2","D-DT-3128","0404634",1000,2,35,"Galvanized steel wire armour",300,20]
[{"$nulls":12},"CABLE,ELECT:BVX3LCV 1,0KV 3C;CU;35 MM2","D-DT-3128","0404489",1000,3,35,"Galvanized steel wire armour",300,20]
[{"$nulls":12},"CABLE,ELECT:BVX4TCV 1,0KV 4C;CU;240 MM2","D-DT-3128","0171185",1000,4,240,"Galvanized steel wire armour",300,20]
[{"$nulls":12},"CABLE,ELECT:BVX3KCV 1,0KV 3C;CU;25 MM2","D-DT-3128","0171198",1000,3,25,"Galvanized steel wire armour",300,20]
[{"$nulls":12},"CABLE,ELECT:BVX3NCV 1,0KV 3C;CU;70 MM2","D-DT-3128","0171333",1000,3,70,"Galvanized steel wire armour",300,20]
[{"$nulls":12},"CABLE,ELECT:BVX2ECV 1,0KV 2C;CU;4 MM2","D-DT-3128","0404122",1000,2,4,"Galvanized steel wire armour",500,20]
[{"$nulls":12},"CABLE,ELECT:BVX4DCV 1,0KV 4C;CU;2.5 MM2","D-DT-3128","0400646",1000,4,2.5,"Galvanized steel wire armour",500,20]
[{"$nulls":12},"CABLE,ELECT:BVX4ECV 1,0KV 4C;CU;4 MM2","D-DT-3128","0404764",1000,4,4,"Galvanized steel wire armour",500,20]
[{"$nulls":12},"CABLE,ELECT:BVX12DCV 1,0KV 12C;CU;PVC","D-DT-3128","0404761",1000,12,2.5,"Galvanized steel wire armour",500,20]
[{"$nulls":12},"CABLE,ELECT:BVX19DCV 1.0KV 19C;CU;PVC","D-DT-3128","0404118",1000,19,2.5,"Galvanized steel wire armour",500,20]
[{"$nulls":12},"CABLE,ELECT:BVX4PCV 1,0KV 4C;CU;95 MM2","D-DT-2128","0400642",1000,4,95,"Galvanized steel wire armour",300,20]
[{"$nulls":12},"CABLE,ELECT:BVX4LAV 1,0KV 4C;AL;35 MM2","D-DT-2128","0171276",1000,4,35,"Galvanized steel wire armour",300,20]
[{"$nulls":12},"CABLE,ELECT:BVX4MAV 1,0KV 4C;AL;50 MM2","D-DT-2128","0528922",1000,4,50,"Galvanized steel wire armour",300,20]
[{"$nulls":12},"CABLE,ELECT:BVX4NAV 1,0KV 4C;AL;70 MM2","D-DT-2128","0403082",1000,4,70,"Galvanized steel wire armour",300,20]
[{"$nulls":12},"CABLE,ELECT:BCX4PAV 1,0KV 4C;AL;95 MM2","D-DT-2128","0171215",1000,4,95,"Galvanized steel wire armour",300,20]
[{"$nulls":12},"CABLE,ELECT:BVX4QAV 1,0KV 4C;AL;120 MM2","D-DT-2128","0403084",1000,4,120,"Galvanized steel wire armour",300,20]
[{"$nulls":12},"CABLE,ELECT:BVX4RAV 1,0KV 4C;AL;150 MM2","D-DT-2128","0171265",1000,4,150,"Galvanized steel wire armour",300,20]
[{"$nulls":12},"CABLE,ELECT:BVX4SAV 1,0KV 4C;AL;185 MM2","D-DT-2128","0403086",1000,4,185,"Galvanized steel wire armour",300,20]
[{"$nulls":12},"CABLE,ELECT:BVX4TAV 1,0KV 4C;AL;240 MM2","D-DT-2128","0171184",1000,4,240,"Galvanized steel wire armour",300,20]
[{"$nulls":12}," CABLE,ELECT:BVX7DCV;POWER;2.5 MM2;PVC","D-DT-3128","0404120",1000,7,2.5,"Galvanized steel wire armour",500,20]
[{"$nulls":12}," CABLE,1.0KV 2C 2,5MM SQ CU BVX2DCV","D-DT-3128","0404127 ",1000,2,2.5,"Galvanized steel wire armour",500,20]

{"sheet":"Deviation Schedule","index":1,"n_rows":4,"n_cols":3,"rows_kept":4,"merged":[[0,0,0,2],[2,0,2,2]],"flags":["formulas_cached_only"]}
["Deviation schedule"]
[null,null,"CABLE,ELECT:BVX4PCV 1,0KV 4C;CU;95 MM2"]
["Any deviations offered to this specification shall be listed below with reasons for deviation.  In addition, evidence shall be provided that the proposed deviation will at least be more cost-effective that that specified by Eskom."]
["Item","Clause","Proposed deviation"]

{"sheet":"Tools, Spares,Drwg & Type Tests","index":2,"n_rows":22,"n_cols":10,"rows_kept":22,"merged":[[0,1,0,9],[1,1,1,9],[2,1,2,9],[5,1,5,4],[6,2,6,4],[7,2,7,4],[8,2,8,4],[9,2,9,4],[10,1,10,4],[14,1,14,4]],"flags":["formulas_cached_only"]}
[null,"Tools, Spares, Drawing and Type Test Report Schedule for LV PVC Cables"]
[]
[null,"SAP: 0400642   CABLE,ELECT:BVX4PCV 1,0KV 4C;CU;95 MM2"]
[]
[null,1,2,3,null,4,5,6,7,8]
[null,"Drawings",{"$nulls":3},"Drawing/ Instruction number ","Revision number","Unique product model/ type/ code offered","Product rating / size offered ","Manufacturing location (Name, Address and Country)"]
[null,"1","Cable cross sectional area drawing"]
[null,"2","Cable embossing drawing"]
[null,"3","Cable drum and drum labelling"]
[null,"4","Conductor and cable marking detail"]
[null,"Type Test Reports and certificates as required in SANS 1507",{"$nulls":3},"Report Number","Test facility and date tested","Unique product model/type type tested","Product rating offered ","Manufacturing location of type tested unit (Name, Address and Country)"]
[null,"Component","Test property","Test method","Requirement"]
[null,"Finished cable","Fire propagation","SANS 60332-3","4.4.1"]
[]
[null,"Routine Test reports and certificates generic copies as required in SANS 1507",{"$nulls":3},"Report Number","Test facility and date tested","Unique product model/type type tested","Product rating offered ","Manufacturing location of type tested unit (Name, Address and Country)"]
[null,"Component","Test property","Test method","Requirement"]
[null,"PVC Insulation","Spark test","SANS 62230","4.2.2.3"]
[null,null,"Core identification","Visual examination","4.2.3"]
[null,null,"Assembly of cores","Visual examination","4.2.4"]
[null,"Finished cable","Marking","Visual examination","SABS 1507-1: 4.2.1"]
[null,null,"Voltage withstand","SANS 6284-3","4.3.2"]
[null,null,"Conductor resistance","SANS 1411-1","4.3.1"]

{"sheet":"Sheet1","index":3,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}

{"sheet":"Sheet2","index":4,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}