NEC3 Term Service Contract (TSC3)

| Between | ESKOM HOLDINGS SOC Ltd (Reg No. 2002/015527/30) |  |
| --- | --- | --- |
| and | [Insert at award stage] (Reg No. ) |  |
| for | [●] |  |
| Contents: |  | No of pages |
| Part C1 | Agreements & Contract Data | [●] |
| Part C2 | Pricing Data | [●] |
| Part C3 | Scope of Work | [●] |
| CONTRACT No. | [Insert at award stage] |  |

# PART C1:	AGREEMENTS & CONTRACT DATA

| Contents: |  | No of pages |
| --- | --- | --- |
| C1.1 | Form of Offer and Acceptance [to be inserted from Returnable Documents at award stage] | [●] |
| C1.2a | Contract Data provided by the Employer | [●] |
| C1.2b | Contract Data provided by the Contractor [to be inserted from Returnable Documents at award stage] | [●] |
| C1.3 | Proforma Guarantees | [●] |

CONTRACT	- II -	TSC3 COVER PAGES

C1.1 Form of Offer & Acceptance

Offer

The Employer, identified in the Acceptance signature block, has solicited offers to enter into a contract for the procurement of:

#### Refurbishment and repairs of MV induction motors for Matimba power station

The tenderer, identified in the Offer signature block, has examined the documents listed in the Tender Data and addenda thereto and by submitting this Offer has accepted the Conditions of Tender.

By the representative of the tenderer, deemed to be duly authorised, signing this part of this Form of Offer and Acceptance the tenderer offers to perform all of the obligations and liabilities of the Contractor under the contract including compliance with all its terms and conditions according to their true intent and meaning for an amount to be determined in accordance with the conditions of contract identified in the Contract Data.

| Options A or C | The offered total of the Prices exclusive of VAT is | R [●] |
| --- | --- | --- |
| Option E | The first forecast of the total Defined Cost plus the Fee exclusive of VAT is | R [●] |
|  | Sub total | R [●] |
|  | Value Added Tax @ 15% is | R [●] |
|  | The offered total of the amount due inclusive of VAT is1 | R [●] |
|  | (in words) [●] |  |

This Offer may be accepted by the Employer by signing the Acceptance part of this Form of Offer and Acceptance and returning one copy of this document including the Schedule of Deviations (if any) to the tenderer before the end of the period of validity stated in the Tender Data, or other period as agreed, whereupon the tenderer becomes the party named as the Contractor in the conditions of contract identified in the Contract Data.

| Signature(s) |  |
| --- | --- |
| Name(s) |  |
| Capacity |  |
| For the tenderer: |  |
| (Insert name and address of organisation) |  |
| Name & signature of witness | Date |
| Tenderer’s CIDB registration number: |  |

1 This total is required by the Employer for budgeting purposes only. Actual amounts due will be assessed in terms of the conditions of contract.

Acceptance

By signing this part of this Form of Offer and Acceptance, the Employer identified below accepts the tenderer’s Offer. In consideration thereof, the Employer shall pay the Contractor the amount due in accordance with the conditions of contract identified in the Contract Data. Acceptance of the tenderer’s Offer shall form an agreement between the Employer and the tenderer upon the terms and conditions contained in this agreement and in the contract that is the subject of this agreement.

The terms of the contract, are contained in:

Part C1	Agreements and Contract Data, (which includes this Form of Offer and Acceptance) Part C2	Pricing Data

Part C3	Scope of Work: Service Information

and drawings and documents (or parts thereof), which may be incorporated by reference into the above listed Parts.

Deviations from and amendments to the documents listed in the Tender Data and any addenda thereto listed in the Returnable Schedules as well as any changes to the terms of the Offer agreed by the tenderer and the Employer during this process of offer and acceptance, are contained in the Schedule of Deviations attached to and forming part of this Form of Offer and Acceptance. No amendments to or deviations from said documents are valid unless contained in this Schedule.

The tenderer shall within two weeks of receiving a completed copy of this agreement, including the Schedule of Deviations (if any), contact the Employer’s agent (whose details are given in the Contract Data) to arrange the delivery of any securities, bonds, guarantees, proof of insurance and any other documentation to be provided in terms of the conditions of contract identified in the Contract Data at, or just after, the date this agreement comes into effect. Failure to fulfil any of these obligations in accordance with those terms shall constitute a repudiation of this agreement.

Notwithstanding anything contained herein, this agreement comes into effect on the date when the tenderer receives one fully completed and signed original copy of this document, including the Schedule of Deviations (if any).

| Signature(s) |  |  |  |
| --- | --- | --- | --- |
| Name(s) |  |  |  |
| Capacity |  |  |  |
| for the Employer |  |  |  |
| (Insert name and address of organisation) |  |  |  |
| Name & signature of witness |  |  | Date |

Note: If a tenderer wishes to submit alternative tenders, use another copy of this Form of Offer and Acceptance.

Schedule of Deviations to be completed by the Employer prior to contract award

Note:

- This part of the Offer & Acceptance would not be required if the contract has been developed by negotiation between the Parties and is not the result of a process of competitive tendering.

- The extent of deviations from the tender documents issued by the Employer prior to the tender closing date is limited to those permitted in terms of the Conditions of Tender.

- A tenderer’s covering letter must not be included in the final contract document. Should any matter in such letter, which constitutes a deviatio n as aforesaid be the subject of agreement reached during the process of Offer and Acceptance, the outcome of such agreement shall be recorded here and the final draft of the contract documents shall be revised to incorporate the effect of it.

| No. | Subject | Details |
| --- | --- | --- |
| 1 | None | N/A |

By the duly authorised representatives signing this Schedule of Deviations below, the Employer and the tenderer agree to and accept this Schedule of Deviations as the only deviations from and amendments to the documents listed in the Tender Data and any addenda thereto listed in the Tender Schedules, as well as any confirmation, clarification or changes to the terms of the Offer agreed by the tenderer and the Employer during this process of Offer and Acceptance.

It is expressly agreed that no other matter whether in writing, oral communication or implied during the period between the issue of the tender documents and the receipt by the tenderer of a completed signed copy of this Form shall have any meaning or effect in the contract between the parties arising from this Agreement.

|  | For the tenderer: |  | For the Employer |
| --- | --- | --- | --- |
| Signature |  |  |  |
| Name |  |  |  |
| Capacity |  |  |  |
| On behalf of | (Insert name and address of organisation) |  | (Insert name and address of organisation) |
| Name & signature of witness |  |  |  |
| Date |  |  |  |

C1.2 TSC3 Contract Data

Part one - Data provided by the Employer

#### [Instructions to the contract compiler: (delete these two notes in the final draft of a contract)

- Please read the relevant clauses in the conditions of contract before you enter data. The number of the clause which requires the data is shown in the left hand column for each statement however other clauses may also use the same data.

- Some TSC3 options are always selected by Eskom Holdings SOC Ltd. The remaining TSC3 options are identified by shading in the left hand column. In the event that the option is not required select and delete the whole row. Where the following symbol is used “[●]” - data is required to be inserted relevant to the specific option selected.]

Completion of this data in full, according to the Options chosen, is essential to create a complete contract.

| Clause | Statement | Data |  |
| --- | --- | --- | --- |
| 1 | General |  |  |
| The conditions of contract are the core clauses and the clauses for main Option: |  |  |  |
|  |  | A: | Priced contract with price list |
|  | dispute resolution Option | W1: | Dispute resolution procedure |
|  | and secondary Options |  |  |
|  |  | X1: | Price adjustment for inflation |
|  |  | X2 | Changes in the law |
|  |  | X17: | Low service damages |
|  |  | X19: | Task Order |
|  |  | Z: | Additional conditions of contract |
| of the NEC3 Term Service Contract April 20131 (TSC3) |  |  |  |
| 10.1 | The Employer is (name): | Eskom Holdings SOC Ltd (reg no: 2002/015527/30), a state owned company incorporated in terms of the company laws of the Republic of South Africa |  |
|  | Address | Registered office at Megawatt Park, Maxwell Drive, Sandton, Johannesburg |  |
|  | Tel No. | 014 763 8831 |  |
|  | Fax No. | N/A |  |
| 10.1 | The Service Manager is (name): | Service Manager |  |

1 Available from Engineering Contract Strategies Tel 011 803 3008 Fax 086 539 1902 www.ecs.co.za

|  | Address | Matimba Power Station, Nelson Mandela Drive, Lephalale, Limpopo |
| --- | --- | --- |
|  | Tel | 014 763 8831 |
|  | Fax | N/A |
|  | e-mail | Sehlakgg@eskom.co.za |
| 11.2(2) | The Affected Property is | Matimba Power Station |
| 11.2(13) | The service is | Refurbishment and repairs of MV induction motors for Matimba power station |
| 11.2(14) | The following matters will be included in the Risk Register |  |
|  |  | N/A |
| 11.2(15) | The Service Information is in | Part 3: Scope of Work and all documents and drawings to which it makes reference. |
| 12.2 | The law of the contract is the law of | the Republic of South Africa |
| 13.1 | The language of this contract is | English |
| 13.3 | The period for reply is | Within 12 hours during Emergencies, or 2 working days at any other time. |
| 2 | The Contractor’s main responsibilities | Data required by this section of the core clauses is also provided by the Contractor in Part 2 and terms in italics used in this section are identified elsewhere in this Contract Data |
| 21.1 | The Contractor submits a first plan for acceptance within |  |
|  |  | With Submission of the Task Order Proposal |
| 3 | Time |  |
| 30.1 | The starting date is. | [●] |
| 30.1 | The service period is | [●] |
| 4 | Testing and defects | Refer to ZL15 |
| 5 | Payment |  |
| 50.1 | The assessment interval is | After every delivery’s. |
| 51.1 | The currency of this contract is the | South African Rand |
| 51.2 | The period within which payments are made is |  |
|  |  | 30 days after receipt of Contractors Invoice |
| 51.4 | The interest rate is | the publicly quoted prime rate of interest (calculated on a 365 day year) charged by from time to time by the Standard Bank of South Africa Limited (as certified, in the event of any dispute, by any manager of such bank, whose appointment it shall not be necessary to prove) for amounts due in Rands and (ii) the LIBOR rate applicable at the time for |

|  |  | amounts due in other currencies. LIBOR is the 6 month London Interbank Offered Rate quoted under the caption “Money Rates” in The Wall Street Journal for the applicable currency or if no rate is quoted for the currency in question then the rate for United States Dollars, and if no such rate appears in The Wall Street Journal then the rate as quoted by the Reuters Monitor Money Rates Service (or such service as may replace the Reuters Monitor Money Rates Service) on the due date for the payment in question, adjusted mutatis mutandis every 6 months thereafter (and as certified, in the event of any dispute, by any manager employed in the foreign exchange department of The Standard Bank of South Africa Limited, whose appointment it shall not be necessary to prove. |
| --- | --- | --- |
| 6 | Compensation events | There is no reference to Contract Data in this section of the core clauses and terms in italics used in this section are identified elsewhere in this Contract Data |
| 7 | Use of Equipment Plant and Materials | There is no reference to Contract Data in this section of the core clauses and terms in italics used in this section are identified elsewhere in this Contract Data |
| 8 | Risks and insurance |  |
| 80.1 | These are additional Employer's risks | N/A |
| 83.1 | The minimum amount of cover for insurance against loss and damage caused by the Contractor to the Employer’s property is | the amount of the deductibles in the amount of R 500 000.00 (Five hundred thousand Rand) relevant to the event described in the “Format A” (Annual Construction All Risk Insurance Policy) |
| 83.1 | The insurance against loss of or damage to the works, Plant and Materials is to include cover for Plant and Materials provided by the Employer for an amount of | The total value of the loss |
| 9 | Termination | If either party wishes to terminate the Contractor’s obligation to Provide the Service, he notifies the Service Manager and the other party giving details of his reason for terminating. The Service Manager issues a termination certificate to both Parties promptly if the reason complies with this contract. |
| 10 | Data for main Option clause |  |
| A | Priced contract with price list |  |
| 20.5 | The Contractor prepares forecasts of the final total of the Prices for the whole of the service at intervals no longer than the share ranges are | N/A |
| 11 | Data for Option W1 |  |

|  | W1.1 | The Adjudicator | the person selected from the ICE-SA Division (or its successor body) of the South African Institution of Civil Engineering Panel of Adjudicators by the Party intending to refer a dispute to him. (see www.ice-sa.org.za). If the Parties do not agree on an Adjudicator the Adjudicator will be appointed by the Arbitration Foundation of Southern Africa (AFSA). |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | Address | [●] |  |  |
|  |  | Tel No. | [●] |  |  |
|  |  | Fax No. | [●] |  |  |
|  |  | e-mail | [●] |  |  |
|  | W1.2(3) | The Adjudicator nominating body is: | the Chairman of ICE-SA a joint Division of the South African Institution of Civil Engineering and the Institution of Civil Engineers (London) (see www.ice-sa.org.za ) or its successor body. |  |  |
|  | W1.4(2) | The tribunal is: | arbitration |  |  |
|  | W1.4(5) | The arbitration procedure is | the latest edition of Rules for the Conduct of Arbitrations published by The Association of Arbitrators (Southern Africa) or its successor body. |  |  |
|  |  | The place where arbitration is to be held is | [●] South Africa |  |  |
|  |  | The person or organisation who will choose an arbitrator - if the Parties cannot agree a choice or - if the arbitration procedure does not state who selects an arbitrator, is | the Chairman for the time being or his nominee of the Association of Arbitrators (Southern Africa) or its successor body. |  |  |
|  | 12 | Data for secondary Option clauses |  |  |  |
|  | X1 | Price adjustment for inflation |  |  |  |
|  | X1.1 | The base date for indices is | The prices as per the price list will be fixed & firm for the 1st year of the contract. Escalation will apply on the anniversary of the contract. A "fixed" portion is included in the CPA formula as per the table below. (15%) |  |  |
|  |  | The proportions used to calculate the Price Adjustment Factor are: | Proport ion | linked to index for | Index prepared by |
|  |  |  | 0.05 | Transport | SEIFSA Table L2 |
|  |  |  | 0.25 | Water, Electricity & Gas | SEIFSA Table U (K) |

|  |  | 0.30 | Labour |  |  | SEIFSA Table C3 |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | 0.10 | Copper |  |  | SEIFSA Table F |
|  |  | 0.15 | Mechanical Engineering |  |  | SEIFSA Table G |
|  |  | 0.15 | non-adjustable |  |  |  |
|  |  | 1.00 |  |  |  |  |
| X2 | Changes in the law | As per the terms and conditions on X2 of NEC3 TSC. |  |  |  |  |
| X17 | Low service damages |  |  |  |  |  |
| X17.1 | The service level table is in | Service level table Description Penalty Motor rework R nil/overtime Poor workmanship Contractor to carry corrective cost Compliance to SOW R1000 p/day overdue schedule as per agreed schedule. The penalty for the late response will be R1000 per day to a maximum of 10% of the task order for the normal breakdown applicable to MV Motor Motor failure under Contractor to carry warranty corrective cost Motor comply with Contractor to carry customer corrective cost specification Emergency Work on 24hrs basis The penalty for the on agreed schedule late response will be R1000 per day to a maximum of 10% of the task order for the normal breakdown applicable to MV Motor. |  |  |  |  |
| X19 | Task Order |  |  |  |  |  |
| X19.5 | The Contractor submits a Task Order programme to the Service Manager within |  |  |  |  |  |
|  |  | 03 days of receiving the Task Order |  |  |  |  |
| Z | The additional conditions of contract are |  |  |  |  |  |
|  |  | Z1 to Z14 always apply |  | . |  |  |
| Z1 | Cession delegation and assignment |  |  |  |  |  |

| Z1.1 | The Contractor does not cede, delegate or assign any of its rights or obligations to any person without the written consent of the Employer. |
| --- | --- |
| Z1.2 | Notwithstanding the above, the Employer may on written notice to the Contractor cede and delegate its rights and obligations under this contract to any of its subsidiaries or any of its present divisions or operations which may be converted into separate legal entities as a result of the restructuring of the Electricity Supply Industry. |
| Z2 | Joint ventures |
| Z2.1 | If the Contractor constitutes a joint venture, consortium or other unincorporated grouping of two or more persons or organisations then these persons or organisations are deemed to be jointly and severally liable to the Employer for the performance of this contract. |
| Z2.2 | Unless already notified to the Employer, the persons or organisations notify the Service Manager within two weeks of the Contract Date of the key person who has the authority to bind the Contractor on their behalf. |
| Z2.3 | The Contractor does not alter the composition of the joint venture, consortium or other unincorporated grouping of two or more persons without the consent of the Employer having been given to the Contractor in writing. |
| Z3 | Change of Broad Based Black Economic Empowerment (B-BBEE) status |
| Z3.1 | Where a change in the Contractor’s legal status, ownership or any other change to his business composition or business dealings results in a change to the Contractor’s B-BBEE status, the Contractor notifies the Employer within seven days of the change. |
| Z3.2 | The Contractor is required to submit an updated verification certificate and necessary supporting documentation confirming the change in his B-BBEE status to the Service Manager within thirty days of the notification or as otherwise instructed by the Service Manager. |
| Z3.3 | Where, as a result, the Contractor’s B-BBEE status has decreased since the Contract Date the Employer may either re-negotiate this contract or alternatively, terminate the Contractor’s obligation to Provide the Service. |
| Z3.4 | Failure by the Contractor to notify the Employer of a change in its B-BBEE status may constitute a reason for termination. If the Employer terminates in terms of this clause, the procedures on termination are P1, P2 and P4 as stated in clause 92, and the amount due is A1 and A3 as stated in clause 93. |
| Z4 | Confidentiality |
| Z4.1 | The Contractor does not disclose or make any information arising from or in connection with this contract available to Others. This undertaking does not, however, apply to information which at the time of disclosure or thereafter, without default on the part of the Contractor, enters the public domain or to information which was already in the possession of the Contractor at the time of disclosure (evidenced by written records in existence at that time). Should the Contractor disclose information to Others in terms of clause 25.1, the Contractor ensures that the provisions of this clause are complied with by the recipient. |
| Z4.2 | If the Contractor is uncertain about whether any such information is confidential, it is to be regarded as such until notified otherwise by the Service Manager. |
| Z4.3 | In the event that the Contractor is, at any time, required by law to disclose any such information which is required to be kept confidential, the Contractor, to the extent permitted by law prior to disclosure, notifies the Employer so that an appropriate protection order and/or any other action can be taken if possible, prior to any disclosure. In the event that such protective order is not, |

|  | or cannot, be obtained, then the Contractor may disclose that portion of the information which it is required to be disclosed by law and uses reasonable efforts to obtain assurances that confidential treatment will be afforded to the information so disclosed. |
| --- | --- |
| Z4.4 | The taking of images (whether photographs, video footage or otherwise) of the Affected Property or any portion thereof, in the course of Providing the Service and after the end of the service period, requires the prior written consent of the Service Manager. All rights in and to all such images vests exclusively in the Employer. |
| Z4.5 | The Contractor ensures that all his subcontractors abide by the undertakings in this clause. |
| Z5 | Waiver and estoppel: Add to core clause 12.3: |
| Z5.1 | Any extension, concession, waiver or relaxation of any action stated in this contract by the Parties, the Service Manager or the Adjudicator does not constitute a waiver of rights, and does not give rise to an estoppel unless the Parties agree otherwise and confirm such agreement in writing. |
| Z6 | Health, safety and the environment: Add to core clause 27.4 |
| Z6.1 | The Contractor undertakes to take all reasonable precautions to maintain the health and safety of persons in and about the execution of the service. Without limitation the Contractor: - accepts that the Employer may appoint him as the “Principal Contractor” (as defined and provided for under the Construction Regulations 2014 (promulgated under the Occupational Health & Safety Act 85 of 1993) (“the Construction Regulations”) for the Affected Property; - warrants that the total of the Prices as at the Contract Date includes a sufficient amount for proper compliance with the Construction Regulations, all applicable health & safety laws and regulations and the health and safety rules, guidelines and procedures provided for in this contract and generally for the proper maintenance of health & safety in and about the execution of the service; and - undertakes, in and about the execution of the service, to comply with the Construction Regulations and with all applicable health & safety laws and regulations and rules, guidelines and procedures otherwise provided for under this contract and ensures that his Subcontractors, employees and others under the Contractor’s direction and control, likewise observe and comply with the foregoing. |
| Z6.2 | The Contractor, in and about the execution of the service, complies with all applicable environmental laws and regulations and rules, guidelines and procedures otherwise provided for under this contract and ensures that his Subcontractors, employees and others under the Contractor’s direction and control, likewise observe and comply with the foregoing. |
| Z7 | Provision of a Tax Invoice and interest. Add to core clause 51 |
| Z7.1 | Within one week of receiving a payment certificate from the Service Manager in terms of core clause 51.1, the Contractor provides the Employer with a tax invoice in accordance with the Employer's procedures stated in the Service Information, showing the amount due for payment equal to that stated in the payment certificate. |
| Z7.2 | If the Contractor does not provide a tax invoice in the form and by the time required by this contract, the time by when the Employer is to make a payment is extended by a period equal in time to the delayed submission of the correct tax invoice. Interest due by the Employer in terms of core clause 51.2 is then calculated from the delayed date by when payment is to be made. |
| Z7.3 | The Contractor (if registered in South Africa in terms of the companies Act) is required to comply with the requirements of the Value Added Tax Act, no 89 of 1991 (as amended) and to include the Employer’s VAT number 4740101508 on each invoice he submits for payment. |

| Z8 | Notifying compensation events |  |
| --- | --- | --- |
| Z8.1 | Delete the last paragraph of core clause 61.3 and replace with: If the Contractor does not notify a compensation event within eight weeks of becoming aware of the event, he is not entitled to a change in the Prices. |  |
| Z9 | Employer’s limitation of liability |  |
| Z9.1 | The Employer’s liability to the Contractor for the Contractor’s indirect or consequential loss is limited to R0.00 (zero Rand) |  |
| Z9.2 | The Contractor’s entitlement under the indemnity in 82.1 is provided for in 60.1(12) and the Employer’s liability under the indemnity is limited to compensation as provided for in core clause 63 and X19.11 if Option X19 Task Order applies to this contract. |  |
| Z10 | Termination: Add to core clause 91.1, at the second main bullet point, fourth sub-bullet point, after the words "against it": |  |
| Z10.1 | or had a business rescue order granted against it. |  |
| Z11 | Ethics |  |
| For the purposes of this Z-clause, the following definitions apply: |  |  |
| Affected Party |  | means, as the context requires, any party, irrespective of whether it is the Contractor or a third party, such party’s employees, agents, or Subcontractors or Subcontractor’s employees, or any one or more of all of these parties’ relatives or friends, |
| Coercive Action |  | means to harm or threaten to harm, directly or indirectly, an Affected Party or the property of an Affected Party, or to otherwise influence or attempt to influence an Affected Party to act unlawfully or illegally, |
| Collusive Action |  | means where two or more parties co-operate to achieve an unlawful or illegal purpose, including to influence an Affected Party to act unlawfully or illegally, |
| Committing Party |  | means, as the context requires, the Contractor, or any member thereof in the case of a joint venture, or its employees, agents, or Subcontractors or the Subcontractor’s employees, |
| Corrupt Action |  | means the offering, giving, taking, or soliciting, directly or indirectly, of a good or service to unlawfully or illegally influence the actions of an Affected Party, |
| Fraudulent Action |  | means any unlawfully or illegally intentional act or omission that misleads, or attempts to mislead, an Affected Party, in order to obtain a financial or other benefit or to avoid an obligation or incurring an obligation, |
| Obstructive Action |  | means a Committing Party unlawfully or illegally destroying, falsifying, altering or concealing information or making false statements to materially impede an investigation into allegations of Prohibited Action, and |
| Prohibited Action |  | means any one or more of a Coercive Action, Collusive Action Corrupt Action, Fraudulent Action or Obstructive Action. |
| Z11.1 | A Committing Party may not take any Prohibited Action during the course of the procurement of this contract or in execution thereof. |  |

| Z11.2 | The Employer may terminate the Contractor’s obligation to Provide the Services if a Committing Party has taken such Prohibited Action and the Contractor did not take timely and appropriate action to prevent or remedy the situation, without limiting any other rights or remedies the Employer has. It is not required that the Committing Party had to have been found guilty, in court or in any other similar process, of such Prohibited Action before the Employer can terminate the Contractor’s obligation to Provide the Services for this reason. |
| --- | --- |
| Z11.3 | If the Employer terminates the Contractor’s obligation to Provide the Services for this reason, the amounts due on termination are those intended in core clauses 92.1 and 92.2. |
| Z11.4 | A Committing Party co-operates fully with any investigation pursuant to alleged Prohibited Action. Where the Employer does not have a contractual bond with the Committing Party, the Contractor ensures that the Committing Party co-operates fully with an investigation. |

#### Z12	Insurance

Z _12_.1	Replace core clause 83 with the following:

#### Insurance cover

#### 83

  - When requested by a Party, the other Party provides certificates from his insurer or broker stating that the insurances required by this contract are in force.

  - The Contractor provides the insurances stated in the Insurance Table A from the starting date until the earlier of Completion and the date of the termination certificate.

ESKOM IS RESPONSIBLE FOR ENSURING ITS OWN ASSETS, INTERCAL ONLY PROVIDES PUBLIC LIABILITY INSURANCE INFORMATION.

#### INSURANCE TABLE A

| Insurance against | Minimum amount of cover or minimum limit of indemnity |
| --- | --- |
| Loss of or damage caused by the Contractor to the Employer’s property | The replacement cost where not covered by the Employer’s insurance. The Employer’s policy deductible as at Contract Date, where covered by the Employer’s insurance. |
| Loss of or damage to Plant and Materials | The replacement cost where not covered by the Employer’s insurance. The Employer’s policy deductible as at Contract Date, where covered by the Employer’s insurance. |
| Loss of or damage to Equipment | The replacement cost where not covered by the Employer’s insurance. The Employer’s policy deductible as at Contract Date, where covered by the Employer’s insurance. |
| The Contractor’s liability for loss of or damage to property (except the Employer’s property, Plant and Materials and Equipment) and liability for bodily injury to or death of a person (not an employee of the Contractor) arising from or in connection with the Contractor’s Providing the Service | Loss of or damage to property The replacement cost Bodily injury to or death of a person The amount required by the applicable law. |
| Liability for death of or bodily injury to employees of the Contractor arising out of and in the course of their employment in connection with this contract | The amount required by the applicable law |

Z	12.2	Replace core clause 86 with the following:

Insurance by the Employer

86

86.1	The Employer provides the insurances stated in the Insurance Table B

#### INSURANCE TABLE B

| Insurance against or name of policy | Minimum amount of cover or minimum li of indemnity |
| --- | --- |
| Assets All Risk | Per the insurance policy document |
| Contract Works insurance | Per the insurance policy document |
| Environmental Liability | Per the insurance policy document |
| General and Public Liability | Per the insurance policy document |
| Transportation (Marine) | Per the insurance policy document |
| Motor Fleet and Mobile Plant | Per the insurance policy document |
| Terrorism | Per the insurance policy document |
| Cyber Liability | Per the insurance policy document |
| Nuclear Material Damage and Business Interruption | Per the insurance policy document |
| Nuclear Material Damage Terrorism | Per the insurance policy document |

| Z13 | Nuclear Liability |
| --- | --- |
| Z13.1 | The Employer is the operator of the Koeberg Nuclear Power Station (KNPS), a nuclear installation, as designated by the National Nuclear Regulator of the Republic of South Africa, and is the holder of a nuclear licence in respect of the KNPS. |
| Z13.2 | The Employer is solely responsible for and indemnifies the Contractor or any other person against any and all liabilities which the Contractor or any person may incur arising out of or resulting from nuclear damage, as defined in Act 47 of 1999, save to the extent that any liabilities are incurred due to the unlawful intent of the Contractor or any other person or the presence of the Contractor or that person or any property of the Contractor or such person at or in the KNPS or on the KNPS |

| site, without the permission of the Employer or of a person acting on behalf of the Employer. |  |  |
| --- | --- | --- |
| Z13.3 | Subject to clause Z13.4 below, the Employer waives all rights of recourse, arising from the aforesaid, save to the extent that any claims arise or liability is incurred due or attributable to the unlawful intent of the Contractor or any other person, or the presence of the Contractor or that person or any property of the Contractor or such person at or in the KNPS or on the KNPS site, without the permission of the Employer or of a person acting on behalf of the Employer. |  |
| Z13.4 | The Employer does not waive its rights provided for in section 30 (7) of Act 47 of 1999, or any replacement section dealing with the same subject matter. |  |
| Z13.5 | The protection afforded by the provisions hereof shall be in effect until the KNPS is decommissioned. |  |
| Z14 | Asbestos |  |
| For the purposes of this Z-clause, the following definitions apply: |  |  |
| AAIA |  | means approved asbestos inspection authority. |
| ACM |  | means asbestos containing materials. |
| AL |  | means action level, i.e. a level of 50% of the OEL, i.e. 0.1 regulated asbestos fibres per ml of air measured over a 4 hour period. The value at which proactive actions is required in order to control asbestos exposure to prevent exceeding the OEL. |
| Ambient Air |  | means breathable air in area of work with specific reference to breathing zone, which is defined to be a virtual area within a radius of approximately 30cm from the nose inlet. |
| Compliance Monitoring |  | means compliance sampling used to assess whether or not the personal exposure of workers to regulated asbestos fibres is in compliance with the Standard’s requirements for safe processing, handling, storing, disposal and phase-out of asbestos and asbestos containing material, equipment and articles. |
| OEL |  | means occupational exposure limit. |
| Parallel Measurements |  | means measurements performed in parallel, yet separately, to existing measurements to verify validity of results. |
| Safe Levels |  | means airborne asbestos exposure levels conforming to the Standard’s requirements for safe processing, handling, storing, disposal and phase-out of asbestos and asbestos containing material, equipment and articles. |
| Standard |  | means the Employer’s Asbestos Standard 32-303: Requirements for Safe Processing, Handling, Storing, Disposal and Phase-out of Asbestos and Asbestos Containing Material, Equipment and Articles. |
| SANAS |  | means the South African National Accreditation System. |
| TWA |  | means the average exposure, within a given workplace, to airborne asbestos fibres, normalised to the baseline of a 4 hour continuous period, also applicable to short term exposures, i.e. 10-minute TWA. |
| Z14.1 | The Employer ensures that the Ambient Air in the area where the Contractor will Provide the Services conforms to the acceptable prescribed South African standard for asbestos, as per the regulations published in GNR 155 of 10 February 2002, under the Occupational Health and Safety Act, 1993 (Act 85 of 1993) (“Asbestos Regulations”). The OEL for asbestos is 0.2 regulated asbestos fibres per millilitre of air as a 4-hour TWA, averaged over any continuous period of four hours, and the short term exposure limit of 0.6 regulated asbestos fibres per millilitre of air as a 10- |  |

|  | minute TWA, averaged over any 10 minutes, measured in accordance with HSG248 and monitored according to HSG173 and OESSM. |
| --- | --- |
| Z14.2 | Upon written request by the Contractor, the Employer certifies that these conditions prevail. All measurements and reporting are effected by an independent, competent, and certified occupational hygiene inspection body, i.e. a SANAS accredited and Department of Employment and Labour approved AAIA. The Contractor may perform Parallel Measurements and related control measures at the Contractor’s expense. For the purposes of compliance the results generated from Parallel Measurements are evaluated only against South African statutory limits as detailed in clause Z14.1. Control measures conform to the requirements stipulated in the AAIA- approved asbestos work plan. |
| Z14.3 | The Employer manages asbestos and ACM according to the Standard. |
| Z14.4 | In the event that any asbestos is identified while Providing the Services, a risk assessment is conducted and if so required, with reference to possible exposure to an airborne concentration of above the AL for asbestos, immediate control measures are implemented and relevant air monitoring conducted in order to declare the area safe. |
| Z14.5 | The Contractor’s personnel are entitled to stop working and leave the contaminated area forthwith until such time that the area of concern is declared safe by either Compliance Monitoring or an AAIA approved control measure intervention, for example, per the emergency asbestos work plan, if applicable. |
| Z14.6 | The Contractor continues to Provide the Services, without additional control measures presented, on presentation of Safe Levels. The contractually agreed dates to Provide the Services, including the Completion Date, are adjusted accordingly. The contractually agreed dates are extended by the notification periods required by regulations 3 and 21 of the Asbestos Regulations, 2001. |
| Z14.7 | Any removal and disposal of asbestos, asbestos containing materials and waste, is done by a registered asbestos contractor, instructed by the Employer at the Employer’s expense, and conducted in line with South African legislation. |
| Z15 | Provision of a Tax Invoice and interest. Add to core clause 51 |
| Z15.1 | The warrantee period is 12 months after completion of each task order. |
| Z15.2 | The Defects correction period is the period during which the Contractor undertakes to repair the Defect. The period for repair of a Defect shall be determined by the nature of the Defect and shall be such period as is reasonable in the circumstances. |
| Z15.3 | The defective Service will be inspected by both the Service Manager and Contractor and a decision made as to how the defective services are to be corrected. Any decision made will be agreed in writing. |

C1.2 Contract Data

Part two - Data provided by the Contractor

Completion of the data in full, according to Options chosen, is essential to create a complete contract.

| Clause | Statement | Data |
| --- | --- | --- |
| 10.1 | The Contractor is (Name): |  |
|  | Address |  |
|  | Tel No. |  |
|  | Fax No. |  |
| 11.2(8) | The direct fee percentage is | % |
|  | The subcontracted fee percentage is | % |
| 11.2(14) | The following matters will be included in the Risk Register |  |
| 11.2(15) | The Service Information for the Contractor’s plan is in: |  |
| 21.1 | The plan identified in the Contract Data is contained in: |  |
| 24.1 | The key people are: |  |
|  | 1 Name: |  |
|  | Job: |  |
|  | Responsibilities: |  |
|  | Qualifications: |  |
|  | Experience: |  |
|  | 2 Name: |  |
|  | Job |  |
|  | Responsibilities: |  |
|  | Qualifications: |  |
|  | Experience: |  |
|  |  | CV's (and further key person's data including CVs) are in . |
| A | Priced contract with price list |  |
| 11.2(12) | The price list is in C2.2 |  |
| 11.2(19) | The tendered total of the Prices is | R |

| C | Target contract with price list |  |
| --- | --- | --- |
| 11.2(12) | The price list is in |  |
| 11.2(20) | The tendered total of the Prices is | R |
| E | Cost reimbursable contract |  |
| 11.2(12) | The price list is in |  |

# PART 2: PRICING DATA

### TSC3 Option A

| Document reference | Title | No of pages |
| --- | --- | --- |
| C2.1 | Pricing assumptions: Option A | 2 |
| C2.2 | The price list | [●] |

C2.1 Pricing assumptions: Option A

- How work is priced and assessed for payment

Clause 11 in NEC3 Term Service Contract (TSC3) core clauses and Option A states:

| Identified and defined terms | 11 11.2 | (12) The Price List is the price list unless later changed in accordance with this contract. |
| --- | --- | --- |
|  |  | (17) The Price for Services Provided to Date is the total of - the Price for each lump sum item in the Price List which the Contractor has completed and - where a quantity is stated for an item in the Price List, an amount calculated by multiplying the quantity which the Contractor has completed by the rate. |
|  |  | (19) The Prices are the amounts stated in the Price column of the Price List. Where a quantity is stated for an item in the Price List, the Price is calculated by multiplying the quantity by the rate. |

This confirms that Option A is a priced contract where the Prices are derived from a list of items of service which can be priced as lump sums or as expected quantities of service multiplied by a rate or a mix of both.

### Function of the Price List

Clause 54.1 in Option A states: “Information in the Price List is not Service Information”. This confirms that instructions to do work or how it is to be done are not included in the Price List but in the Service Information. This is further confirmed by Clause 20.1 which states, “The Contractor Provides the Service in accordance with the Service Information”. Hence the Contractor does not Provide the Service in accordance with the Price List. The Price List is only a pricing document.

- Link to the Contractor’s plan

Clause 21.4 states “The Contractor provides information which shows how each item description on the Price List relates to the operations on each plan which he submits for acceptance”. Hence when compiling the price list, the tendering contractor needs to develop his first clause 21.2 plan in such a way that operations shown on it can be priced in the price list and result in a satisfactory cash flow in terms of clause 11.2(17).

- Preparing the price list

Before preparing the price list, both the Employer and tendering contractors should read the TSC3 Guidance Notes pages 14 and 15. In an Option A contract, either Party may have entered items into the price list either as a process of offer and acceptance (tendering) or by negotiation depending on the nature of the service to be provided. Alternatively the Employer, in his Instructions to Tenderers or in a Tender Schedule, may have listed some items that he requires the Contractor to include in the price list to be prepared and priced by him.

It is assumed that in preparing or finalising the price list the Contractor:

  - Has taken account of the guidance given in the TSC3 Guidance Notes relevant to Option A;

  - Understands the function of the Price List and how work is priced and paid for;

  - Is aware of the need to link operations shown in his plan to items shown in the Price List;

  - Has listed and priced items in the price list which are inclusive of everything necessary and incidental to Providing the Service in accordance with the Service Information, as it was at the time of tender, as well as correct any Defects not caused by an Employer’s risk;

  - Has priced work he decides not to show as a separate item within the Prices or rates of other listed items in order to fulfil the obligation to complete the service for the tendered total of the Prices.

  - Understands there is no adjustment to items priced as lump sums if the amount, or quantity, of work within that item later turns out to be different to that which the Contractor estimated at time of tender. The only basis for a change to the (lump sum) Prices is as a result of a compensation event.

  - Format of the price list

(From the example given in an Appendix within the TSC3 Guidance Notes)

Entries in the first four columns in the price list in section C2.2 are made either by the Employer or the tendering contractor.

If the Contractor is to be paid an amount for the item which is not adjusted if the quantity of work in the item changes, the tendering contractor enters the amount in the Price column only, the Unit, Expected Quantity and Rate columns being left blank.

If the Contractor is to be paid an amount for an item of work which is the rate for the work multiplied by the quantity completed, the tendering contractor enters the rate which is then multiplied by the Expected Quantity to produce the Price, which is also entered.

If the Contractor is to be paid a Price for an item proportional to the length of time for which a service is provided, a unit of time is stated in the Unit column and the expected length of time (as a quantity of the stated units of time) is stated in the Expected Quantity column.

C2.2 the price list

    - ID FAN MOTOR 3270kW

| Item No | Description |
| --- | --- |
|  | GENERAL |
| 1 | Collect motor from Matimba Power Station |
| 2 | Deliver motor to Matimba Power Station |
| 3 | Open motor, clean and complete assessment report |
| 4 | Assemble motor |
| 5 | Paint complete motor |
|  | TERMINAL BOX AND LEADS |
| 1 | Replace leads |
| 2 | Replace terminal box studs |
| 3 | Supply and replace box gaskets and seals |
| 4 | Replace current Electric CT |
|  | HEAT EXCHANGER |
| 1 | Remove oil from cooler tubes (clean with solvent) |
| 2 | Replace damping rubbers |
| 3 | Overhaul the heat exchanger / radiator |
| 4 | Replace broken cooler tubes/radiator |
| 5 | Pressure test the coolers tubes/radiator |
| 6 | Replace gaskets and seals |
|  | SPACE HEATERS |
| 1 | Test heaters |
| 2 | Replace heaters |
| 3 | Overhaul heaters (Replace wiring) |
|  | STATOR HOUSING |
| 1 | Polish stator foot mounting |
| 2 | Clean and dry stator |
| 3 | Treat and paint stator with anti-rust paint |
| 4 | Check the concentricity of the stator |
| 5 | Rectify or correct the stator concentricity |
| 6 | Replace tail leads (including terminal box and leads) |
| 7 | Reinsulate tail leads |
|  | ROTOR |
| 1 | Treat and paint rotor with anti-rust paint |
| 2 | Balance rotor at operating speed with fan and half key inserted |
| 3 | Polish the journals (NDE) |
| 4 | Polish the journals (DE) |
| 5 | Polish seal landings (NDE) |
| 6 | Polish seal landings (DE) |
| 7 | Polish fan landing (DE) |

| Item No | Description |
| --- | --- |
| 8 | Polish fan landing (NDE) |
| 9 | Check shaft run out / concentricity |
| 10 | Rectify or correct the rotor concentricity |
| 11 | Micro welding rotor shaft (DE) |
| 12 | Micro welding rotor shaft (NDE) |
| 13 | Brazing of rotor end laminations |
| 14 | Fit new mag center indicator |
|  | RESISTANCE TEMPERATURE DETECTOR |
| 1 | PT100 resistance test/ measure RTD |
| 2 | Install PT100 on the overhang winding (2 per phase, 6 in total) |
|  | DE SHIELD/NDE SHIELD |
| 1 | Replace fixing bolts |
|  | WHITE METAL BEARINGS |
| 1 | Re-metal white metal DE bearing |
| 2 | Re-metal white metal NDE bearing |
| 3 | Refurbish DE bearing housing to fit standard bearing refurbishment specifications |
| 4 | Refurbish NDE bearing housing to fit standard bearing refurbishment specifications |
| 5 | Overhaul DE seal |
| 6 | Overhaul NDE seal |
| 7 | Replace site glass and clean ports |
| 8 | Replace seals |
| 9 | Bearing insulation test point inspect and repair (Inspect specifically for test point housing insulation damage) |
| 10 | Replace bearing (see nameplate data supplied on SOW for this motor) |
| 11 | Inspect bearing housing (Assess the bearing housing, bearing seating surfaces for wear/damage) |
|  | ACCESSORIES |
| 1 | Fit new internal fans as and when required |
| 2 | Inspect shock absorber rubbers (replace if damaged) |
| 3 | Fit new floating lab seals |
| 4 | Supply new sight glasses |
| 5 | Supply new breathers |
| 6 | Supply new pipe work and ball valves |
| 7 | Fit new set of O-rings |
| 8 | Shotblast, clean and paint the housings |
| 9 | Repair journals and landings |
| 10 | Burn out stator, remove coils and prepare core for rewind |
| 11 | Manufacture new stator coil and insulation rewind kit |
| 12 | Install the new winding kit, VPI and curing |
| 13 | Overhaul air to air canopy |
| 14 | Replace connector blocks |
| 15 | Supply and fit new insulators-triangle type |
| 16 | Skim Stator Feet |
| 17 | Re-tap Mounting Holes |

| Item No | Description |
| --- | --- |
| 18 | Re-tap Holes & Fit New Jacking Bolts |
| 19 | Micro-weld & machine NDE/DE outer seal landing 270 X 90 / 340 X 135 |
| 20 | Micro-weld & machine NDE/DE inner seal landing 270 X 70 / 340 X 123 |
| 21 | Micro-weld & machine NDE/DE inner seal landing 270 X 50 / 340 X 123 |
| 22 | Fit new earth lugs |
| 23 | Clean & polish spigots |
| 24 | Fit new earth brush & holder |
| 25 | Fit new Zorc |
| 26 | Manufacture new rotor core |
| 27 | Remove old rotor core & fit new |
| 28 | Machine off-rotor end rings & remove rotor bars |
| 29 | Manufacture new rotor end rings & bars |
| 30 | Re-bar rotor complete |
| 31 | Fit new bearing probes DE & NDE |
| 32 | Repair oil rings & fit new screws |
| 33 | Repair bearing housing nips |
| 34 | Re-sleeve vacuum seals |
| 35 | Light line bore stator core |
| 36 | Skim rotor core |
| 37 | Supply & fit new earth brush & holder 2 off |
| 38 | Supply & fit new insulated rings |
| 39 | Repair bearing housing nips |
| 40 | Replace missing wedges & epoxy |
| 41 | Machine DE bearing journal radius |
| 42 | Light machine DE outer seal landing |
| 43 | Overhaul desicator |
| 44 | Fit new insulated rings & final machine OD |
| 45 | Chemical clean 2 off cooler bundles |
| 46 | Supply stainless steel bolts |
| 47 | Pressure test after repair |
| 48 | Replace 2 off missing stator wedges & epoxy |
| 49 | Re-tap all mounting holes |
| 50 | Manufacture new interlock dust seal carrier |
| 51 | Re-insulated bearing OD & final machine |
| 52 | Manufacture new DE outer seal sleeve |
| 53 | Supply & fit new earth brush & holder |
| 54 | Replace stator jacking bolts |
| 55 | Supply new vibration blocks |
| 56 | Supply & fit new bearing temperature |
| 57 | Repair bearing nips |
| 58 | Fit new pipe work & ball valves |
| 59 | Fit new magnetic wedges & blocks |
| 60 | Replace current Electric CT’s 3 off |
| 61 | Install current Electric CT’s 3 off (Free issue) |
|  | ROUTINE TESTS AND TEST AS AND WHEN REQUIRED |
| 1 | Measure and record winding resistance test |

| Item No | Description |
| --- | --- |
| 2 | Perform and record insulation resistance test |
| 3 | Perform and record polarization test |
| 4 | Perform and record Tan Delta test |
| 5 | Perform and record off-line partial discharge test |
| 6 | Perform wedge tightness test on stator |
| 7 | Perform induction test |
| 8 | Perform stator ELCID test on rotor |
| 9 | Perform rotor core ELCID test |
| 10 | NDT on the rotor shaft |
| 11 | NDT on fan impellers or runners (Whole impeller) |
| 12 | Perform rotor bar to bar test (consider the number of bars per rotor) |
| 13 | Ultrasonic testing on white metal bearing surface |
| 14 | High voltage AC test |
| 15 | Balancing test |
| 16 | Copper material analysis test /check |
| 17 | Bearing insulation test |
| 18 | Bearing heat run test and check the bearing temperatures and vibration |
| 19 | Stator winding temperature measurements |
| 20 | Load test the motor and check efficiency |

#### FD FAN MOTOR 2310kW

| Item No | Description |
| --- | --- |
|  | GENERAL |
| 1 | Collect motor from Matimba Power Station |
| 2 | Deliver motor to Matimba Power Station |
| 3 | Open motor, clean and complete assessment report |
| 4 | Assemble motor |
| 5 | Paint complete motor |
|  | TERMINAL BOX AND LEADS |
| 1 | Replace leads |
| 2 | Replace terminal box studs |
| 3 | Supply and replace box gaskets and seals |
| 4 | Replace current Electric CT |
|  | HEAT EXCHANGER |
| 1 | Remove oil from cooler tubes (clean with solvent) |
| 2 | Replace damping rubbers |
| 3 | Overhaul the heat exchanger / radiator |
| 4 | Replace broken cooler tubes |
| 5 | Pressure test the coolers tubes / radiator |
| 6 | Replace gaskets and seals |
|  | SPACE HEATERS |
| 1 | Test heaters |
| 2 | Overhaul heaters (replace wiring) |
| 3 | Replace heaters |

| Item No | Description |
| --- | --- |
|  | STATOR HOUSING |
| 1 | Polish stator foot mounting |
| 2 | Clean and dry stator |
| 3 | Treat and paint stator with anti-rust paint |
| 4 | Check the concentricity of the stator |
| 5 | Rectify or correct the stator concentricity |
| 6 | Replace tail leads (including terminal box and leads) |
| 7 | Reinsulate tail leads |
|  | ROTOR |
| 1 | Treat and paint rotor with anti-rust paint |
| 2 | Balance rotor at operating speed with fan and half key inserted |
| 3 | Polish the journals (NDE) |
| 4 | Polish the journals (DE) |
| 5 | Polish seal landings (NDE) |
| 6 | Polish seal landings (DE) |
| 7 | Polish fan landing (DE) |
| 8 | Polish fan landing (NDE) |
| 9 | Check shaft run out / concentricity |
| 10 | Rectify or correct the rotor concentricity |
| 11 | Micro welding rotor shaft (DE) |
| 12 | Micro welding rotor shaft (NDE) |
| 13 | Brazing of rotor end laminations |
| 14 | Supply new earth brushes |
| 15 | Fit new mag centre indicator |
|  | RESISTANCE TEMPERATURE DETECTOR |
| 1 | PT100 resistance test/measure RTD |
| 2 | Install PT100 on the overhang winding (2 per phase, 6 in total) |
|  | DE SHIELD/ NDE SHIELD |
| 1 | Replace fixing bolts |
|  | WHITE METAL BEARINGS |
| 1 | Re-metal white DE metal bearing |
| 2 | Re-metal white NDE metal bearing |
| 3 | Refurbishment DE bearing housing to fit standard bearing refurbishment specifications |
| 4 | Refurbishment NDE bearing housing to fit standard bearing refurbishment specifications |
| 5 | Overhaul DE seal |
| 6 | Overhaul NDE seal |
| 7 | Replace site glass and clean ports |
| 8 | Replace seals |
| 9 | Bearing insulation test point inspect and repair (Inspect specifically for test point housing insulation damage) |
| 10 | Replace bearing (see nameplate data supplied on SOW for this motor) |
| 11 | Inspect bearing housing |
|  | ACCESSORIES |

| Item No | Description |
| --- | --- |
| 1 | Replace stator jacking bolts |
| 2 | Supply and fit new DE bearing |
| 3 | Conduct stator core flux and watts loss test |
| 4 | Rewind stator complete fit new magnetic wedges and blocks |
| 5 | VPI stator, cure, fit new stator leads and PT100’s |
| 6 | Open keyway, check run out, pre-machine coupling journal |
| 7 | Pre-machine DE and NDE outer and inner seal landings and bearing journals |
| 8 | Re-cut keyway, final grind journals |
| 9 | Supply new external fan |
| 10 | Skim stator feet |
| 11 | Supply new desiccators |
| 12 | Re-insulate bearing OD |
| 13 | Repair bearing nips |
| 14 | Repair stator core (vibrate stator core to remove hot spots) |
| 15 | New internal fans |
| 16 | Inspect shock absorber rubbers (replace if damaged) |
| 17 | Supply new earth brushes |
| 18 | Supply new vibration blocks |
| 19 | Fit new floating lab seals |
| 20 | Supply new sight glasses |
| 21 | Supply new breathers |
| 22 | Fit new pipe work and ball valves |
| 23 | Fit new set of O-rings |
| 24 | Shotblast, clean and paints the housings |
| 25 | Repair journals and landings |
| 26 | Burn out stator, remove coils and prepare core for rewind |
| 27 | Manufacture new stator coil and insulation rewind kit |
| 28 | Install the new winding kit, VPI and curing |
| 29 | Overhaul air to air canopy |
| 30 | Replace connector blocks |
| 31 | Supply and fit new insulators-triangular type |
| 32 | Test stator, QC and paint |
| 33 | Modify terminal boxes on request |
| 34 | Extend supply leads on request |
| 35 | Fit new gaskets bolts |
| 36 | Touch up paint work and routine test |
| 37 | Supply & fit new bearing probes DE & NDE |
| 38 | Fit new earth lugs |

| Item No | Description |
| --- | --- |
| 39 | Replace missing stator wedges & epoxy |
| 40 | Panel beat radiator cover |
| 41 | Manufacture new DE/NDE inner/outer seal sleeve in different sizes |
| 42 | Microweld & machine DE/NDE coupling landing in different sizes |
| 43 | Microweld & machine DE/NDE inner seal landing in different sizes |
| 44 | Fit new high jacking pies & inlet pipes |
| 45 | Machine housings for oil jacking pipes |
| 46 | Remove terminal boxes, main & star |
| 47 | Supply & fit new main & star side leads & re-solder lugs |
| 48 | Re-fit terminal boxes, main & star |
| 49 | Re-tap all mounting holes |
| 50 | Replace missing wedges & epoxy |
| 51 | Clean & polish stator spigots |
| 52 | Fit new bearing insulted rings |
| 53 | Chemical clean 2 off cooler/tube bundles |
| 54 | Supply stainless steel bolts |
| 55 | Pressure test after repair |
| 56 | Supply and fit new desicator (1or2 off) |
| 57 | Remove inner and outer seal landing sleeves and manufacture new, refit to shaft |
| 58 | Supply and fit new DE & NDE bearing probes on site (2 off) |

| Item No | Description |
| --- | --- |
| 59 | Replace missing wedges & epoxy |
| 60 | Machine bearing housing for oil jacking |
| 61 | Fit new stain steel fasteners |
| 62 | Supply and fit new insulated rings 2 off |
| 63 | Fit missing stator wedges |
| 64 | Fit new bearing probes |
| 65 | Fit new PT connector |
| 66 | Overhaul mono-blocks |
| 67 | New high jacking pipes and inner pipes |
| 68 | Clean cooling tube bundle A |
| 69 | Clean cooling tube bundle B |
| 70 | Replace current Electric CT’s 3 off |
| 71 | Install current Electric CT’s 3 off (Free issue) |
|  | ROUTINE TESTS AND TEST AS AND WHEN REQUIRED |
| 1 | Measure and record winding Resistance test |
| 2 | Perform and record Insulation resistance test |
| 3 | Perform and record Polarization test |
| 4 | Perform and record Tan Delta test |
| 5 | Perform and record off-line partial discharge test |
| 6 | Perform wedge tightness test on stator |
| 7 | Perform induction test |

| Item No | Description |
| --- | --- |
| 8 | Preform stator ELCID test on the stator |
| 9 | Perform rotor core ELCID test |
| 10 | NDT on the rotor shaft |
| 11 | NDT on fan impellers or runners (Whole impeller) |
| 12 | Perform rotor bar to bar test (consider the number of bars per rotor) |
| 13 | Ultrasonic testing on white metal bearing surface |
| 14 | High voltage AC test |
| 15 | Balancing test |
| 16 | Copper material analysis test /check |
| 17 | Bearing insulation test |
| 18 | Bearing heat run test and check the bearing temperatures and vibration |
| 19 | Stator winding temperature measurements |
| 20 | Load test the motor and check efficiency |

    - PA FAN MOTOR 2350kW

| Item No | Description |
| --- | --- |
|  | GENERAL |
| 1 | Collect motor from Matimba Power Station |
| 2 | Deliver motor to Matimba Power Station |
| 3 | Open motor, clean and complete assessment report |
| 4 | Assemble motor |
| 5 | Paint complete motor |
|  | TERMINAL BOX AND LEADS |
| 1 | Replace leads |
| 2 | Replace terminal box studs |
| 3 | Supply and replace box gaskets and seals |
| 4 | Replace current Electric CT |
|  | HEAT EXCHANGER |

| Item No | Description |
| --- | --- |
| 1 | Remove oil from cooler tubes (clean with solvent) |
| 2 | Replace damping rubbers |
| 3 | Overhaul the heat exchanger / radiator |
| 4 | Replace broken cooler tubes |
| 5 | Pressure test the coolers tubes / radiator |
| 6 | Replace gaskets and seals |
|  | SPACE HEATERS |
| 1 | Test heaters |
| 2 | Overhaul heaters (Replace wiring) |
| 3 | Replace heaters |
|  | STATOR HOUSING |
| 1 | Polish stator foot mounting |
| 2 | Clean and dry stator |
| 3 | Treat and paint stator with anti-rust paint |
| 4 | Check the concentricity of the stator |
| 5 | Rectify or correct the stator concentricity |
| 6 | Replace tail leads (including Terminal box and leads-point1) |
| 7 | Re-insulate tail leads |
|  | ROTOR |
| 1 | Treat and paint rotor with anti-rust paint |
| 2 | Balance rotor at operating speed with fan and half key inserted |
| 3 | Polish the journals (NDE) |
| 4 | Polish the journals (DE) |
| 5 | Polish seal landings (NDE) |
| 6 | Polish seal landings (DE) |
| 7 | Polish fan landing (DE) |
| 8 | Polish fan landing (NDE) |
| 9 | Check shaft run out / concentricity |
| 10 | Rectify or correct the rotor concentricity |
| 11 | Micro welding rotor shaft (DE) |
| 12 | Micro welding rotor shaft (NDE) |
| 13 | Brazing of rotor end laminations |
| 14 | Fit new mag center indicator |
|  | RESISTANCE TEMPERATURE DETECTOR |
| 1 | PT100 resistance test/measure RTD |
| 2 | Install PT100 on the overhang winding (2 per phase, 6 in total) |
|  | DE SHIELD/ NDE SHIELD |
| 1 | Replace fixing bolts |
|  | WHITE METAL BEARINGS |
| 1 | Re-metal white metal DE bearing (see nameplate data supplied on SOW for this motor |
| 2 | Re-metal white metal NDE bearing (see nameplate data supplied on SOW for this motor |
| 3 | Refurbishment DE bearing housing to fit standard bearing refurbishment specifications |

| Item No | Description |
| --- | --- |
| 4 | Refurbishment NDE bearing housing to fit standard bearing refurbishment specifications |
| 5 | Overhaul DE seal |
| 6 | Overhaul NDE seal |
| 7 | Replace site glass and clean ports |
| 8 | Replace seals |
| 9 | Bearing insulation test point inspect and repair (Inspect specifically for test point housing insulation damage) |
| 10 | Replace bearing (see nameplate data supplied on SOW for this motor) |
| 11 | Inspect bearing housing |
|  | ACCESSORIES |
| 1 | Replace stator jacking bolts |
| 2 | Supply and fit new DE bearing |
| 3 | Conduct stator core flux and watts loss test |
| 4 | Rewind stator complete fit new magnetic wedges and blocks |
| 5 | VPI stator, cure, fit new stator leads and PT100’s |
| 6 | Open keyway, check run out, pre-machine coupling journal |
| 7 | Pre-machine DE and NDE outer and inner seal landings and bearing journals |
| 8 | Re-cut keyway, final grind journals |
| 9 | Supply new external fan |
| 10 | Skim stator feet |
| 11 | Supply new desiccators |
| 12 | Re-insulate bearing OD |
| 13 | Repair bearing nips |
| 14 | Repair stator core (vibrate stator core to remove hot spots) |
| 15 | New internal fans |
| 16 | Inspect shock absorber rubbers (replace if damaged) |
| 17 | Supply new earth brushes |
| 18 | Supply new vibration blocks |
| 19 | Supply new breathers |
| 20 | Fit new pipe work and ball valves |
| 21 | Fit new set of O-rings |
| 22 | Shotblast, clean and paints the housings |
| 23 | Repair journals and landings |
| 24 | Burn out stator, remove coils and prepare core for rewind |
| 25 | Manufacture new stator coil and insulation rewind kit |
| 26 | Install the new winding kit, VPI and curing |
| 27 | Overhaul air to air canopy |
| 28 | Replace connector blocks |
| 29 | Supply and fit new insulators-triangular type |
| 30 | Test stator, QC and paint |
| 31 | Skim Stator Feet |
| 32 | Re-tap Mounting Holes |
| 33 | Re-tap Holes & Fit New Jacking Bolts |
| 34 | Micro-weld & machine NDE/DE outer seal landing |
| 35 | Micro-weld & machine NDE/DE inner seal landing |

| Item No | Description |
| --- | --- |
| 36 | Fit new earth lugs |
| 37 | Clean & polish spigots |
| 38 | Fit new earth brush & holder |
| 39 | Fit new Zorc |
| 40 | Manufacture new rotor core |
| 41 | Remove old rotor core & fit new |
| 42 | Machine off rotor end rings & remove rotor bars |
| 43 | Manufacture new rotor end rings & bars |
| 44 | Re-bar rotor complete |
| 45 | Fit new bearing probes DE & NDE |
| 46 | Repair oil rings & fit new screws |
| 47 | Repair bearing housing nips |
| 48 | Re-sleeve vacuum seals |
| 49 | Light line bore stator core |
| 50 | Skim rotor core |
| 51 | Supply & fit new earth brush & holder 2 off |
| 52 | Supply & fit new insulated rings |
| 53 | Repair bearing housing nips |
| 54 | Replace missing wedges & epoxy |
| 55 | Machine DE bearing journal radius |
| 56 | Light machine DE/NDE outer seal landing |
| 57 | Overhaul desicator |
| 58 | Fit new insulated rings & final machine OD |
| 59 | Chemical clean 2 off cooler bundles |
| 60 | Supply stainless steel bolts & assemble |
| 61 | Pressure test after repair |
| 62 | Replace 2 off missing stator wedges & epoxy |
| 63 | Re-tap all mounting holes |
| 64 | Manufacture new interlock dust seal carrier |
| 65 | Re-insulated bearing OD & final machine |
| 66 | Manufacture new DE outer seal sleeve |
| 67 | Supply & fit new earth brush & holder |
| 68 | Fit new DE/NDE circlips 2 off 170mm |
| 69 | Supply & fit new DE/NDE bearing probes |
| 70 | Grit blast & paint heat exchanger casing |
| 71 | Supply & fit new DE/NDE bearing (6034 C3) |
| 72 | Repair bearing housings OD’S & machine back to standard |
| 73 | Fit new magnetic wedges & blocks |
| 74 | Replace current Electric CT’s 3 off |
| 75 | Install current Electric CT’s 3 off (Free issue) |
|  | ROUTINE TESTS AND TEST AS WHEN REQUIRED |
| 1 | Measure and record winding resistance test |
| 2 | Perform and record insulation resistance test |
| 3 | Perform and record polarization test |
| 4 | Tan Delta test |
| 5 | Partial Discharge test |
| 6 | Slot wedging test on stator |

| Item No | Description |
| --- | --- |
| 7 | ELCID test on stator |
| 8 | ELCID test on rotor |
| 9 | NDT on the rotor shaft |
| 10 | NDT on fan impellers or runners (Whole impeller) |
| 11 | Rotor bar to bar test (consider the number of bars per rotor) |
| 12 | Ultrasonic testing on white metal bearing surface |
| 13 | High voltage test |
| 14 | Balancing test |
| 15 | Copper material analysis test /check |
| 16 | Bearing insulation test |
| 17 | Bearing heat run test and check the bearing temperatures and vibration |
| 18 | Perform induction test |
| 19 | Stator winding temperature measurements |
| 20 | Load test the motor and check efficiency |

#### Mill Motor 2150kW

| Item No | Description |
| --- | --- |
|  | GENERAL |
| 1 | Collect motor from Matimba Power Station |
| 2 | Deliver motor to Matimba Power Station |
| 3 | Open motor, clean and complete assessment report |
| 4 | Assemble motor |
| 5 | Paint complete motor |
|  | TERMINAL BOX AND LEADS |
| 1 | Replace leads |
| 2 | Replace terminal box studs |
| 3 | Supply and replace box gaskets and seals |
| 4 | Replace current Electric CT |
|  | HEAT EXCHANGER |
| 1 | Remove oil from cooler tubes (clean with solvent) |
| 2 | Replace damping rubbers (each) |
| 3 | Overhaul the cooler |
| 4 | Pressure test the coolers tubes / radiator |
| 5 | Replace gaskets and seals |
|  | SPACE HEATERS |
| 1 | Test heaters |
| 2 | Overhaul heaters (replace wiring) |
| 3 | Replace heaters |
|  | STATOR HOUSING |
| 1 | Polish stator foot mounting |

| Item No | Description |
| --- | --- |
| 2 | Clean and dry stator |
| 3 | Treat and paint stator with anti-rust paint |
| 4 | Check the concentricity of the stator |
| 5 | Rectify or correct the stator concentricity |
| 6 | Replace tail leads (including in terminal box and leads) |
| 7 | Reinsulate tail leads |
|  | ROTOR |
| 1 | Treat and paint rotor with anti-rust paint |
| 2 | Balance rotor at operating speed with fan and half key inserted |
| 3 | Polish the journals (NDE) |
| 4 | Polish the journals (DE) |
| 5 | Polish seal landings (NDE) |
| 6 | Polish seal landings (DE) |
| 7 | Polish fan landing (DE) |
| 8 | Polish fan landing (NDE) |
| 9 | Check shaft run out / concentricity |
| 10 | Rectify or correct the rotor concentricity |
| 11 | Micro welding rotor shaft (DE) |
| 12 | Micro welding rotor shaft (NDE) |
| 13 | Inspect coupling keyway on shaft for damage and coupling bore (Repair with micro weld if needed |
| 14 | Brazing of rotor end laminations |
| 15 | Fit new mag center indicator |
|  | RESISTANCE TEMPERATURE DETECTOR |
| 1 | PT100 resistance test/ Measure RTD |
| 2 | Install PT100 on the overhang winding (2 per phase, 6 in total) |
|  | DE SHIELD AND NDE SHIELD |
| 1 | Replace fixing bolts |
|  | WHITE METAL BEARING |
| 1 | Re-metal white metal DE bearing (see nameplate data supplied on SOW for this motor) |
| 2 | Re-metal white metal NDE bearing (see nameplate data supplied on SOW for this motor) |
| 3 | Refurbishment DE bearing housing to fit standard bearing refurbishment specifications |
| 4 | Refurbishment NDE bearing housing to fit standard bearing refurbishment specifications |
| 5 | Overhaul DE seal |
| 6 | Overhaul NDE seal |
| 7 | Replace site glass and clean ports |
| 8 | Replace seals |
| 9 | Bearing insulation test point inspect and repair (Inspect specifically for test point housing insulation damage) |
| 10 | Replace bearing (see nameplate data supplied on SOW for this motor) |
| 11 | Inspect bearing housing (assess the bearing housing, bearing seating surfaces for wear/damage) |
|  | ACCESSORIES |

| Item No | Description |
| --- | --- |
| 1 | Replace stator jacking bolts |
| 2 | Supply and fit new DE bearing |
| 3 | Conduct stator core flux and watts loss test |
| 4 | Rewind stator complete fit new magnetic wedges and blocks |
| 5 | VPI stator, cure, fit new stator leads and PT100’s |
| 6 | Open keyway, check run out, pre-machine coupling journal |
| 7 | Pre-machine DE and NDE outer and inner seal landings and bearing journals |
| 8 | Re-cut keyway, final grind journals |
| 9 | Supply new external fan |
| 10 | Skim stator feet |
| 11 | Supply new desiccators |
| 12 | Re-insulate bearing OD |
| 13 | Repair bearing nips |
| 14 | Repair stator core (vibrate stator core to remove hot spots) |
| 15 | New internal fans |
| 16 | Inspect shock absorber rubbers (replace if damaged) |
| 17 | Supply new earth brushes |
| 18 | Supply new vibration blocks |
| 19 | Supply new breathers |
| 20 | Fit new pipe work and ball valves |
| 21 | Fit new set of O-rings |
| 22 | Shotblast, clean and paints the housings |
| 23 | Repair journals and landings |
| 24 | Burn out stator, remove coils and prepare core for rewind |
| 25 | Manufacture new stator coil and insulation rewind kit |
| 26 | Install the new winding kit, VPI and curing |
| 27 | Overhaul air to air canopy |
| 28 | Replace connector blocks |
| 29 | Supply and fit new insulators-triangular type |
| 30 | Test stator, QC and paint |
| 31 | Re-tap all mounting holes |
| 32 | Clean & polish spigots |
| 33 | Manufacture new fan cowl screen |
| 34 | Microweld & machine NDE outer seal landing in different sizes |
| 35 | Manufacture new insulated rings 2 off |
| 36 | Manufacture new stator core – stacked, welded & machines |
| 37 | Skim rotor core |
| 38 | Overhaul fan cowl & external |
| 39 | Microweld & machine DE/NDE coupling landing in different sizes & cut keyway |
| 40 | Microweld & machine DE/NDE inner/outer seal landing in different sizes |
| 41 | Fit new insulated rings |
| 42 | Fit new high jacking pipes & inlet pipes and machine housing |
| 43 | Machine bearing housing for oil jacking pipes |
| 44 | Re-insulate bearing OD |
| 45 | Re-insulate bearing nips |

| Item No | Description |
| --- | --- |
| 46 | Fit new high jacking pipes & inlet pipes |
| 47 | Re-sleeve vacuum seals |
| 48 | Overhaul earth brush & holder |
| 49 | Overhaul desicator 1 or 2 off |
| 50 | Fit new bearing probes wire DE/NDE |
| 51 | Supply new earth brushes & holder |
| 52 | Repair mounting holes on star point terminal box mounting to stator & re-fit |
| 53 | Supply & fit new star point connector |
| 54 | Replace current Electric CT’s 3 off |
| 55 | Manufacture new DE/NDE outer seal sleeves landing in different sizes |
| 56 | Manufacture new DE/NDE inner seal sleeves landing in different sizes |
| 57 | Fit new bolts and washers on bearing housings DE/NDE |
| 58 | Line bore stator core to remove hotspots |
| 59 | Repair damaged wedges on stator |
| 60 | Light skim rotor core surface |
| 61 | Manufacture new brass oil pick up ring |
| 62 | New drain plugs |
| 63 | Manufacture new DE/NDE seal plate (earth brush holder cover plate) |
| 64 | Remove old stator core |
| 65 | Weld and machine casing bore to suit new core, fit new core and secure |
| 66 | Re-tap all jacking bolt holes |
| 67 | Manufacture new rotor core complete |
| 68 | Rebar new rotor core with new bars and end-rings double cage rotor |
| 69 | Remove old rotor core and fit new to shaft |
| 70 | Machine rotor core to suit air gap |
| 71 | Repair broken seal carrier housing |
| 72 | Manufacture new brass oil pickup ring |
| 73 | Manufacture new inner/outer vacuum seal and insert |
| 74 | Manufacture new seal carrier |
| 75 | Manufacture new seal carrier insert |
| 76 | Supply new bearing housing earthing straps |
| 77 | Repair fibre glass baffle plate |
| 78 | Light machine rotor core surface |
| 79 | Manufacture new NDE/DE white bearing |
| 80 | Overhaul external fan & cowl |
| 81 | New insulation rings |
| 82 | Re-NDT rotor shaft after micro welding |
| 83 | Supply and fit new earth straps |
| 84 | Supply fit new cowl mounting rubbers |
| 85 | Fit new PT connectors |
| 86 | Fit new diots |
| 87 | Fit new sleeving for bearing probes |
| 88 | Fit new bolt, washers and springs |
| 89 | Repair terminal box to suit casing |

| Item No | Description |
| --- | --- |
| 90 | Repair screen |
| 91 | Repair cowl baffles |
| 92 | Sand blast all loose components |
| 93 | Overhaul external and internal fan |
| 94 | Fit new wedges |
| 95 | Repair internal baffles |
| 96 | Overhaul stator and spray with insulation varnish |
| 97 | Manufacture new DE & NDE inner and outer sleeves |
| 98 | Manufacture new floating LAB seals 2 off |
| 99 | Fit new earth lugs |
| 100 | Overhaul coupling and re-fit |
| 101 | Overhaul fiberglass inserts |
| 102 | Plug stator holes |
| 103 | Panel beat casing |
| 104 | Sandblast all loose components |
| 105 | Supply and fit new stainless-steel fasteners and pressure test tube bundle |
| 106 | Supply silicon gaskets |
| 107 | Fit new insulator for connection side |
| 108 | Overhaul rotor and spray with insulation varnish |
| 109 | Manufacture new terminal box bottom cover |
| 110 | Supply & fit 4 off new heater terminal blocks |
| 111 | Repair epoxy baffles |
| 112 | Fit new magnetic wedges & blocks |
| 113 | Install current Electric CT’s 2 off (Free issue) |
|  | ROUTINE TESTS AND TEST AS WHEN REQUIRED |
| 1 | Measure and record winding resistance test |
| 2 | Perform and record insulation resistance test |
| 3 | Perform and record Tan Delta test |
| 4 | Perform and record polarization test |
| 5 | Perform and record off-line partial discharge test |
| 6 | Perform wedge tightness test on stator |
| 7 | Perform induction test |
| 8 | Perform stator ELCID test on stator |
| 9 | Perform rotor core ELCID test |
| 10 | NDT on the rotor shaft |
| 11 | NDT on fan impellers or runners (Whole impeller) |
| 12 | Perform rotor bar to bar test (consider the number of bars per rotor) |
| 13 | Ultrasonic testing on white metal bearing surface |
| 14 | High voltage AC test |
| 15 | Balancing test |
| 16 | Copper material analysis test /check |
| 17 | Bearing insulation test |
| 18 | Bearing heat run test and check the bearing temperatures and vibration |
| 19 | Stator winding temperature measurements |
| 20 | Load test the motor and check efficiency |

    - T1 Conveyor Drive Motor 820kW

| Item No | Description |
| --- | --- |
|  | GENERAL |
| 1 | Collect motor from Matimba Power Station |
| 2 | Deliver motor to Matimba Power Station |
| 3 | Open motor, clean and complete assessment report |
| 4 | Assemble motor |
| 5 | Paint complete motor |
|  | TERMINAL BOX AND LEADS |
| 1 | Replace leads |
| 2 | Replace terminal box studs |
| 3 | Supply and replace box gaskets and seals |
| 4 | Replace current Electric CT |
|  | HEAT EXCHANGER |
| 1 | Remove oil from cooler tubes (clean with solvent) |
| 2 | Replace damping rubbers |
| 3 | Overhaul the cooler |
| 4 | Pressure test the cooler |
| 5 | Replace gaskets and seals |
|  | SPACE HEATERS |
| 1 | Test heaters |
| 2 | Overhaul heaters (replace wiring) |
| 3 | Replace heaters |
|  | STATOR HOUSING |
| 1 | Polish stator foot mounting |
| 2 | Clean and dry stator |
| 3 | Treat and paint stator with anti-rust paint |
| 4 | Check the concentricity of the stator |
| 5 | Rectify or correct the stator concentricity |
| 6 | Replace tail leads (incl terminal box and leads-point1) |
| 7 | Reinsulate tail leads |
|  | RESISTANCE TEMPERATURE DETECTOR |
| 1 | PT100 resistance test/measure RTD |
| 2 | Install PT100 on the overhang winding (2 per phase, 6 in total) |
|  | ROTOR |
| 1 | Treat and paint stator with anti-rust paint |
| 2 | Balance rotor at operating speed with fan and half key inserted |
| 3 | Polish the journals (NDE) |
| 4 | Polish the journals (DE) |
| 5 | Polish seal landings (NDE) |
| 6 | Polish seal landings (DE) |
| 7 | Polish fan landing (DE) |
| 8 | Polish fan landing (NDE) |
| 9 | Check shaft run out / concentricity |

| Item No | Description |
| --- | --- |
| 10 | Rectify or correct the rotor concentricity |
| 11 | Micro welding rotor shaft (DE) |
| 12 | Micro welding rotor shaft (NDE) |
| 13 | Brazing of rotor end laminations |
| 14 | Fit new mag center indicator |
|  | DE SHIELD/ NDE SHIELD |
| 1 | Replace fixing bolts |
|  | WHITE METAL BEARING |
| 1 | Re-metal white metal DE bearing (see nameplate data supplied on SOW for this motor |
| 2 | Re-metal white metal NDE bearing (see nameplate data supplied on SOW for this motor |
| 3 | Refurbishment DE bearing housing to fit standard bearing refurbishment specifications |
| 4 | Refurbishment NDE bearing housing to fit standard bearing refurbishment specifications |
| 5 | Overhaul DE seal |
| 6 | Overhaul NDE seal |
| 7 | Replace site glass and clean ports |
| 8 | Replace seals |
| 9 | Bearing insulation test point inspect and repair (Inspect specifically for test point housing insulation damage) |
| 10 | Replace bearing (see nameplate data supplied on SOW for this motor) |
| 11 | Inspect bearing housing |
|  | ACCESSORIES |
| 1 | Fit new internal fans as and when required |
| 2 | Inspect shock absorber rubbers (replace if damaged) |
| 3 | Fit new floating lab seals |
| 4 | Supply new sight glasses |
| 5 | Supply new breathers |
| 6 | Supply new pipe work and ball valves |
| 7 | Fit new set of O-rings |
| 8 | Shotblast, clean and paint the housings |
| 9 | Repair journals and landings |
| 10 | Burn out stator, remove coils and prepare core for rewind |
| 11 | Manufacture new stator coil and insulation rewind kit |
| 12 | Install the new winding kit, VPI and curing |
| 13 | Overhaul air to air canopy |
| 14 | Replace connector blocks |
| 14 | Supply and fit new insulators-triangle type |
| 15 | High voltage AC test |
| 16 | Balancing test |
| 17 | Copper material analysis test /check |
| 18 | Bearing insulation test |
| 19 | Bearing heat run test and check the bearing temperatures and vibration |
| 20 | Stator winding temperature measurements |
| 21 | Load test the motor and check efficiency |
| 22 | Cut keyway |

| Item No | Description |
| --- | --- |
| 23 | NDT after micro welding |
| 24 | Replace stripped, missing bolts and plugs |
| 25 | Supply and fit 2 off new desicator |
| 26 | Fit new earth lugs |
| 27 | Sandblast all loose components |
| 28 | Fit new nuts on terminal box threads |
| 29 | Remove old and fit new feet (4 off) |
| 30 | Skim stator feet |
| 31 | Re-tap all mounting holes |
| 32 | Polish spigots |
| 33 | Overhaul screens and fans |
| 34 | Re-insulate bearing housings |
| 35 | Fit new earth brush and holder complete |
| 36 | Re-sleeve vacuum seal |
| 37 | Manufacture new IP55 seals |
| 38 | Manufacture new oil rings |
| 39 | Re-insulate vacuum seal (2 off) |
| 40 | Supply and fit bearing probes (3 off) |
| 41 | Fit new probes 200mm (2 off) |
| 42 | Fit new desicator (2 off) |
| 43 | Fit new temperature gauge |
| 44 | Remove clean and refit coupling |
| 45 | Re-tap all mounting holes |
| 46 | Fit missing bolts, flats, and springs |
| 47 | Overhaul screen and external fan |
| 48 | Microweld and machine coupling landing |
| 49 | Microweld and machine NDE outer seal landing |
| 50 | Re-insulate bearing housing |
| 51 | Fit new earth brush and holder complete |
| 52 | Manufacture new rotor core |
| 53 | Machine off rotor short circuiting rings & remove rotor bars |
| 54 | Manufacture new rotor bars & short-circuiting rings |
| 55 | Re-bar rotor complete |
| 56 | Replace current Electric CT’s 3 off |
| 57 | Install current Electric CT’s 3 off (Free issue) |

#### S1 Conveyor Motor 700kW

| Item No | Description |
| --- | --- |
|  | GENERAL |
| 1 | Collect motor from Matimba Power Station |
| 2 | Deliver motor to Matimba Power Station |
| 3 | Open motor, clean and complete assessment report |
| 4 | Assemble motor |
| 5 | Paint complete motor |
|  | TERMINAL BOX AND LEADS |
| 1 | Replace leads |
| 2 | Replace terminal box studs |
| Item No | Description |
| 3 | Supply and replace box gaskets and seals |
| 4 | Replace current Electric CT |
|  | HEAT EXCHANGER |
| 1 | Remove oil from cooler tubes and clean with solvent |
| 2 | Replace damping rubbers |
| 3 | Overhaul the cooler |
| 4 | Pressure test the coolers |
| 5 | Replace gaskets and seals |
|  | SPACE HEATERS |
| 1 | Test heaters |
| 2 | Overhaul heaters (Replace wiring) |
| 3 | Replace heaters |
|  | STATOR HOUSING |
| 1 | Polish stator foot mounting |
| 2 | Clean and dry stator |
| 3 | Treat and paint stator with anti-rust paint |
| 4 | Check the concentricity of the stator |
| 5 | Rectify or correct the stator concentricity |
| 6 | Replace tail leads (including Terminal box and leads- point1) |
| 7 | Re-insulate tail leads |
|  | ROTOR |
| 1 | Treat and paint rotor with anti-rust paint |
| 2 | Balance rotor at operating speed with fan and half key inserted |
| 3 | Polish the journals (NDE) |
| 4 | Polish the journals (DE) |
| 5 | Polish seal landings (NDE) |
| 6 | Polish seal landings (DE) |
| 7 | Polish fan landing (DE) |
| 8 | Polish fan landing (NDE) |
| 9 | Check shaft run out / concentricity |
| 10 | Rectify or correct the rotor concentricity |
| 11 | Micro welding rotor shaft (DE) |
| 12 | Micro welding rotor shaft (NDE) |
| 13 | Brazing of rotor end laminations |
| 14 | Fit new mag center indicator |
|  | RESISTANCE TEMPERATURE DETECTOR |
| 1 | PT100 resistance test/ Measure RTD |
| 2 | Install PT100 on the overhang winding (2 per phase, 6 in total) |
|  | DE SHIELD / NDE SHIELD |
| 1 | Replace fixing bolts |
|  | BEARINGS |
| 1 | Refurbishment DE bearing housing to fit standard bearing refurbishment specifications. |
| 2 | Refurbishment NDE bearing housing to fit standard bearing refurbishment specifications. |

| Item No | Description |
| --- | --- |
| 3 | Replace bearing (see nameplate data supplied on SOW for this motor) |
| 4 | Inspect bearing housing |
| 5 | Replace seals |
|  | ACCESSORIES |
| 1 | Fit new internal fans as and when required |
| 2 | Inspect shock absorber rubbers (replace if damaged) |
| 3 | Fit new floating lab seals |
| 4 | Supply new sight glasses |
| 5 | Supply new breathers |
| 6 | Supply new pipe work and ball valves |
| 7 | Fit new set of O-rings |
| 8 | Shotblast, clean and paint the housings |
| 9 | Repair journals and landings |
| 10 | Burn out stator, remove coils and prepare core for rewind |
| 11 | Manufacture new stator coil and insulation rewind kit |
| 12 | Install the new winding kit, VPI and curing |
| 13 | Overhaul air to air canopy |
| 14 | Replace connector blocks |
| 15 | Supply and fit new insulators-triangle type |
| 16 | Balancing test |
| 17 | Copper material analysis test/ check |
| 18 | Bearing insulation test |
| 19 | Bearing heat run test and check the bearing temperatures and vibration |
| 20 | Stator winding temperature measurements |
| 21 | Load test the motor and check efficiency |
| 22 | NDT rotor shaft |
| 23 | Manufacture new rotor core |
| 24 | Remove old rotor core and fit new |
| 25 | Machine off rotor short circuiting rings & remove rotor bars |
| 26 | Manufacture new rotor bars & short-circuiting rings |
| 27 | Re-bar rotor complete |
| 28 | Re-insulate DE & NDE bearing housings |
| 29 | Fit earth lugs |
| 30 | Fit new grease pipes & fittings |
| 31 | Re-insulate bearings cap / Manufacture new NDE/DE bearing cap |
| 32 | Manufacture new NDE/DE flinger |
| 33 | Re-tap all mounting holes |
| 34 | Polish spigots |
| 35 | Remove, clean & Re-fit coupling |
| 36 | Re-insulate NDE/DE bearing housings |
| 37 | Fit new lock washers 110mm |
| 38 | Fit new earth brush & holder |
| 39 | Repair baffles |
| 40 | Overhaul coupling & re-fit |
| 41 | Overhaul external fan |

| Item No | Description |
| --- | --- |
| 42 | Skim stator feet |
| 43 | Supply & fit new auxiliary terminal box for heaters |
| 44 | Light machine flingers & cut new threads |
| 45 | Repair rotor shaft threads |
| 46 | Manufacture new stator core – stacked & welded |
| 47 | Line bore stator core for air gap |
| 48 | Machine off rotor end rings & remove rotor bars |
| 49 | Manufacture new rotor end rings & rotor bars |
| 50 | Microweld & machine NDE/DE inner seal landing in different sizes |
| 51 | Microweld & machine NDE/DE outer seal landing in different sizes |
| 52 | Microweld & machine NDE/DE external fan landing in different sizes |
| 53 | Weld & machine NDE/DE bearing cap |
| 54 | Re-tap holes & fit new jacking bolts |
| 55 | Supply & fit new jacking bolts |
| 56 | Weld & machine DE/NDE bearing housing bore to suit shaft - cracked |
| 57 | Replace bearing probes |
| 58 | Fit new grease pipes & fittings |
| 59 | Overhaul fan cowl |
| 60 | Replace current Electric CT’s 3 off |
| 61 | Install current Electric CT’s 3 off (Free issue) |

    - S2 Conveyor Motor 200kW

| Item No | Description |
| --- | --- |
|  | GENERAL |
| 1 | Collect motor from Matimba Power Station |
| 2 | Deliver motor to Matimba Power Station |
| 3 | Open motor, clean and complete assessment report |
| 4 | Assemble motor |
| 5 | Paint complete motor |
|  | TERMINAL BOX AND LEADS |
| 1 | Replace leads |
| 2 | Replace terminal box studs |
| 3 | Supply and replace box gaskets and seals |
| 4 | Replace current Electric CT |
|  | HEAT EXCHANGER |
| 1 | Remove oil from cooler tubes with solvent |
| 2 | Replace damping rubbers |
| 3 | Overhaul the cooler |
| 4 | Pressure test the coolers |
| 5 | Replace gaskets and seals |
|  | SPACE HEATERS |
| 1 | Test heaters |
| 2 | Overhaul heaters (replace wiring) |
| 3 | Replace heaters |
|  | STATOR HOUSING |
| 1 | Polish stator foot mounting |

| Item No | Description |
| --- | --- |
| 2 | Clean and dry stator |
| 3 | Treat and paint stator with anti-rust paint |
| 4 | Check the concentricity of the stator |
| 5 | Rectify or correct the stator concentricity |
| 6 | Replace tail leads (Including Terminal box and leads-point1) |
| 7 | Reinsulate tail leads |
|  | ROTOR |
| 1 | Treat and paint rotor with anti-rust paint |
| 2 | Balance rotor at operating speed with fan and half key inserted |
| 3 | Polish the journals (NDE) |
| 4 | Polish the journals (DE) |
| 5 | Polish seal landings (NDE) |
| 6 | Polish seal landings (DE) |
| 7 | Polish fan landing (DE) |
| 8 | Polish fan landing (NDE) |
| 9 | Check shaft run out / concentricity |
| 10 | Rectify or correct the rotor concentricity |
| 11 | Micro welding rotor shaft (DE) |
| 12 | Micro welding rotor shaft (NDE) |
| 13 | Brazing of rotor end laminations |
| 14 | Fit new mag center indicator |
|  | RESISTANCE TEMPERATURE DETECTOR |
| 1 | PT100 resistance test/ Measure RTD |
| 2 | Install PT100 on the overhang winding (2 per phase, 6 in total) |
|  | DE SHIELD/NDE SHIELD |
| 1 | Replace fixing bolts |
|  | BEARINGS |
| 1 | Refurbishment DE bearing housing to fit standard bearing refurbishment specifications |
| 2 | Refurbishment NDE bearing housing to fit standard bearing refurbishment specifications |
| 3 | Replace bearing (see nameplate data supplied on SOW for this motor) |
| 4 | Inspect bearing housing |
| 5 | Replace seals |
|  | ACCESSORIES |
| 1 | Fit new internal fans as and when required |
| 2 | Inspect shock absorber rubbers (replace if damaged) |
| 3 | Fit new floating lab seals |
| 4 | Supply new sight glasses |
| 5 | Supply new breathers |
| 6 | Supply new pipe work and ball valves |
| 7 | Fit new set of O-rings |
| 8 | Shotblast, clean and paint the housings |
| 9 | Repair journals and landings |
| 10 | Burn out stator, remove coils and prepare core for rewind |

| Item No | Description |
| --- | --- |
| 11 | Manufacture new stator coil and insulation rewind kit |
| 12 | Install the new winding kit, VPI and curing |
| 13 | Overhaul air to air canopy |
| 14 | Replace connector blocks |
| 15 | Supply and fit new insulators-triangle type |
| 16 | Balancing test |
| 17 | Copper material analysis test/check |
| 18 | Bearing insulation test |
| 19 | Stator winding temperature measurements |
| 20 | Bearing heat run test and check the bearing temperatures and vibration |
| 21 | Load test the motor and check efficiency |
| 22 | NDT rotor shaft |
| 23 | Manufacture new rotor core |
| 24 | Remove old rotor core and fit new |
| 25 | Machine off rotor short circuiting rings & remove rotor bars |
| 26 | Manufacture new rotor bars & short-circuiting rings |
| 27 | Re-bar rotor complete |
| 28 | Re-insulate DE & NDE bearing housings |
| 29 | Fit earth lugs |
| 30 | Fit new grease pipes & fittings |
| 31 | Re-insulate bearings cap / Manufacture new NDE/DE bearing cap |
| 32 | Manufacture new NDE/DE flinger |
| 33 | Re-tap all mounting holes |
| 34 | Polish spigots |
| 35 | Remove, clean & Re-fit coupling |
| 36 | Re-insulate NDE/DE bearing housings |
| 37 | Fit new lock washers 110mm |
| 38 | Fit new earth brush & holder |
| 39 | Repair baffles |
| 40 | Overhaul coupling & re-fit |
| 41 | Overhaul external fan |
| 42 | Skim stator feet |
| 43 | Supply & fit new auxiliary terminal box for heaters |
| 44 | Light machine flingers & cut new threads |
| 45 | Repair rotor shaft threads |
| 46 | Manufacture new stator core – stacked & welded |
| 47 | Line bore stator core for air gap |
| 48 | Machine off rotor end rings & remove rotor bars |
| 49 | Manufacture new rotor end rings & rotor bars |
| 50 | Microweld & machine NDE/DE inner seal landing in different sizes |
| 51 | Microweld & machine NDE/DE outer seal landing in different sizes |
| 52 | Microweld & machine NDE/DE external fan landing in different sizes |
| 53 | Weld & machine NDE/DE bearing cap |
| 54 | Re-tap holes & fit new jacking bolts |
| 55 | Supply & fit new jacking bolts |
| 56 | Weld & machine DE/NDE bearing housing bore to suit shaft - cracked |
| 57 | Replace bearing probes |
| 58 | Fit new grease pipes & fittings |
| 59 | Overhaul fan cowl |
| 60 | Replace current Electric CT’s 3 off |
| 61 | Install current Electric CT’s 3 off (Free issue) |

#### S3 Conveyor Motor 275kW

| Item No | Description |
| --- | --- |
|  | GENERAL |
| 1 | Collect motor from Matimba Power Station |
| 2 | Deliver motor to Matimba Power Station |
| 3 | Open motor, clean and complete assessment report |
| 4 | Assemble motor |
| 5 | Paint complete motor |
|  | TERMINAL BOX AND LEADS |
| 1 | Replace leads |
| 2 | Replace terminal box studs |
| 3 | Supply and replace box gaskets and seals |
| 4 | Replace current Electric CT |
|  | HEAT EXCHANGER |
| 1 | Remove oil from cooler tubes (clean with solvent) |
| 2 | Replace damping rubbers |
| 3 | Overhaul the cooler |
| 4 | Pressure test the coolers |
| 5 | Replace gaskets and seals |
|  | SPACE HEATERS |
| 1 | Test heaters |
| 2 | Overhaul heaters (Replace wiring) |
| 3 | Replace heaters |
|  | STATOR HOUSING |
| 1 | Polish stator foot mounting |
| 2 | Clean and dry stator |
| 3 | Treat and paint stator with anti-rust paint |
| 4 | Check the concentricity of the stator |
| 5 | Rectify or correct the stator concentricity |
| 6 | Replace tail leads (including in terminal box & leads- point1) |
| 7 | Reinsulate tail leads |
|  | ROTOR |
| 1 | Treat and paint rotor with anti-rust paint |
| 2 | Balance rotor at operating speed with fan and half key inserted |
| 3 | Polish the journals (NDE) |
| 4 | Polish the journals (DE) |
| 5 | Polish seal landings (NDE) |
| 6 | Polish seal landings (DE) |
| 7 | Polish fan landing (DE) |

| Item No | Description |
| --- | --- |
| 8 | Polish fan landing (NDE) |
| 9 | Check shaft run out / concentricity |
| 10 | Rectify or correct the rotor concentricity |
| 11 | Micro welding rotor shaft (DE) |
| 12 | Micro welding rotor shaft (NDE) |
| 13 | Replace fixing bolts |
| 14 | Brazing of rotor and laminations |
| 15 | Fit new mag center indicator |
|  | RESISTANCE TEMPERATURE DETECTOR |
| 1 | PT100 resistance test/ measure RTD |
| 2 | Install PT100 on the overhang winding (2 per phase, 6 in total) |
|  | DE SHIELD/ NDE SHIELD |
| 1 | Replace fixing bolts |
|  | BEARINGS |
| 1 | Refurbish DE bearing housing to fit standard bearing refurbishment specifications |
| 2 | Refurbish NDE bearing housing to fit standard bearing refurbishment specifications |
| 3 | Replace bearing (see nameplate data supplied on SOW for this motor) |
| 4 | Replace seals |
| 5 | Inspect bearing housing |
|  | ACCESSORIES |
| 1 | Fit new internal fans as and when required |
| 2 | Inspect shock absorber rubbers (replace if damaged) |
| 3 | Fit new floating lab seals |
| 4 | Supply new sight glasses |
| 5 | Supply new breathers |
| 6 | Supply new pipe work and ball valves |
| 7 | Fit new set of O-rings |
| 8 | Shotblast, clean and paint the housings |
| 9 | Repair journals and landings |
| 10 | Burn out stator, remove coils and prepare core for rewind |
| 11 | Manufacture new stator coil and insulation rewind kit |
| 12 | Install the new winding kit, VPI and curing |
| 13 | Overhaul air to air canopy |
| 14 | Replace connector blocks |
| 15 | Supply and fit new insulators-triangle type |
| 16 | Bearing insulation test |
| 17 | Bearing heat run test and check the bearing temperatures and vibration |
| 18 | Stator winding temperature measurements |
| 19 | Load test the motor and check efficiency |
| 20 | NDT rotor shaft |
| 21 | Manufacture new rotor core |
| 22 | Remove old rotor core and fit new |

| 23 | Machine off rotor short circuiting rings & remove rotor bars |
| --- | --- |
| 24 | Manufacture new rotor bars & short-circuiting rings |
| 25 | Re-bar rotor complete |
| 26 | Re-insulate DE & NDE bearing housings |
| 27 | Fit earth lugs |
| 28 | Fit new grease pipes & fittings |
| 29 | Re-insulate bearings cap / Manufacture new NDE/DE bearing cap |
| 30 | Manufacture new NDE/DE flinger |
| 31 | Re-tap all mounting holes |
| 32 | Polish spigots |
| 33 | Remove, clean & Re-fit coupling |
| 34 | Re-insulate NDE/DE bearing housings |
| 35 | Fit new lock washers 110mm |
| 36 | Fit new earth brush & holder |
| 37 | Repair baffles |
| 38 | Overhaul coupling & re-fit |
| 39 | Overhaul external fan |
| 40 | Skim stator feet |
| 41 | Supply & fit new auxiliary terminal box for heaters |
| 42 | Light machine flingers & cut new threads |
| 43 | Repair rotor shaft threads |
| 44 | Manufacture new stator core – stacked & welded |
| 45 | Line bore stator core for air gap |
| 46 | Machine off rotor end rings & remove rotor bars |
| 47 | Manufacture new rotor end rings & rotor bars |
| 48 | Microweld & machine NDE/DE inner seal landing in different sizes |
| 49 | Microweld & machine NDE/DE outer seal landing in different sizes |
| 50 | Microweld & machine NDE/DE external fan landing in different sizes |
| 51 | Weld & machine NDE/DE bearing cap |
| 52 | Re-tap holes & fit new jacking bolts |
| 53 | Supply & fit new jacking bolts |
| 54 | Weld & machine DE/NDE bearing housing bore to suit shaft - cracked |
| 55 | Replace bearing probes |
| 56 | Fit new grease pipes & fittings |
| 57 | Overhaul fan cowl |
| 58 | Replace current Electric CT’s 3 off |
| 59 | Install current Electric CT’s 3 off (Free issue) |

    - S4 Conveyor Motor 320kW

| Item No | Description |
| --- | --- |
|  | GENERAL |
| 1 | Collect motor from Matimba Power Station |
| 2 | Deliver motor to Matimba Power Station |
| 3 | Open motor, clean and complete assessment report |
| 4 | Assemble motor |

| Item No | Description |
| --- | --- |
| 5 | Paint complete motor |
|  | TERMINAL BOX AND LEADS |
| 1 | Replace leads |
| 2 | Replace terminal box studs |
| 3 | Supply and replace box gaskets and seals |
| 4 | Replace current Electric CT |
|  | HEAT EXCHANGER |
| 1 | Remove oil from cooler tubes (clean with solvent) |
| 2 | Replace damping rubbers |
| 3 | Overhaul the cooler |
| 4 | Pressure test the coolers |
| 5 | Replace gaskets and seals |
|  | SPACE HEATERS |
| 1 | Test heaters |
| 2 | Overhaul heaters (replace wiring) |
| 3 | Replace heaters |
|  | STATOR WINDING |
| 1 | Polish stator foot mounting |
| 2 | Clean and dry stator |
| 3 | Treat and paint stator with anti-rust paint |
| 4 | Check the concentricity of the stator |
| 5 | Rectify or correct the stator concentricity |
| 6 | Replace tail leads (including terminal box and leads-point1) |
| 7 | Reinsulate tail leads |
|  | ROTOR |
| 1 | Treat and paint rotor with anti-rust paint |
| 2 | Balance rotor at operating speed with fan and half key inserted |
| 3 | Polish the journals (NDE) |
| 4 | Polish the journals (DE) |
| 5 | Polish seal landings (NDE) |
| 6 | Polish seal landings (DE) |
| 7 | Polish fan landing (DE) |
| 8 | Polish fan landing (NDE) |
| 9 | Check shaft run out / concentricity |
| 10 | Rectify or correct the rotor concentricity |
| 11 | Micro welding rotor shaft (DE) |
| 12 | Micro welding rotor shaft (NDE) |
| 13 | Brazing of rotor end laminations |
| 14 | Fit new center indicator |
|  | RESISTANCE TEMPERATURE DETECTOR |
| 1 | PT100 resistance test/measure RTD |
| 2 | Install PT100 on the overhang winding (2 per phase, 6 in total) |
|  | DE SHIELD/NDE SHIELD |
| 1 | Replace fixing bolts |

| Item No | Description |
| --- | --- |
|  | BEARINGS |
| 1 | Refurbishment DE bearing housing to fit standard bearing refurbishment specifications |
| 2 | Refurbish NDE bearing housing to fit standard bearing refurbishment specifications |
| 3 | Replace bearing (see nameplate data supplied on SOW for this motor) |
| 4 | Inspect bearing housing |
| 5 | Replace seals |
|  | ACCESSORIES |
| 1 | Fit new internal fans as and when required |
| 2 | Inspect shock absorber rubbers (replace if damaged) |
| 3 | Fit new floating lab seals |
| 4 | Supply new sight glasses |
| 5 | Supply new breathers |
| 6 | Supply new pipe work and ball valves |
| 7 | Fit new set of O-rings |
| 8 | Shotblast, clean and paint the housings |
| 9 | Repair journals and landings |
| 10 | Burn out stator, remove coils and prepare core for rewind |
| 11 | Manufacture new stator coil and insulation rewind kit |
| 12 | Install the new winding kit, VPI and curing |
| 13 | Overhaul air to air canopy |
| 14 | Replace connector blocks |
| 15 | Supply and fit new insulators-triangle type |
| 16 | Balancing test |
| 17 | Copper material analysis test/check |
| 18 | Bearing insulation test |
| 19 | Bearing heat run test and check the bearing temperatures and vibration |
| 20 | Stator winding temperature measurements |
| 21 | Load test the motor and check efficiency |
| 22 | NDT rotor shaft |
| 23 | Manufacture new rotor core |
| 24 | Remove old rotor core and fit new |
| 25 | Machine off rotor short circuiting rings & remove rotor bars |
| 26 | Manufacture new rotor bars & short-circuiting rings |
| 27 | Re-bar rotor complete |
| 28 | Re-insulate DE & NDE bearing housings |
| 29 | Fit earth lugs |
| 30 | Fit new grease pipes & fittings |
| 31 | Re-insulate bearings cap / Manufacture new NDE/DE bearing cap |
| 32 | Manufacture new NDE/DE flinger |
| 33 | Re-tap all mounting holes |
| 34 | Polish spigots |
| 35 | Remove, clean & Re-fit coupling |
| 36 | Re-insulate NDE/DE bearing housings |
| 37 | Fit new lock washers 110mm |

| Item No | Description |
| --- | --- |
| 38 | Fit new earth brush & holder |
| 39 | Repair baffles |
| 40 | Overhaul coupling & re-fit |
| 41 | Overhaul external fan |
| 42 | Skim stator feet |
| 43 | Supply & fit new auxiliary terminal box for heaters |
| 44 | Light machine flingers & cut new threads |
| 45 | Repair rotor shaft threads |
| 46 | Manufacture new stator core – stacked & welded |
| 47 | Line bore stator core for air gap |
| 48 | Machine off rotor end rings & remove rotor bars |
| 49 | Manufacture new rotor end rings & rotor bars |
| 50 | Microweld & machine NDE/DE inner seal landing in different sizes |
| 51 | Microweld & machine NDE/DE outer seal landing in different sizes |
| 52 | Microweld & machine NDE/DE external fan landing in different sizes |
| 53 | Weld & machine NDE/DE bearing cap |
| 54 | Re-tap holes & fit new jacking bolts |
| 55 | Supply & fit new jacking bolts |
| 56 | Weld & machine DE/NDE bearing housing bore to suit shaft - cracked |
| 57 | Replace bearing probes |
| 58 | Fit new grease pipes & fittings |
| 59 | Overhaul fan cowl |
| 60 | Replace current Electric CT’s 3 off |
| 61 | Install current Electric CT’s 3 off (Free issue) |

#### S5 Conveyor Motor 250kW

| Item No | Description |
| --- | --- |
|  | GENERAL |
| 1 | Collect motor from Matimba Power Station |
| 2 | Deliver motor to Matimba Power Station |
| 3 | Open motor, clean and complete assessment report |
| 4 | Assemble motor |
| 5 | Paint complete motor |
|  | TERMINAL BOX AND LEADS |
| 1 | Replace leads |
| 2 | Replace terminal box studs |
| 3 | Supply and replace box gaskets and seals |
| 4 | Replace current Electric CT |
|  | HEAT EXCHANGER |
| 1 | Remove oil from cooler tubes (Clean with solvent) |
| 2 | Replace damping rubbers |
| 3 | Overhaul the cooler |
| 4 | Pressure test the coolers |
| 5 | Replace gaskets and seals |
|  | SPACE HEATERS |

| Item No | Description |
| --- | --- |
| 1 | Test heaters |
| 2 | Replace heaters |
| 3 | Overhaul heaters (replace wiring) |
|  | STATOR HOUSING |
| 1 | Polish stator foot mounting |
| 2 | Clean and dry stator |
| 3 | Treat and paint stator with anti-rust paint |
| 4 | Check the concentricity of the stator |
| 5 | Rectify or correct the stator concentricity |
| 6 | Replace tail leads (including terminal box and leads-point 1) |
| 7 | Reinsulate tail leads |
|  | ROTOR |
| 1 | Treat and paint rotor with anti-rust paint |
| 2 | Balance rotor at operating speed with fan and half key inserted |
| 3 | Polish the journals (NDE) |
| 4 | Polish the journals (DE) |
| 5 | Polish seal landings (NDE) |
| 6 | Polish seal landings (DE) |
| 7 | Polish fan landing (DE) |
| 8 | Polish fan landing (NDE) |
| 9 | Check shaft run out / concentricity |
| 10 | Rectify or correct the rotor concentricity |
| 11 | Micro welding rotor shaft (DE) |
| 12 | Micro welding rotor shaft (NDE) |
| 13 | Fit new mag center indicator |
|  | RESISTANCE TEMPERATURE DETECTOR |
| 1 | PT100 resistance test/ Measure RTD |
| 2 | Install PT100 on the overhang winding (2 per phase, 6 in total) |
|  | DE SHIELD/NDE SHIELD |
| 1 | Replace fixing bolts |
|  | BEARINGS |
| 1 | Refurbish DE bearing housing to fit standard bearing refurbishment specifications |
| 2 | Refurbishment NDE bearing housing to fit standard bearing refurbishment specifications |
| 3 | Replace bearing (see nameplate data supplied on SOW for this motor) |
| 4 | Replace seals |
| 5 | Inspect bearing housing |
|  | ACCESSORIES |
| 1 | Fit new internal fans as and when required |
| 2 | Inspect shock absorber rubbers (replace if damaged) |
| 3 | Fit new floating lab seals |
| 4 | Supply new sight glasses |
| 5 | Supply new breathers |
| 6 | Supply new pipe work and ball valves |

| Item No | Description |
| --- | --- |
| 7 | Fit new set of O-rings |
| 8 | Shotblast, clean and paint the housings |
| 9 | Repair journals and landings |
| 10 | Burn out stator, remove coils and prepare core for rewind |
| 11 | Manufacture new stator coil and insulation rewind kit |
| 12 | Install the new winding kit, VPI and curing |
| 13 | Overhaul air to air canopy |
| 14 | Replace connector blocks |
| 15 | Supply and fit new insulators-triangle type |
| 16 | High voltage test |
| 17 | Copper material analysis test/check |
| 18 | Bearing insulation test |
| 19 | Bearing heat run test and check the bearing temperatures and vibration |
| 20 | Stator winding temperature measurements |
| 21 | Load test the motor and check efficiency |
| 22 | NDT rotor shaft |
| 23 | Manufacture new rotor core |
| 24 | Remove old rotor core and fit new |
| 25 | Machine off rotor short circuiting rings & remove rotor bars |
| 26 | Manufacture new rotor bars & short-circuiting rings |
| 27 | Re-bar rotor complete |
| 28 | Re-insulate DE & NDE bearing housings |
| 29 | Fit earth lugs |
| 30 | Fit new grease pipes & fittings |
| 31 | Re-insulate bearings cap / Manufacture new NDE/DE bearing cap |
| 32 | Manufacture new NDE/DE flinger |
| 33 | Re-tap all mounting holes |
| 34 | Polish spigots |
| 35 | Remove, clean & Re-fit coupling |
| 36 | Re-insulate NDE/DE bearing housings |
| 37 | Fit new lock washers 110mm |
| 38 | Fit new earth brush & holder |
| 39 | Repair baffles |
| 40 | Overhaul coupling & re-fit |
| 41 | Overhaul external fan |
| 42 | Skim stator feet |
| 43 | Supply & fit new auxiliary terminal box for heaters |
| 44 | Light machine flingers & cut new threads |
| 45 | Repair rotor shaft threads |
| 46 | Manufacture new stator core – stacked & welded |
| 47 | Line bore stator core for air gap |
| 48 | Machine off rotor end rings & remove rotor bars |
| 49 | Manufacture new rotor end rings & rotor bars |
| 50 | Microweld & machine NDE/DE inner seal landing in different sizes |
| 51 | Microweld & machine NDE/DE outer seal landing in different sizes |

| Item No | Description |
| --- | --- |
| 52 | Microweld & machine NDE/DE external fan landing in different sizes |
| 53 | Weld & machine NDE/DE bearing cap |
| 54 | Re-tap holes & fit new jacking bolts |
| 55 | Supply & fit new jacking bolts |
| 56 | Weld & machine DE/NDE bearing housing bore to suit shaft - cracked |
| 57 | Replace bearing probes |
| 58 | Fit new grease pipes & fittings |
| 59 | Overhaul fan cowl |
| 60 | Replace current Electric CT’s 3 off |
| 61 | Install current Electric CT’s 3 off (Free issue) |

    - Overland Conveyor Drive Motor 500kW

| Item No | Description |
| --- | --- |
|  | GENERAL |
| 1 | Collect motor from Matimba Power Station |
| 2 | Deliver motor to Matimba Power Station |
| 3 | Open motor, clean and complete assessment report |
| 4 | Assemble motor |
| 5 | Paint complete motor |
|  | TERMINAL BOX AND LEADS |
| 1 | Replace leads |
| 2 | Replace terminal box studs |
| 3 | Supply and replace box gaskets and seals |
| 4 | Replace current Electric CT |
|  | HEATING EXCHANGER |
| 1 | remove oil from cooler tubes (Clean with solvent) |
| 2 | Replace damping rubbers |
| 3 | Overhaul the cooler |
| 4 | Pressure test the cooler |
| 5 | Replace gaskets and seals |
|  | SPACE HEATERS |
| 1 | Test heaters |
| 2 | Overhaul heaters (replace wiring) |
| 3 | Replace heaters |
|  | STATOR HOUSING |
| 1 | Polish stator foot mounting |
| 2 | Clean and dry stator |
| 3 | Treat and paint stator with anti-rust paint |
| 4 | Check the concentricity of the stator |
| 5 | Rectify or correct the stator concentricity |
| 6 | Replace tail leads (including terminal box and leads-point1) |
| 7 | Reinsulate tail leads |
|  | ROTOR |
| 1 | Treat and paint rotor with anti-rust paint |
| 2 | Balance rotor at operating speed with fan and half key inserted |
| 3 | Polish the journals (NDE) |
| 4 | Polish the journals (DE) |
| 5 | Polish seal landings (NDE) |
| 6 | Polish seal landings (DE) |
| 7 | Polish fan landing (DE) |
| 8 | Polish fan landing (NDE) |
| 9 | Check shaft run out / concentricity |
| 10 | Rectify or correct the rotor concentricity |
| 11 | Micro welding rotor shaft (DE) |
| 12 | Micro welding rotor shaft (NDE) |
| 13 | Brazing of rotor end laminations |
| 14 | Fit new mag center indicator |
|  | RESISTANCE TEMPERATURE DETECTOR |
| Item No | Description |
| 1 | PT100 resistance test/ Measure RTD |
| 2 | Install PT100 on the overhang winding (2 per phase, 6 in total) |
|  | DE SHIELD/ NDE SHIELD |
| 1 | Replace fixing bolts |
|  | BEARINGS |
| 1 | Refurbish DE bearing housing to fit standard bearing refurbishment specifications |
| 2 | Refurbishment NDE bearing housing to fit standard bearing refurbishment specifications |
| 3 | Replace bearing (see nameplate data supplied on SOW for this motor) |
| 4 | Replace seals |
| 5 | Inspect bearing housing |
|  | ACCESSORIES |
| 1 | Measure and record Winding Resistance test |
| 2 | Perform and Insulation resistance test |
| 3 | Perform and record Polarization test |
| 4 | Perform and record Tan Delta test |
| 5 | Perform and record off-line Partial Discharge test |
| 6 | Perform wedge tightness test on stator |
| 7 | Perform induction test |
| 8 | Perform stator ELCID test on stator |
| 9 | Perform rotor core ELCID test |
| 10 | NDT on the rotor shaft |
| 11 | NDT on fan impellers or runners (Whole impeller) |
| 12 | Rotor bar to bar test (consider the number of bars per motor) |
| 13 | High voltage test |
| 14 | Balancing test |
| 15 | Copper material analysis test/check |
| 16 | Bearing heat run test and check the bearing temperatures and vibration |
| 17 | Bearing insulation test |
| 18 | Stator winding temperature measurements |
| 19 | Fit new internal fans as and when required |
| 20 | Inspect shock absorber rubbers (replace if damaged) |
| 21 | Fit new floating lab seals |
| 22 | Supply new sight glasses |
| 23 | Supply new breathers |
| 24 | Supply new pipe work and ball valves |
| 25 | Fit new set of O-rings |
| 26 | Shotblast, clean and paint the housings |
| 27 | Repair journals and landings |
| 28 | Burn out stator, remove coils and prepare core for rewind |
| 29 | Manufacture new stator coil and insulation rewind kit |
| 30 | Install the new winding kit, VPI and curing |
| 31 | Overhaul air to air canopy |
| 32 | Replace connector blocks |
| 33 | Supply and fit new insulators-triangle type |
| 34 | NDT rotor shaft |
| 35 | Manufacture new rotor core |
| 36 | Remove old rotor core and fit new |
| 37 | Machine off rotor short circuiting rings & remove rotor bars |
| 38 | Manufacture new rotor bars & short-circuiting rings |
| 39 | Re-bar rotor complete |
| 40 | Re-insulate DE & NDE bearing housings |
| 41 | Fit earth lugs |
| 42 | Fit new grease pipes & fittings |
| 43 | Re-insulate bearings cap / Manufacture new NDE/DE bearing cap |
| 44 | Manufacture new NDE/DE flinger |
| 45 | Re-tap all mounting holes |
| 46 | Polish spigots |
| 47 | Remove, clean & Re-fit coupling |
| 48 | Re-insulate NDE/DE bearing housings |
| 49 | Fit new lock washers 110mm |
| 50 | Fit new earth brush & holder |
| 51 | Repair baffles |
| 52 | Overhaul coupling & re-fit |
| 53 | Overhaul external fan |
| 54 | Skim stator feet |
| 55 | Supply & fit new auxiliary terminal box for heaters |
| 56 | Light machine flingers & cut new threads |
| 57 | Repair rotor shaft threads |
| 58 | Manufacture new stator core – stacked & welded |
| 59 | Line bore stator core for air gap |
| 60 | Machine off rotor end rings & remove rotor bars |
| 61 | Manufacture new rotor end rings & rotor bars |
| 62 | Microweld & machine NDE/DE inner seal landing in different sizes |
| 63 | Microweld & machine NDE/DE outer seal landing in different sizes |
| 64 | Microweld & machine NDE/DE external fan landing in different sizes |
| 65 | Weld & machine NDE/DE bearing cap |
| 66 | Re-tap holes & fit new jacking bolts |
| 67 | Supply & fit new jacking bolts |
| 68 | Weld & machine DE/NDE bearing housing bore to suit shaft - cracked |
| 69 | Replace bearing probes |
| 70 | Supply & fit new grease pipes & fittings |
| 71 | Overhaul fan cowl |
| 72 | Replace current Electric CT’s 3 off |
| 73 | Install current Electric CT’s 3 off (Free issue) |

    - Shiftable Conveyor Drive Motor 250kW

| Item No | Description |
| --- | --- |
|  | GENERAL |
| 1 | Collect motor from Matimba Power Station |
| 2 | Deliver motor to Matimba Power Station |
| 3 | Open motor, clean and complete assessment report |
| 4 | Assemble motor |
| 5 | Paint complete motor |
|  | TERMINAL BOX AND LEADS |
| 1 | Replace leads |
| 2 | Replace terminal box studs |
| 3 | Supply and replace box gaskets and seals |
| 4 | Replace current Electric CT |
|  | HEAT EXCHANGER |
| 1 | Remove oil from cooler tubes (clean with solvent) |
| 2 | Replace damping rubbers (each) |
| 3 | Overhaul the cooler |
| 4 | Pressure test the cooler |
| 5 | Replace gaskets and seals |
|  | SPACE HEATERS |
| 1 | Test heaters |
| 2 | Overhaul heaters (replace wiring) |
| 3 | Replace heaters |
|  | STATOR HOUSING |
| 1 | Polish stator foot mounting |
| 2 | Clean and dry stator |
| 3 | Treat and paint stator with anti-rust paint |
| 4 | Check the concentricity of the stator |
| 5 | Rectify or correct the stator concentricity |
| 6 | Replace tail leads (including terminal box and leads-point 1) |
| 7 | Reinsulate tail leads |
|  | ROTOR |
| 1 | Treat and paint rotor with anti-rust paint |
| 2 | Balance rotor at operating speed with fan and half key inserted |
| 3 | Polish the journals (NDE) |
| Item No | Description |
| 4 | Polish the journals (DE) |
| 5 | Polish seal landings (NDE) |
| 6 | Polish seal landings (DE) |
| 7 | Polish fan landing (DE) |
| 8 | Polish fan landing (NDE) |
| 9 | Check shaft run out / concentricity |
| 10 | Rectify or correct the rotor concentricity |
| 11 | Micro welding rotor shaft (DE) |
| 12 | Micro welding rotor shaft (NDE) |
| 13 | Brazing of rotor end laminations |
| 14 | Fit new center indicator |
|  | RESISTANCE TEMPERATURE DETECTOR |
| 1 | PT100 resistance test/ Measure RTD |
| 2 | Install PT100 on the overhang winding (2 per phase, 6 in total) |
|  | DE SHIELD/ NDE SHIELD |
| 1 | Replace fixing bolts |
|  | BEARINGS |
| 1 | Refurbish DE bearing housing to fit standard bearing refurbishment specifications |
| 2 | Refurbish NDE bearing housing to fit standard bearing refurbishment specifications |
| 3 | Replace bearing (see nameplate data supplied on SOW for this motor) |
| 4 | Replace seals |
| 5 | Inspect bearing housing |
|  | ACCESSORIES |
| 1 | Measure and record Winding Resistance test |
| 2 | Perform and record Insulation resistance test |
| 3 | Perform and record Polarization test |
| 4 | Perform and record Tan Delta test |
| 5 | Perform and record off-line Partial Discharge test |
| 6 | Perform wedge tightness test on stator |
| 7 | Perform induction test |
| 8 | Perform stator ELCID test on stator |
| 9 | Perform rotor core ELCID test |
| 10 | NDT on the rotor shaft |
| 11 | NDT on fan impellers or runners (Whole impeller) |
| 12 | Rotor bar to bar test (consider the number of bars per motor) |
| 13 | High voltage test |
| 14 | Balancing test |
| 15 | Copper analysis test/check |
| 16 | Bearing insulation test |
| 17 | Bearing heat run test and check the bearing temperatures and vibration |
| 18 | Stator winding temperature measurements |
| 19 | Fit new internal fans as and when required |
| 20 | Inspect shock absorber rubbers (replace if damaged) |
| 21 | Fit new floating lab seals |
| 22 | Supply new sight glasses |
| 23 | Supply new breathers |
| 24 | Supply new pipe work and ball valves |
| 25 | Fit new set of O-rings |
| 26 | Shotblast, clean and paint the housings |
| 27 | Repair journals and landings |
| 28 | Burn out stator, remove coils and prepare core for rewind |
| 29 | Manufacture new stator coil and insulation rewind kit |
| 30 | Install the new winding kit, VPI and curing |
| 31 | Overhaul air to air canopy |
| 32 | Replace connector blocks |
| 33 | Supply and fit new insulators-triangle type |
| 34 | NDT rotor shaft |
| 35 | Manufacture new rotor core |
| 36 | Remove old rotor core and fit new |
| 37 | Machine off rotor short circuiting rings & remove rotor bars |
| 38 | Manufacture new rotor bars & short-circuiting rings |
| 39 | Re-bar rotor complete |
| 40 | Re-insulate DE & NDE bearing housings |
| 41 | Fit earth lugs |
| 42 | Fit new grease pipes & fittings |
| 43 | Re-insulate bearings cap / Manufacture new NDE/DE bearing cap |
| 44 | Manufacture new NDE/DE flinger |
| 45 | Re-tap all mounting holes |
| 46 | Polish spigots |
| 47 | Remove, clean & Re-fit coupling |
| 48 | Re-insulate NDE/DE bearing housings |
| 49 | Fit new lock washers 110mm |
| 50 | Fit new earth brush & holder |
| 51 | Repair baffles |
| 52 | Overhaul coupling & re-fit |
| 53 | Overhaul external fan |
| 54 | Skim stator feet |
| 55 | Supply & fit new auxiliary terminal box for heaters |
| 56 | Light machine flingers & cut new threads |
| 57 | Repair rotor shaft threads |
| 58 | Manufacture new stator core – stacked & welded |
| 59 | Line bore stator core for air gap |
| 60 | Machine off-rotor end rings & remove rotor bars |
| 61 | Manufacture new rotor end rings & rotor bars |
| 62 | Microweld & machine NDE/DE inner seal landing in different sizes |
| 63 | Microweld & machine NDE/DE outer seal landing in different sizes |
| 64 | Microweld & machine NDE/DE external fan landing in different sizes |
| 65 | Weld & machine NDE/DE bearing cap |
| 66 | Re-tap holes & fit new jacking bolts |
| 67 | Supply & fit new jacking bolts |
| 68 | Weld & machine DE/NDE bearing housing bore to suit shaft - cracked |
| 69 | Replace bearing probes |
| 70 | Supply fit new grease pipes & fittings |
| 71 | Overhaul fan cowl |
| 72 | Replace current Electric CT’s 3 off |
| 73 | Install current Electric CT’s 3 off (Free issue) |

#### Extendable Conveyor Drive Motor 185kW

| Item No | Description |
| --- | --- |
|  | GENERAL |
| 1 | Collect motor from Matimba Power Station |
| 2 | Deliver motor to Matimba Power Station |
| 3 | Open motor, clean and complete assessment report |
| 4 | Assemble motor |
| 5 | Paint complete motor |
|  | TERMINAL BEX AND LEADS |
| 1 | Replace leads |
| 2 | Replace terminal box studs |
| 3 | Supply and replace box gaskets and seals |
| 4 | Replace current Electric CT |
|  | HEAT EXCHANGER |
| 1 | Remove oil from cooler tubes (Clean with solvent) |
| 2 | Replace damping rubbers |
| 3 | Overhaul the cooler |
| 4 | Pressure test the coolers |
| 5 | Replace gaskets and seals |
|  | SPACE HEATERS |
| 1 | Test heaters |
| 2 | Overhaul the heaters (replace wiring) |
| 2 | Replace heaters |
|  | STATOR HOUSING |
| 1 | Polish stator foot mounting |
| 2 | Clean and dry stator |
| 3 | Treat and paint stator with anti-rust paint |
| 4 | Check the concentricity of the stator |
| 5 | Rectify or correct the stator concentricity |
| 6 | Replace tail leads (including terminal box and leads-point1) |
| 7 | Reinsulate tail leads |
|  | ROTOR |
| 1 | Treat and paint rotor with anti-rust paint |
| 2 | Balance rotor at operating speed with fan and half key inserted |
| 3 | Polish the journals (NDE) |
| 4 | Polish the journals (DE) |
| Item No | Description |
| 5 | Polish seal landings (NDE) |
| 6 | Polish seal landings (DE) |
| 7 | Polish fan landing (DE) |
| 8 | Polish fan landing (NDE) |
| 9 | Check shaft run out / concentricity |
| 10 | Rectify or correct the rotor concentricity |
| 11 | Micro welding rotor shaft (DE) |
| 12 | Micro welding rotor shaft (NDE) |
| 13 | Brazing of rotor end laminations |
| 14 | Fit new mag center indicator |
|  | RESISTANCE TEMPERATURE DETECTOR |
| 1 | PT100 resistance test/ Measure RTD |
| 2 | Install PT100 on the overhang winding (2 per phase, 6 in total) |
|  | DE SHIELD AND NDE SHIELD |
| 1 | Replace fixing bolts |
|  | ACCESSORIES |
| 1 | Fit new internal fans as and when required |
| 2 | Inspect shock absorber rubbers (replace if damaged) |
| 3 | Fit new floating lab seals |
| 4 | Supply new sight glasses |
| 5 | Supply new breathers |
| 6 | Supply new pipe work and ball valves |
| 7 | Fit new set of O-rings |
| 8 | Shotblast, clean and paint the housings |
| 9 | Repair journals and landings |
| 10 | Burn out stator, remove coils and prepare core for rewind |
| 11 | Manufacture new stator coil and insulation rewind kit |
| 12 | Install the new winding kit, VPI and curing |
| 13 | Overhaul air to air canopy |
| 14 | Replace connector blocks |
| 15 | Supply and fit new insulators-triangle type |
| 16 | Perform stator ELCID test on stator |
| 17 | Perform rotor core ELCID test |
| 18 | NDT on the rotor shaft |
| 19 | NDT on fan impellers or runners (Whole impeller) |
| 20 | Perform Rotor bar to bar test (consider the number of bars per motor) |
| 21 | High voltage test |
| 22 | Balancing test |
| 23 | Copper analysis test/check |
| 24 | Bearing heat run test and check the bearing temperatures and vibration |
| 25 | Stator winding temperature measurements |
| 26 | Bearing insulation rest |
| 27 | Load test the motor and check efficiency |
| 28 | NDT rotor shaft |
| 29 | Manufacture new rotor core |
| 30 | Remove old rotor core and fit new |
| 31 | Machine off rotor short circuiting rings & remove rotor bars |
| 32 | Manufacture new rotor bars & short-circuiting rings |
| 33 | Re-bar rotor complete |
| 34 | Re-insulate DE & NDE bearing housings |
| 35 | Fit earth lugs |
| 36 | Fit new grease pipes & fittings |
| 37 | Re-insulate bearings cap / Manufacture new NDE/DE bearing cap |
| 38 | Manufacture new NDE/DE flinger |
| 39 | Re-tap all mounting holes |
| 40 | Polish spigots |
| 41 | Remove, clean & Re-fit coupling |
| 42 | Re-insulate NDE/DE bearing housings |
| 43 | Fit new lock washers 110mm |
| 44 | Fit new earth brush & holder |
| 45 | Repair baffles |
| 46 | Overhaul coupling & re-fit |
| 47 | Overhaul external fan |
| 48 | Skim stator feet |
| 49 | Supply & fit new auxiliary terminal box for heaters |
| 50 | Light machine flingers & cut new threads |
| 51 | Repair rotor shaft threads |
| 52 | Manufacture new stator core – stacked & welded |
| 53 | Line bore stator core for air gap |
| 54 | Machine off rotor end rings & remove rotor bars |
| 55 | Manufacture new rotor end rings & rotor bars |
| 56 | Microweld & machine NDE/DE inner seal landing in different sizes |
| 57 | Microweld & machine NDE/DE outer seal landing in different sizes |
| 58 | Microweld & machine NDE/DE external fan landing in different sizes |
| 59 | Weld & machine NDE/DE bearing cap |
| 60 | Re-tap holes & fit new jacking bolts |
| 61 | Supply & fit new jacking bolts |
| 62 | Weld & machine DE/NDE bearing housing bore to suit shaft - cracked |
| 63 | Replace bearing probes |
| 64 | Fit new grease pipes & fittings |
| 65 | Overhaul fan cowl |
| 66 | Polish DE/NDE bearing housings to specification |
| 67 | Manufacture new grease slinger NDE/DE |
| 68 | Supply & fit new DE/NDE bearings, seals circlips (NU 322 C3 & 6322 C3) |
| 69 | Microweld & machine DE/NDE coupling landing & cut keyway in different sizes |
| 70 | Microweld & machine DE/NDE fan landing & cut keyway in different sizes |
| 71 | Replace current Electric CT’s 3 off |
| 72 | Install current Electric CT’s 3 off (Free issue) |

#### T8 Incline Conveyor Drive Motor 260kW

| Item No | Description |
| --- | --- |
|  | GENERAL |
| Item No | Description |
| 1 | Collect motor from Matimba Power Station |
| 2 | Deliver motor to Matimba Power Station |
| 3 | Open motor, clean and complete assessment report |
| 4 | Assemble motor |
| 5 | Paint complete motor |
|  | TERMINAL BOX AND LEADS |
| 1 | Replace leads |
| 2 | Replace terminal box studs |
| 3 | Supply and replace box gaskets and seals |
| 4 | Replace current Electric CT |
|  | HEAT EXCHANGER |
| 1 | Remove oil from cooler tubes (clean with solvent) |
| 2 | Replace damping rubbers |
| 3 | Overhaul the cooler |
| 4 | Pressure test the cooler |
| 5 | Replace gaskets and seals |
|  | SPACE HEATERS |
| 1 | Test heaters |
| 2 | Overhaul the heaters (replace wiring) |
| 3 | Replace heaters |
|  | STATOR HOUSING |
| 1 | Polish stator foot mounting |
| 2 | Clean and dry stator |
| 3 | Treat and paint stator with anti-rust paint |
| 4 | Check the concentricity of the stator |
| 5 | Rectify or correct the stator concentricity |
| 6 | Replace tail leads (including terminal box and leads-point1) |
| 7 | Reinsulate tail leads |
|  | ROTOR |
| 1 | Treat and paint rotor with anti-rust paint |
| 2 | Balance rotor at operating speed with fan and half key inserted |
| 3 | Polish the journals (NDE) |
| 4 | Polish the journals (DE) |
| 5 | Polish seal landings (NDE) |
| 6 | Polish seal landings (DE) |
| 7 | Polish fan landing (DE) |
| 8 | Polish fan landing (NDE) |
| 9 | Check shaft run out / concentricity |
| 10 | Rectify or correct the rotor concentricity |
| 11 | Micro welding rotor shaft (DE) |
| 12 | Micro welding rotor shaft (NDE) |
| 13 | Brazing of rotor end laminations |
| 14 | Fit new mag center indicator |
|  | RESISTANCE TEMPERATURE DETECTOR |
| 1 | PT100 resistance test/ Measure RTD |
| 2 | Install PT100 on the overhang winding (2 per phase, 6 in total) |
|  | DE SHIELD/ NDE SHIELD |
| 1 | Replace fixing bolts |
|  | BEARINGS |
| 1 | Refurbish DE bearing housing to fit standard bearing refurbishment specifications |
| 2 | Refurbish NDE bearing housing to fit standard bearing refurbishment specifications |
| 3 | Replace bearing (see nameplate data supplied on SOW for this motor) |
| 4 | Replace seals |
| 5 | Inspect bearing housing |
|  | ACCESSORIES |
| 1 | Fit new internal fans as and when required |
| 2 | Inspect shock absorber rubbers (replace if damaged) |
| 3 | Fit new floating lab seals |
| 4 | Supply new sight glasses |
| 5 | Supply new breathers |
| 6 | Supply new pipe work and ball valves |
| 7 | Fit new set of O-rings |
| 8 | Shotblast, clean and paint the housings |
| 9 | Repair journals and landings |
| 10 | Burn out stator, remove coils and prepare core for rewind |
| 11 | Manufacture new stator coil and insulation rewind kit |
| 12 | Install the new winding kit, VPI and curing |
| 13 | Overhaul air to air canopy |
| 14 | Replace connector blocks |
| 15 | Supply and fit new insulators-triangle type |
| 16 | Copper analysis test/check |
| 17 | Bearing insulation test |
| 18 | Stator winding temperature measurements |
| 19 | High voltage test |
| 20 | Bearing heat run test and check the bearing temperatures and vibration |
| 21 | Load test the motor and check efficiency |
| 22 | NDT rotor shaft |
| 23 | Manufacture new rotor core |
| 24 | Remove old rotor core and fit new |
| 25 | Machine off rotor short circuiting rings & remove rotor bars |
| 26 | Manufacture new rotor bars & short-circuiting rings |
| 27 | Re-bar rotor complete |
| 28 | Re-insulate DE & NDE bearing housings |
| 29 | Fit earth lugs |
| 30 | Fit new grease pipes & fittings |
| 31 | Re-insulate bearings cap / Manufacture new NDE/DE bearing cap |
| 32 | Manufacture new NDE/DE flinger |
| 33 | Re-tap all mounting holes |
| 34 | Polish spigots |
| 35 | Remove, clean & Re-fit coupling |
| 36 | Re-insulate NDE/DE bearing housings |
| 37 | Fit new lock washers 110mm |
| 38 | Fit new earth brush & holder |
| 39 | Repair baffles |
| 40 | Overhaul coupling & re-fit |
| 41 | Overhaul external fan |
| 42 | Skim stator feet |
| 43 | Supply & fit new auxiliary terminal box for heaters |
| 44 | Light machine flingers & cut new threads |
| 45 | Repair rotor shaft threads |
| 46 | Manufacture new stator core – stacked & welded |
| 47 | Line bore stator core for air gap |
| 48 | Machine off rotor end rings & remove rotor bars |
| 49 | Manufacture new rotor end rings & rotor bars |
| 50 | Microweld & machine NDE/DE inner seal landing in different sizes |
| 51 | Microweld & machine NDE/DE outer seal landing in different sizes |
| 52 | Microweld & machine NDE/DE external fan landing in different sizes |
| 53 | Weld & machine NDE/DE bearing cap |
| 54 | Re-tap holes & fit new jacking bolts |
| 55 | Supply & fit new jacking bolts |
| 56 | Weld & machine DE/NDE bearing housing bore to suit shaft - cracked |
| 57 | Replace bearing probes |
| 58 | Fit new grease pipes & fittings |
| 59 | Overhaul fan cowl |
| 60 | Replace current Electric CT’s 3 off |
| 61 | Install current Electric CT’s 3 off (Free issue) |

    - Shiftable Conveyor Drive Motor 185kW

|  | Description |
| --- | --- |
|  | GENERAL |
| 1 | Collect motor from Matimba Power Station |
| 2 | Deliver motor to Matimba Power Station |
| 3 | Open motor, clean and complete assessment report |
| 4 | Assemble motor |
| 5 | Paint complete motor |
|  | TERMINAL BEX AND LEADS |
| 1 | Replace leads |
| 2 | Replace terminal box studs |
| 3 | Supply and replace box gaskets and seals |
| 4 | Replace current Electric CT |
|  | HEAT EXCHANGER |
| 1 | Remove oil from cooler tubes (Clean with solvent) |
| 2 | Replace damping rubbers |
|  | Description |
| 3 | Overhaul the cooler |
| 4 | Pressure test the coolers |
| 5 | Replace gaskets and seals |
|  | SPACE HEATERS |
| 1 | Test heaters |
| 2 | Overhaul the heaters (replace wiring) |
| 2 | Replace heaters |
|  | STATOR HOUSING |
| 1 | Polish stator foot mounting |
| 2 | Clean and dry stator |
| 3 | Treat and paint stator with anti-rust paint |
| 4 | Check the concentricity of the stator |
| 5 | Rectify or correct the stator concentricity |
| 6 | Replace tail leads (including terminal box and leads-point1) |
| 7 | Reinsulate tail leads |
|  | ROTOR |
| 1 | Treat and paint rotor with anti-rust paint |
| 2 | Balance rotor at operating speed with fan and half key inserted |
| 3 | Polish the journals (NDE) |
| 4 | Polish the journals (DE) |
| 5 | Polish seal landings (NDE) |
| 6 | Polish seal landings (DE) |
| 7 | Polish fan landing (DE) |
| 8 | Polish fan landing (NDE) |
| 9 | Check shaft run out / concentricity |
| 10 | Rectify or correct the rotor concentricity |
| 11 | Micro welding rotor shaft (DE) |
| 12 | Micro welding rotor shaft (NDE) |
| 13 | Brazing of rotor end laminations |
| 14 | Fit new mag center indicator |
|  | RESISTANCE TEMPERATURE DETECTOR |
| 1 | PT100 resistance test/ Measure RTD |
| 2 | Install PT100 on the overhang winding (2 per phase, 6 in total) |
|  | DE SHIELD AND NDE SHIELD |
| 1 | Replace fixing bolts |
|  | ACCESSORIES |
| 1 | Fit new internal fans as and when required |
| 2 | Inspect shock absorber rubbers (replace if damaged) |
| 3 | Fit new floating lab seals |
| 4 | Supply new sight glasses |
| 5 | Supply new breathers |
| 6 | Supply new pipe work and ball valves |
| 7 | Fit new set of O-rings |
| 8 | Shotblast, clean and paint the housings |
|  | Description |
| 9 | Repair journals and landings |
| 10 | Burn out stator, remove coils and prepare core for rewind |
| 11 | Manufacture new stator coil and insulation rewind kit |
| 12 | Install the new winding kit, VPI and curing |
| 13 | Overhaul air to air canopy |
| 14 | Replace connector blocks |
| 15 | Supply and fit new insulators-triangle type |
| 16 | Perform stator ELCID test on stator |
| 17 | Perform rotor core ELCID test |
| 18 | NDT on the rotor shaft |
| 19 | NDT on fan impellers or runners (Whole impeller) |
| 20 | Perform Rotor bar to bar test (consider the number of bars per motor) |
| 21 | High voltage test |
| 22 | Balancing test |
| 23 | Copper analysis test/check |
| 24 | Bearing heat run test and check the bearing temperatures and vibration |
| 25 | Stator winding temperature measurements |
| 26 | Bearing insulation rest |
| 27 | Load test the motor and check efficiency |
| 28 | NDT rotor shaft |
| 29 | Manufacture new rotor core |
| 30 | Remove old rotor core and fit new |
| 31 | Machine off rotor short circuiting rings & remove rotor bars |
| 32 | Manufacture new rotor bars & short-circuiting rings |
| 33 | Re-bar rotor complete |
| 34 | Re-insulate DE & NDE bearing housings |
| 35 | Fit earth lugs |
| 36 | Fit new grease pipes & fittings |
| 37 | Re-insulate bearings cap / Manufacture new NDE/DE bearing cap |
| 38 | Manufacture new NDE/DE flinger |
| 39 | Re-tap all mounting holes |
| 40 | Polish spigots |
| 41 | Remove, clean & Re-fit coupling |
| 42 | Re-insulate NDE/DE bearing housings |
| 43 | Fit new lock washers 110mm |
| 44 | Fit new earth brush & holder |
| 45 | Repair baffles |
| 46 | Overhaul coupling & re-fit |
| 47 | Overhaul external fan |
| 48 | Skim stator feet |
| 49 | Supply & fit new auxiliary terminal box for heaters |
| 50 | Light machine flingers & cut new threads |
| 51 | Repair rotor shaft threads |
| 52 | Manufacture new stator core – stacked & welded |
| 53 | Line bore stator core for air gap |
| 54 | Machine off-rotor end rings & remove rotor bars |
| 55 | Manufacture new rotor end rings & rotor bars |
| 56 | Microweld & machine NDE/DE inner seal landing in different sizes |
| 57 | Microweld & machine NDE/DE outer seal landing in different sizes |
| 58 | Microweld & machine NDE/DE external fan landing in different sizes |
| 59 | Weld & machine NDE/DE bearing cap |
| 60 | Re-tap holes & fit new jacking bolts |
| 61 | Supply & fit new jacking bolts |
| 62 | Weld & machine DE/NDE bearing housing bore to suit shaft - cracked |
| 63 | Replace bearing probes |
| 64 | Fit new grease pipes & fittings |
| 65 | Overhaul fan cowl |
| 66 | Polish DE/NDE bearing housings to specification |
| 67 | Manufacture new grease slinger NDE/DE |
| 68 | Supply & fit new DE/NDE bearings, seals circlips (NU 322 C3 & 6322 C3) |
| 69 | Microweld & machine DE/NDE coupling landing & cut keyway in different sizes |
| 70 | Microweld & machine DE/NDE fan landing & cut keyway in different sizes |
| 71 | Replace current Electric CT’s 3 off |
| 72 | Install current Electric CT’s 3 off (Free issue) |

#### Auxiliary Colling Pump Motor 450kW

| Item No | Description |
| --- | --- |
|  | GENERAL |
| 1 | Collect motor from Matimba Power Station |
| 2 | Deliver motor to Matimba Power Station |
| 3 | Open motor, clean and complete assessment report |
| 4 | Assemble motor |
| 5 | Paint complete motor |
|  | TERMINAL BOX AND LEADS |
| 1 | Replace leads |
| 2 | Replace terminal box studs |
| 3 | Supply and replace box gaskets and seals |
| 4 | Replace current Electric CT |
|  | HEAT EXCHANGER |
| 1 | Remove oil from cooler tubes (clean with solvent) |
| 2 | Replace damping rubbers |
| 3 | Overhaul the cooler |
| 4 | Pressure test the coolers |
| 5 | Replace gaskets and seals |
|  | SPACE HEATERS |
| 1 | Test heaters |
| 2 | Replace heaters |
| 3 | Overhaul the heater (Replace wiring) |
|  | STATOR HOUSING |
| 1 | Polish stator foot mounting |
| 2 | Clean and dry stator |
| Item No | Description |
| 3 | Treat and paint stator with anti-rust paint |
| 4 | Check the concentricity of the stator |
| 5 | Rectify or correct the stator concentricity |
| 6 | Replace tail leads (including terminal box and leads- point1) |
| 7 | Reinsulate tail leads |
|  | ROTOR |
| 1 | Treat and paint rotor with anti-rust paint |
| 2 | Balance rotor at operating speed with fan and half key inserted |
| 3 | Polish the journals (NDE) |
| 4 | Polish the journals (DE) |
| 5 | Polish seal landings (NDE) |
| 6 | Polish seal landings (DE) |
| 7 | Polish fan landing (DE) |
| 8 | Polish fan landing (NDE) |
| 9 | Check shaft run out / concentricity |
| 10 | Rectify or correct the rotor concentricity |
| 11 | Micro welding rotor shaft (DE) |
| 12 | Micro welding rotor shaft (NDE) |
| 13 | Brazing of rotor end laminations |
| 14 | Fit new mag center indicator |
|  | DE SHIELD/ NDE SHIELD |
| 1 | Replace fixing bolts |
|  | RESISTANCE TEMPERATURE DETECTOR |
| 1 | PT100 resistance test/ measure RTD |
| 2 | Install PT100 on the overhang winding (2 per phase, 6 in total) |
|  | BEARINGS |
| 1 | Refurbish DE bearing housing to fit standard bearing refurbishment specifications |
| 2 | Refurbishment NDE bearing housing to fit standard bearing refurbishment specifications |
| 3 | Replace bearing (see nameplate data supplied on SOW for this motor) |
| 4 | Replace seals |
| 5 | Inspect bearing housing |
|  | ACCESSORIES |
| 1 | Fit new internal fans as and when required |
| 2 | Inspect shock absorber rubbers (replace if damaged) |
| 3 | Fit new floating lab seals |
| 4 | Supply new sight glasses |
| 5 | Supply new breathers |
| 6 | Supply new pipe work and ball valves |
| 7 | Fit new set of O-rings |
| 8 | Shotblast, clean and paint the housings |
| 9 | Repair journals and landings |
| 10 | Burn out stator, remove coils and prepare core for rewind |
| 11 | Manufacture new stator coil and insulation rewind kit |
| 12 | Install the new winding kit, VPI and curing |
| 13 | Overhaul air to air canopy |
| 14 | Replace connector blocks |
| 15 | Supply and fit new insulators-triangle type |
| 16 | Copper analysis test/check |
| 17 | Bearing insulation test |
| 18 | High voltage test |
| 19 | Stator winding temperature measurements |
| 20 | Bearing heat run test and check the bearing temperatures and vibration |
| 21 | Load test the motor and check efficiency |
| 22 | NDT rotor shaft |
| 23 | Manufacture new rotor core |
| 24 | Remove old rotor core and fit new |
| 25 | Machine off rotor short circuiting rings & remove rotor bars |
| 26 | Manufacture new rotor bars & short-circuiting rings |
| 27 | Re-bar rotor complete |
| 28 | Re-insulate DE & NDE bearing housings |
| 29 | Fit earth lugs |
| 30 | Fit new grease pipes & fittings |
| 31 | Re-insulate bearings cap / Manufacture new NDE/DE bearing cap |
| 32 | Manufacture new NDE/DE flinger |
| 33 | Re-tap all mounting holes |
| 34 | Polish spigots |
| 35 | Remove, clean & Re-fit coupling |
| 36 | Re-insulate NDE/DE bearing housings |
| 37 | Fit new lock washers 110mm |
| 38 | Fit new earth brush & holder |
| 39 | Repair baffles |
| 40 | Overhaul coupling & re-fit |
| 41 | Overhaul external fan |
| 42 | Skim stator feet |
| 43 | Supply & fit new auxiliary terminal box for heaters |
| 44 | Light machine flingers & cut new threads |
| 45 | Repair rotor shaft threads |
| 46 | Manufacture new stator core – stacked & welded |
| 47 | Line bore stator core for air gap |
| 48 | Machine off rotor end rings & remove rotor bars |
| 49 | Manufacture new rotor end rings & rotor bars |
| 50 | Microweld & machine NDE/DE inner seal landing in different sizes |
| 51 | Microweld & machine NDE/DE outer seal landing in different sizes |
| 52 | Microweld & machine NDE/DE external fan landing in different sizes |
| 53 | Weld & machine NDE/DE bearing cap |
| 54 | Re-tap holes & fit new jacking bolts |
| 55 | Supply & fit new jacking bolts |
| 56 | Weld & machine DE/NDE bearing housing bore to suit shaft - cracked |
| 57 | Replace bearing probes |
| 58 | Fit new grease pipes & fittings |
| 59 | Overhaul fan cowl |
| 60 | Polish DE/NDE bearing housings to specification |
| 61 | Manufacture new grease slinger NDE/DE |
| 62 | Supply & fit new DE/NDE bearings, seals circlips (NU 322 C3 & 6322 C3) |
| 63 | Microweld & machine DE/NDE coupling landing & cut keyway in different sizes |
| 64 | Microweld & machine DE/NDE fan landing & cut keyway in different sizes |
| 65 | Replace current Electric CT’s 3 off |
| 66 | Install current Electric CT’s 3 off (Free issue) |

    - Compressor Motor 310kW

| Item No | Description |
| --- | --- |
|  | GENERAL |
| 1 | Collect motor from Matimba Power Station |
| 2 | Deliver motor to Matimba Power Station |
| 3 | Open motor, clean and complete assessment report |
| 4 | Assemble motor |
| 5 | Paint complete motor |
|  | TERMINAL BOX AND LEADS |
| 1 | Replace leads |
| 2 | Replace terminal box studs |
| 3 | Supply and replace box gaskets and seals |
| 4 | Replace current Electric CT |
|  | HEAT EXCHANGER |
| 1 | remove oil from cooler tubes (clean with solvent) |
| 2 | Replace damping rubbers (each) |
| 3 | Overhaul the cooler |
| 4 | Pressure test the cooler |
| 5 | Replace gaskets and seals |
|  | SPACE HEATERS |
| 1 | Test heaters |
| 2 | Overhaul heaters (replace wiring) |
| 3 | Replace heaters |
|  | STATOR HOUSING |
| 1 | Polish stator foot mounting |
| 2 | Clean and dry stator |
| 3 | Treat and paint stator with anti-rust paint |
| 4 | Check the concentricity of the stator |
| 5 | Rectify or correct the stator concentricity |
| 6 | Replace tail leads (including terminal box and leads-point1) |
| 7 | Reinsulate tail leads |
|  | ROTOR |
| 1 | Treat and paint rotor with anti-rust paint |
| 2 | Balance rotor at operating speed with fan and half key inserted |
| Item No | Description |
| 3 | Polish the journals (NDE) |
| 4 | Polish the journals (DE) |
| 5 | Polish seal landings (NDE) |
| 6 | Polish seal landings (DE) |
| 7 | Polish fan landing (DE) |
| 8 | Polish fan landing (NDE) |
| 9 | Check shaft run out / concentricity |
| 10 | Rectify or correct the rotor concentricity |
| 11 | Micro welding rotor shaft (DE) |
| 12 | Micro welding rotor shaft (NDE) |
| 13 | Brazing of rotor end laminations |
| 14 | Fit new mag center indicator |
|  | DE SHIELD/ NDE SHIELD |
| 1 | Replace fixing bolts |
|  | BEARINGS |
| 1 | Refurbish DE bearing housing to fit standard bearing refurbishment specifications |
| 2 | Refurbishment NDE bearing housing to fit standard bearing refurbishment specifications |
| 3 | Replace bearing (see nameplate data supplied on SOW for this motor) |
| 4 | Replace seals |
| 5 | Inspect bearing housing |
|  | RESISTANCE TEMPERATURE DETECTOR |
| 1 | PT100 resistance test/ measure RTD |
| 2 | Install PT100 on the overhang winding (2 per phase, 6 in total) |
|  | ACCESSORIES |
| 1 | Fit new internal fans as and when required |
| 2 | Inspect shock absorber rubbers (replace if damaged) |
| 3 | Fit new floating lab seals |
| 4 | Supply new sight glasses |
| 5 | Supply new breathers |
| 6 | Supply new pipe work and ball valves |
| 7 | Fit new set of O-rings |
| 8 | Shotblast, clean and paint the housings |
| 9 | Repair journals and landings |
| 10 | Burn out stator, remove coils and prepare core for rewind |
| 11 | Manufacture new stator coil and insulation rewind kit |
| 12 | Install the new winding kit, VPI and curing |
| 13 | Overhaul air to air canopy |
| 14 | Replace connector blocks |
| 15 | Supply and fit new insulators-triangle type |
| 16 | Balancing test |
| 17 | Copper material analysis test/check |
| 18 | Bearing insulation test |
| 19 | Bearing heat run test and check the bearing temperatures and vibration |
| 20 | Stator winding temperature measurements |
| 21 | Load test the motor and check efficiency |
| 22 | NDT rotor shaft |
| 23 | Manufacture new rotor core |
| 24 | Remove old rotor core and fit new |
| 25 | Machine off rotor short circuiting rings & remove rotor bars |
| 26 | Manufacture new rotor bars & short-circuiting rings |
| 27 | Re-bar rotor complete |
| 28 | Re-insulate DE & NDE bearing housings |
| 29 | Fit earth lugs |
| 30 | Fit new grease pipes & fittings |
| 31 | Re-insulate bearings cap / Manufacture new NDE/DE bearing cap |
| 32 | Manufacture new NDE/DE flinger |
| 33 | Re-tap all mounting holes |
| 34 | Polish spigots |
| 35 | Remove, clean & Re-fit coupling |
| 36 | Re-insulate NDE/DE bearing housings |
| 37 | Fit new lock washers 110mm |
| 38 | Fit new earth brush & holder |
| 39 | Repair baffles |
| 40 | Overhaul coupling & re-fit |
| 41 | Overhaul external fan |
| 42 | Skim stator feet |
| 43 | Supply & fit new auxiliary terminal box for heaters |
| 44 | Light machine flingers & cut new threads |
| 45 | Repair rotor shaft threads |
| 46 | Manufacture new stator core – stacked & welded |
| 47 | Line bore stator core for air gap |
| 48 | Machine off-rotor end rings & remove rotor bars |
| 49 | Manufacture new rotor end rings & rotor bars |
| 50 | Microweld & machine NDE/DE inner seal landing in different sizes |
| 51 | Microweld & machine NDE/DE outer seal landing in different sizes |
| 52 | Microweld & machine NDE/DE external fan landing in different sizes |
| 53 | Weld & machine NDE/DE bearing cap |
| 54 | Re-tap holes & fit new jacking bolts |
| 55 | Supply & fit new jacking bolts |
| 56 | Weld & machine DE/NDE bearing housing bore to suit shaft - cracked |
| 57 | Replace bearing probes |
| 58 | Fit new grease pipes & fittings |
| 59 | Overhaul fan cowl |
| 60 | Polish DE/NDE bearing housings to specification |
| 61 | Manufacture new grease slinger NDE/DE |
| 62 | Supply & fit new DE/NDE bearings, seals circlips (NU 322 C3 & 6322 C3) |
| 63 | Microweld & machine DE/NDE coupling landing & cut keyway in different sizes |
| 64 | Microweld & machine DE/NDE fan landing & cut keyway in different sizes |
| 65 | Replace current Electric CT’s 3 off |
| 66 | Install current Electric CT’s 3 off (Free issue) |

#### Extraction Pump Motor 1150kw

|  | Description |
| --- | --- |
|  | GENERAL |
| 1 | Collect motor from Matimba Power Station |
| 2 | Deliver motor to Matimba Power Station |
| 3 | Open motor, clean and complete assessment report |
| 4 | Assemble motor |
| 5 | Paint complete motor |
|  | TERMINAL BOX AND LEADS |
| 1 | Replace leads |
| 2 | Replace terminal box studs |
| 3 | Supply and replace box gaskets and seals |
| 4 | Replace current Electric CT |
|  | HEAT EXCHANGER |
| 1 | Remove oil from cooler tubes (clean with solvent) |
| 2 | Replace damping rubbers |
| 3 | Overhaul the cooler |
| 4 | Pressure test the cooler |
| 5 | Replace gaskets and seals |
|  | SPACE HEATERS |
| 1 | Test heaters |
| 3 | Overhaul heaters (replace wiring) |
| 2 | Replace heaters |
|  | STATOR HOUSING |
| 1 | Polish stator foot mounting |
| 2 | Clean and dry stator |
| 3 | Treat and paint stator with anti-rust paint |
| 4 | Check the concentricity of the stator |
| 5 | Rectify or correct the stator concentricity |
| 6 | Replace tail leads (including terminal box and leads-point1) |
| 7 | Reinsulate tail leads |
|  | ROTOR |
| 1 | Treat and paint rotor with anti-rust paint |
| 2 | Balance rotor at operating speed with fan and half key inserted |
| 3 | Polish the journals (NDE) |
| 4 | Polish the journals (DE) |
| 5 | Polish seal landings (NDE) |
| 6 | Polish seal landings (DE) |
| 7 | Polish fan landing (DE) |
| 8 | Polish fan landing (NDE) |
| 9 | Check shaft run out / concentricity |
| 10 | Rectify or correct the rotor concentricity |
| 11 | Micro welding rotor shaft (DE) |
| 12 | Micro welding rotor shaft (NDE) |
| 13 | Brazing of rotor end laminations |
| 14 | Fit new mag center indicator |
|  | RESISTANCE TEMPERATURE DETECTOR |
| 1 | PT100 resistance test/ measure RTD |
| 2 | Install PT100 on the overhang winding (DE and NDE) |
|  | DE SHIELD/ NDE SHIELD |
| 1 | Replace fixing bolts |
|  | BEARINGS |
| 1 | Refurbish DE bearing housing to fit standard bearing refurbishment specifications |
| 2 | Refurbishment bearing housing to fit standard bearing refurbishment specifications |
| 3 | Replace bearing (see nameplate data supplied on SOW for this motor) |
| 4 | Replace seals |
| 5 | Inspect bearing housing |
|  | ACCESSORIES |
| 1 | Fit new internal fans as and when required |
| 2 | Inspect shock absorber rubbers (replace if damaged) |
| 3 | Fit new floating lab seals |
| 4 | Supply new sight glasses |
| 5 | Supply new breathers |
| 6 | Supply new pipe work and ball valves |
| 7 | Fit new set of O-rings |
| 8 | Shotblast, clean and paint the housings |
| 9 | Repair journals and landings |
| 10 | Burn out stator, remove coils and prepare core for rewind |
| 11 | Manufacture new stator coil and insulation rewind kit |
| 12 | Install the new winding kit, VPI and curing |
| 13 | Overhaul air to air canopy |
| 14 | Replace connector blocks |
| 15 | Supply and fit new insulators-triangle type |
| 16 | Balancing test |
| 17 | Copper material analysis test/check |
| 18 | Bearing insulation test |
| 19 | Bearing heat run test and check the bearing temperatures and vibration |
| 20 | Stator winding temperature measurements |
| 21 | Load test the motor and check efficiency |
| 22 | NDT rotor shaft |
| 23 | Drill and dowl DE/NDE bearing housings end shield before dismantling |
| 24 | Re-sleeve NDE/DE bearing housings |
| 25 | Re-fit motor to transport stand |
| 26 | Fit new O rings |
| 27 | Pressure test second cooler |
| 28 | Re-tap all mounting holes |
| 29 | Polish DE/NDE caps and flange spigots |
| 30 | Clean grease pipe fitting & replace nipples |
| 31 | Fit new earth lugs |
| 32 | Overhaul internal fan |
| 33 | Overhaul stator and spray with insulation varnish |
| 34 | Overhaul DE/NDE bearing housings |
| 35 | Drill and dell motor and supply new pin |
| 36 | Microweld and machine DE/NDE coupling landing and journal in different sizes |
| 37 | Microweld & machine NDE/DE inner seal landing in different sizes |
| 38 | Microweld & machine NDE/DE outer seal landing in different sizes |
| 39 | Microweld & machine NDE/DE external fan landing in different sizes |
| 40 | Fit new lock washers (2) |
| 41 | Fit new desicator |
| 42 | Fit 3 fiber glass inserts |
| 43 | Fit new automatic grease feeder 2 off |
| 44 | Additional bearing for NDE/DE 7320 C3 |
| 45 | Replace current Electric CT’s 3 off |
| 46 | Install current Electric CT’s 3 off (Free issue) |

    - Cross Conveyor Drive Motor 260kW

| Item No | Description |
| --- | --- |
|  | GENERAL |
| 1 | Collect motor from Matimba Power Station |
| 2 | Deliver motor to Matimba Power Station |
| 3 | Open motor, clean and complete assessment report |
| 4 | Assemble motor |
| 5 | Paint complete motor |
|  | TERMINAL BOX AND LEADS |
| 1 | Replace leads |
| 2 | Replace terminal box studs |
| 3 | Supply and replace box gaskets and seals |
| 4 | Replace current Electric CT |
|  | HEAT EXCHANGER |
| 1 | Remove oil from cooler tubes (clean with solvent) |
| 2 | Replace damping rubbers |
| 3 | Overhaul the cooler |
| 4 | Pressure test the cooler |
| 5 | Replace gaskets and seals |
|  | SPACE HEATERS |
| 1 | Test heaters |
| 2 | Overhaul heater (replace wiring) |
| 2 | Replace heaters |
|  | STATOR HOUSING |
| 1 | Polish stator foot mounting |
| 2 | Clean and dry stator |
| 3 | Treat and paint stator with anti-rust paint |
| 4 | Check the concentricity of the stator |
| 5 | Rectify or correct the stator concentricity |
| 6 | Replace tail leads |
| 7 | Reinsulate tail leads |
|  | ROTOR |
| 1 | Treat and paint rotor with anti-rust paint |
| 2 | Balance rotor at operating speed with fan and half key inserted |
| 3 | Polish the journals (NDE) |
| 4 | Polish the journals (DE) |
| 5 | Polish seal landings (NDE) |
| 6 | Polish seal landings (DE) |
| 7 | Polish fan landing (DE) |
| 8 | Polish fan landing (NDE) |
| 9 | Check shaft run out / concentricity |
| 10 | Rectify or correct the rotor concentricity |
| 11 | Micro welding rotor shaft (DE) |
| 12 | Micro welding rotor shaft (NDE) |
| 13 | Brazing of rotor end laminations |
| 14 | Fit new mag center indicator |
|  | DE SHIELD/ NDE SHIELD |
| 1 | Replace fixing bolts |
|  | BEARINGS |
| 1 | Refurbish DE bearing housing to fit standard bearing refurbishment specifications |
| 2 | Refurbishment NDE bearing housing to fit standard bearing refurbishment specifications |
| 3 | Replace bearing (see nameplate data supplied on SOW for this motor) |
| 4 | Replace seals |
| 5 | Inspect bearing housing |
|  | RESISTANCE TEMPERATURE DETECTOR |
| 1 | PT100 resistance test/ measure RTD |
| 2 | Install PT100 on the overhang winding (2 per phase, 6 in total) |
|  | ACCESSORIES |
| 1 | Fit new internal fans as and when required |
| 2 | Inspect shock absorber rubbers (replace if damaged) |
| 3 | Fit new floating lab seals |
| 4 | Supply new sight glasses |
| 5 | Supply new breathers |
| 6 | Supply new pipe work and ball valves |
| 7 | Fit new set of O-rings |
| 8 | Shotblast, clean and paint the housings |
| 9 | Repair journals and landings |
| 10 | Burn out stator, remove coils and prepare core for rewind |
| 11 | Manufacture new stator coil and insulation rewind kit |
| 12 | Install the new winding kit, VPI and curing |
| 13 | Overhaul air to air canopy |
| 14 | Replace connector blocks |
| 15 | Supply and fit new insulators-triangle type |
| 16 | Balancing test |
| 17 | Copper material analysis test |
| 18 | Bearing insulation test |
| 19 | Bearing heat run test and check the bearing temperatures and vibration |
| 20 | Stator winding temperature measurement |
| 21 | Load test the motor and check efficiency |
| 22 | NDT rotor shaft |
| 23 | Manufacture new rotor core |
| 24 | Remove old rotor core and fit new |
| 25 | Machine off rotor short circuiting rings & remove rotor bars |
| 26 | Manufacture new rotor bars & short-circuiting rings |
| 27 | Re-bar rotor complete |
| 28 | Re-insulate DE & NDE bearing housings |
| 29 | Fit earth lugs |
| 30 | Fit new grease pipes & fittings |
| 31 | Re-insulate bearings cap / Manufacture new NDE/DE bearing cap |
| 32 | Manufacture new NDE/DE flinger |
| 33 | Re-tap all mounting holes |
| 34 | Polish spigots |
| 35 | Remove, clean & Re-fit coupling |
| 36 | Re-insulate NDE/DE bearing housings |
| 37 | Fit new lock washers 110mm |
| 38 | Fit new earth brush & holder |
| 39 | Repair baffles |
| 40 | Overhaul coupling & re-fit |
| 41 | Overhaul external fan |
| 42 | Skim stator feet |
| 43 | Supply & fit new auxiliary terminal box for heaters |
| 44 | Light machine flingers & cut new threads |
| 45 | Repair rotor shaft threads |
| 46 | Manufacture new stator core – stacked & welded |
| 47 | Line bore stator core for air gap |
| 48 | Machine off-rotor end rings & remove rotor bars |
| 49 | Manufacture new rotor end rings & rotor bars |
| 50 | Microweld & machine NDE/DE inner seal landing in different sizes |
| 51 | Microweld & machine NDE/DE outer seal landing in different sizes |
| 52 | Microweld & machine NDE/DE external fan landing in different sizes |
| 53 | Weld & machine NDE/DE bearing cap |
| 54 | Re-tap holes & fit new jacking bolts |
| 55 | Supply & fit new jacking bolts |
| 56 | Weld & machine DE/NDE bearing housing bore to suit shaft - cracked |
| 57 | Replace bearing probes |
| 58 | Fit new grease pipes & fittings |
| 59 | Overhaul fan cowl |
| 60 | Replace current Electric CT’s 3 off |
| 61 | Install current Electric CT’s 3 off (Free issue) |

    - Forced Cooling Compressor 475KW.

| Item No | Description |
| --- | --- |
|  | GENERAL |
| 1 | Collect motor from Matimba Power Station |
| 2 | Deliver motor to Matimba Power Station |
| 3 | Open motor, clean and complete assessment report |
| 4 | Assemble motor |
| 5 | Paint complete motor |
|  | TERMINAL BOX AND LEADS |
| 1 | Replace leads |
| 2 | Replace terminal box studs |
| 3 | Supply and replace box gaskets and seals |
| 4 | Replace current Electric CT |
|  | HEAT EXCHANGER |
| 1 | Remove oil from cooler tubes |
| 2 | Replace dumping rubbers |
| 3 | Overhaul the cooler |
| 4 | Pressure test the cooler |
| 5 | Replace gaskets and seals |
|  | SPACE HEATERS |
| 1 | Test heaters |
| 2 | Overhaul heaters (replace wiring) |
| 3 | Replace heaters |
|  | STATOR HOUSING |
| 1 | Polish stator foot mounting |
| 2 | Clean and dry stator |
| 3 | Treat and paint stator with anti-rust paint |
| 4 | Check the concentricity of the stator |
| 5 | Replace tail leads |
| 6 | Reinsulate tail leads |
|  | ROTOR |
| 1 | Treat and paint rotor with anti-rust paint |
| 2 | Balance rotor at operating speed with fan and half key inserted |
| 3 | Polish the journals (NDE) |
| 4 | Polish the journals (DE) |
| 5 | Polish seal landings (NDE) |
| 6 | Polish seal landings (DE) |
| 7 | Polish fan landing (DE) |
| 8 | Polish fan landing (NDE) |
| 9 | Check shaft run out / concentricity |
| 10 | Rectify or correct the rotor concentricity |
| 11 | Micro welding rotor shaft (DE) |
| 12 | Micro welding rotor shaft (NDE) |
| 13 | Brazing of rotor end laminations |
| 14 | Fit new mag center indicator |
|  | RESISTANCE TEMPERATURE DETECTOR |
| 1 | PT100 resistance test/measure RTD |
| 2 | Install PT100 on the overhang winding (2 per phase, 6 in total) |
|  | ACCESSORIES |
| 1 | Fit new internal fans as and when required |
| 2 | Inspect shock absorber rubbers (replace if damaged) |
| 3 | Fit new floating lab seals |
| 4 | Supply new sight glasses |
| 5 | Supply new breathers |
| 6 | Supply new pipe work and ball valves |
| 7 | Fit new set of O-rings |
| 8 | Shotblast, clean and paint the housings |
| 9 | Repair journals and landings |
| 10 | Burn out stator, remove coils and prepare core for rewind |
| 11 | Manufacture new stator coil and insulation rewind kit |
| 12 | Install the new winding kit, VPI and curing |
| 13 | Overhaul air to air canopy |
| 14 | Replace connector blocks |
| 15 | Supply and fit new insulators-triangle type |
| 16 | Perform and record Polarization test |
| 17 | Perform and record Tan Delta test |
| 18 | Perform and record off-line Partial Discharge test |
| 19 | Perform wedge tightness test on stator |
| 20 | Perform stator ELCID test on stator |
| 21 | Perform rotor core ELCID test |
| 22 | Perform induction test |
| 23 | NDT on the rotor shaft |
| 24 | NDT on fan impellers or runners (Whole impeller) |
| 25 | Perform Rotor bar to bar test (consider the number of bars per rotor) |
| 26 | Ultrasonic testing on white metal bearing surface |
| 27 | High voltage test |
| 28 | Balancing test |
| 29 | Copper material analysis test /check |
| 30 | Bearing insulation test |
| 31 | Bearing heat run test and check the bearing temperatures and vibration |
| 32 | Stator winding temperature measurements |
| 33 | Load test the motor and check efficiency |
| 33 | NDT rotor shaft |
| 34 | Manufacture new rotor core |
| 35 | Remove old rotor core and fit new |
| 36 | Machine off rotor short circuiting rings & remove rotor bars |
| 37 | Manufacture new rotor bars & short-circuiting rings |
| 38 | Re-bar rotor complete |
| 39 | Re-insulate DE & NDE bearing housings |
| 40 | Fit earth lugs |
| 41 | Fit new grease pipes & fittings |
| 42 | Re-insulate bearings cap / Manufacture new NDE/DE bearing cap |
| 43 | Manufacture new NDE/DE flinger |
| 44 | Re-tap all mounting holes |
| 45 | Polish spigots |
| 46 | Remove, clean & Re-fit coupling |
| 47 | Re-insulate NDE/DE bearing housings |
| 48 | Fit new lock washers 110mm |
| 49 | Fit new earth brush & holder |
| 50 | Repair baffles |
| 51 | Overhaul coupling & re-fit |
| 52 | Overhaul external fan |
| 53 | Skim stator feet |
| 54 | Supply & fit new auxiliary terminal box for heaters |
| 55 | Light machine flingers & cut new threads |
| 56 | Repair rotor shaft threads |
| 57 | Manufacture new stator core – stacked & welded |
| 58 | Line bore stator core for air gap |
| 59 | Machine off rotor end rings & remove rotor bars |
| 60 | Manufacture new rotor end rings & rotor bars |
| 61 | Microweld & machine NDE/DE inner seal landing in different sizes |
| 62 | Microweld & machine NDE/DE outer seal landing in different sizes |
| 63 | Microweld & machine NDE/DE external fan landing in different sizes |
| 64 | Weld & machine NDE/DE bearing cap |
| 65 | Re-tap holes & fit new jacking bolts |
| 66 | Supply & fit new jacking bolts |
| 67 | Weld & machine DE/NDE bearing housing bore to suit shaft - cracked |
| 68 | Replace bearing probes |
| 69 | Fit new grease pipes & fittings |
| 70 | Overhaul fan cowl |
| 71 | Replace current Electric CT’s 3 off |
| 72 | Install current Electric CT’s 3 off (Free issue) |

| Item No | Description | qty | unit price | Amount (R) |
| --- | --- | --- | --- | --- |
| Perform onsite fault finding as and when required |  |  |  |  |
| 1 | Estimating to five times per year | 5 |  |  |

Note: The resources assigned to perform onsite fault-finding as and when required will be expected to provide and carry their own appropriate tools and equipment necessary to perform alignment and address other related technical issues associated with all motors included in the SOW.

# PART 3: SCOPE OF WORK

| Document reference | Title | No of pages |
| --- | --- | --- |
|  | This cover page | 1 |
| C3.1 | Employer’s Service Information |  |
| C3.2 | Contractor’s Service Information |  |
|  | Total number of pages |  |

# C3.1: EMPLOYER’S SERVICE INFORMATION

## Contents

When the document is complete, insert a ‘Table of Contents’. To do this go to:   Insert, → Reference, → Index and tables → Table of Contents. Three levels and the title (but not the subtitle) may be shown if the formats used in this template are retained.

Otherwise insert list of contents manually.

Part 3: Scope of Work	1

C3.1: Employer’s service Information	2

- Description of the service	4

  - Executive overview	4

  - Employer’s requirements for the service	4

  - Interpretation and terminology	4

  - Contract Requirements & Specification	5

- Management strategy and start up	14

  - The Contractor’s plan for the service	14

  - Management meetings	14

  - Contractor’s management, supervision and key people	15

  - Provision of bonds and guarantees	15

  - Documentation control	15

  - Invoicing and payment	15

  - Contract change management	15

  - Records of Defined Cost to be kept by the Contractor	16

  - Insurance provided by the Employer	16

  - Training workshops and technology transfer	16

  - Design and supply of Equipment	16

  - Things provided at the end of the service period for the Employer’s use	16

    - Equipment	16

    - Information and other things	16

  - Management of work done by Task Order	17

- Health and safety, the environment and quality assurance	17

  - Health and safety risk management	17

  - Environmental constraints and management	17

  - Quality assurance requirements	18

- Procurement	18

  - People	18

    - Minimum requirements of people employed	18

    - BBBEE and preferencing scheme	18

    - Accelerated Shared Growth Initiative – South Africa (ASGI-SA)	18

  - Subcontracting	18

    - Preferred subcontractors	18

    - Subcontract documentation, and assessment of subcontract tenders	18

    - Limitations on subcontracting	19

    - Attendance on subcontractors	19

  - Plant and Materials	19

    - Specifications	19

    - Correction of defects	19

    - Contractor’s procurement of Plant and Materials	19

    - Tests and inspections before delivery	19

    - Plant & Materials provided “free issue” by the Employer	19

    - Cataloguing requirements	19

- Working on the Affected Property	19

  - Employer’s site entry and security control, permits, and site regulations	20

  - People restrictions, hours of work, conduct and records	20

  - Health and safety facilities on the Affected Property	20

  - Environmental controls, fauna & flora	20

  - Cooperating with and obtaining acceptance of Others	20

  - Records of Contractor’s Equipment	20

  - Equipment provided by the Employer	20

  - Site services and facilities	20

    - Provided by the Employer	20

    - Provided by the Contractor	20

  - Control of noise, dust, water and waste	21

  - Hook ups to existing works	21

  - Tests and inspections	21

    - Description of tests and inspections	21

    - Materials facilities and samples for tests and inspections	21

- List of drawings	21

  - Drawings issued by the Employer	21

- Description of the service

### Executive overview

The works covers transportation to and from Matimba Power Station, stripping, assessment, refurbishment, overhaul, rewind, testing, compile failure reports and supply of test certificates for refurbishment of MV induction motors.

The Employer has limited design information on the motors. The contractor shall obtain all the design and manufacturing details required for the works. On completion of the works, motors shall be delivered to and offloaded at Matimba Power Station Main stores (or venue preferred by the employer).

  - Employer’s requirements for the service

    - The preliminary scope of work covered by this contract is as follows:

      - Transportation of motors from Matimba Power Station to the contractor’s works and back to site at Matimba Power Station after completion of works. The supplier accepts full responsibility for the motor/s when the motor/s is handed over to the supplier on site to be transported from matimba site for refurbishment. Any additional damage during transport or during stripping, testing, assessment, refurbishment and re-assemble will be for the supplier’s account and could include the cost for a new motor in the worst-case scenario.

      - Strip the motor and mark all part with unique relevant job number.

      - Do a full assessment of the motor condition, and complete assessment sheet, ensuring that any evidence of failure or deterioration is kept for review by the employer, if not present during assessment.

      - The complete assessment report will determine the detailed scope of work for refurbishment; refer to Appendix 1 for assessment form.

      - Execute the scope of work on each individual motor as approved by employer, including the relevant Engineering work as detailed in paragraph 1.6. Ensure that quality management is incorporated in refurbishment process as defined in approved Process Quality Plan's (PQP’s).

      - Should the motor be found to be beyond repair, and the employer concurs with the finding, the contractor will be required to re-assemble the motor and return the motor to Matimba Power Station accompanied by a full breakdown report on the findings and motivation for beyond repair status.

      - Where additional test or work, not covered by the contract, is required from the motor assessment, a quotation must be submitted to Matimba Power Station before any commencement of such activities.

      - The employer reserves the right to do a price matching of any additional work specified in the assessment report, with the intent to ensure market related pricing of additional work.

      - During the Matimba Switchgear Project implementation, the contractor shall supply (Current Transformers) CTs for the motors mentioned in the contract. Specifications will be given during the implementation.

If required include here definitions additional to those used in the conditions of contract which are required only for the purpose of making the Service Information easier to draft and read. Also list abbreviations used and provide a full interpretation of each one, for example:

Interpretation and terminology

The following abbreviations are used in this Service Information:

| Abbreviations | Explanation |
| --- | --- |
| AC | Alternating Current |
| KPA | Key performance area |
| KPI | Key performance indicators |
| DC | Direct Current |
| DE | Drive End |
| IBI | Integrated Business Improvement Model |
| MV | Medium Voltage |
| MM | Material Management |
| NDE | Non- drive end |
| SOS/SOW | Scope of service/ Scope of work |
| OEM | Original Equipment Manufacture |
| PPE | Personal protective equipment |
| QC | Quality control |

### Contract Requirements & Specification

The motors covered by this contract are as follows;

The works are to be carried out at the contractor’s yard on the following Matimba Medium Voltage motors. The name plate data has been given for the purpose of quoting.

| ITEM NO | ALLOCATION: | AUXILARY COOLING PUMP MOTOR |  | ITEM NO | ALLOCATION: | COMPRESSOR MOTOR |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | MAKE | HAWKER SIDLEY |  | 2 | MAKE | HAWKER SIDLEY |
|  | kW | 450 |  |  | kW | 310 |
|  | POLE | 4 |  |  | POLE | 4 |
|  | VOLTS | 3300 |  |  | VOLTS | 3300 |
|  | AMPS | 98 |  |  | AMPS | 77.5 |
|  | RPM | 1474 |  |  | RPM | 1474 |
|  | FRAME SIZE | NA315L30 |  |  | FRAME SIZE | NA355830 |
|  | DE BEARINGS | NU322 CM |  |  | DE BEARINGS | NU322 |
|  | NDE BEARINGS | 6322 |  |  | NDE BEARINGS | 6322 |
|  | WEIGHT | 4500 KG |  |  | WEIGHT | 3100KG |

| ITEM NO | ALLOCATION: | EXTENDABLE /SHIFTABLE 15 CONVEYOR DRIVE MOTOR |  | ITEM NO | ALLOCATION: | COMPRESSOR MOTOR |
| --- | --- | --- | --- | --- | --- | --- |
| 3 | MAKE | WEG |  | 4 | MAKE | ACTOM |
|  | kW | 185 |  |  | kW | 310 |
|  | POLE | 4 |  |  | POLE | 8 |
|  | VOLTS | 3300 |  |  | VOLTS | 3300 |

|  | AMPS | 40.7 |  |  | AMPS | 71 |
| --- | --- | --- | --- | --- | --- | --- |
|  | RPM | 1485 |  |  | RPM | 741 |
|  | FRAME SIZE/TYPE | HGF 315L/A/B |  |  | FRAME SIZE/TYPE | UDX355/100 |
|  | DE BEARINGS | NU322-C3 |  |  | DE BEARINGS | NU324 ECM |
|  | NDE BEARINGS | 6316-C3 |  |  | NDE BEARINGS | 6324 C3 |
|  | WEIGHT | 1977 KG |  |  | WEIGHT | 3100KG |

| ITEM NO | ALLOCATION | CROSS CONVEYOR DRIVE MOTOR |  | ITEM NO | ALLOCATION | EXTENDABLE /SHIFTABLE 15 CONVEYOR DRIVE MOTOR |
| --- | --- | --- | --- | --- | --- | --- |
| 5 | MAKE | HAWKER SIDLEY |  | 6 | MAKE | HAWKER SIDLEY |
|  | kW | 260 |  |  | kW | 185 |
|  | POLE | 4 |  |  | POLE | 4 |
|  | VOLTS | 3 300 |  |  | VOLTS | 3300 |
|  | AMPS | 57.5 |  |  | AMPS | 41.5 |
|  | RPM | 1 488 |  |  | RPM | 1488 |
|  | FRAME SIZE/TYPE | D355/30 |  |  | FRAME SIZE/TYPE | D315L |
|  | DE BEARINGS | N224 |  |  | DE BEARINGS | NU322 |
|  | NDE BEARINGS | 6224 |  |  | NDE BEARINGS | 6322 |
|  | WEIGHT | 2600 KG |  |  | WEIGHT | 1850KG |

| ITEM NO | ALLOCATION | EXTRACTION PUMP MOTOR |  | ITEM NO | ALLOCATION | EXTRACTION PUMP MOTOR |
| --- | --- | --- | --- | --- | --- | --- |
| 7 | MAKE | MITSUBUSHI |  | 8 | MAKE | ACTOM |
|  | Kw | 1150 |  |  | Kw | 1150 |
|  | POLE | 4 |  |  | POLE | 4 |
|  | VOLTS | 6600 |  |  | VOLTS | 6600 |
|  | AMPS | 118 |  |  | AMPS | 118 |
|  | RPM | 1485 |  |  | RPM | 1485 |
|  | FRAME SIZE/TYPE | F4KE |  |  | FRAME SIZE/TYPE | F4KE |
|  | DE BEARINGS | 6226 CM |  |  | DE BEARINGS | 6226 C3 |
|  | NDE BEARINGS | 7320 BT |  |  | NDE BEARINGS | 2 X 7320 BECBM |
|  | WEIGHT | 11500 KG |  |  | WEIGHT | 5 500KG |

| ITEM NO | ALLOCATION | FD FAN MOTOR |  | ITEM NO | ALLOCATION | FD FAN MOTOR |
| --- | --- | --- | --- | --- | --- | --- |
| 9 | MAKE | ABB |  | 10 | MAKE | BBC |
|  | Kw | 2310 |  |  | Kw | 2310 |
|  | POLE | 8 |  |  | POLE | 8 |
|  | VOLTS | 6600 |  |  | VOLTS | 6600 |

|  | AMPS | 233 |  |  | AMPS | 238 |
| --- | --- | --- | --- | --- | --- | --- |
|  | RPM | 743 |  |  | RPM | 744 |
|  | FRAME SIZE/TYPE | BQWGH710/8-163 |  |  | FRAME SIZE/TYPE | QWG 710 IA8 |
|  | DE BEARINGS | WHITE METAL BEARING |  |  | DE BEARINGS | WHITE METAL BEARING |
|  | NDE BEARINGS | WHITE METAL BEARING |  |  | NDE BEARINGS | WHITE METAL BEARING |
|  | WEIGHT | 11 482 KG |  |  | WEIGHT | 11 100 KG |

| ITEM NO | ALLOCATION | ID FAN MOTOR |  | ITEM NO | ALLOCATION | ID FAN MOTOR |
| --- | --- | --- | --- | --- | --- | --- |
| 11 | MAKE | BBC |  | 12 | MAKE | ABB |
|  | kW | 3720 |  |  | kW | 3850 |
|  | POLE | 10 |  |  | POLE | 10 |
|  | VOLTS | 6600 |  |  | VOLTS | 6600 |
|  | AMPS | 395 |  |  | AMPS | 395 |
|  | RPM | 597 |  |  | RPM | 597 |
|  | FRAME SIZE/TYPE | QWG 900HA10 |  |  | FRAME SIZE/TYPE | BQWGH900/10-233 |
|  | DE BEARINGS | WHITE METAL BEARING |  |  | DE BEARINGS | WHITE METAL BEARING |
|  | NDE BEARINGS | WHITE METAL BEARING |  |  | NDE BEARINGS | WHITE METAL BEARING |
|  | WEIGHT | 21 100 KG |  |  | WEIGHT | 24 300kg |

| ITEM NO | ALLOCATION | MILL MOTOR |  |  | ITEM NO | ALLOCATION | OVERLAND CONVERYOR MTR | DRIVE |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 13 | MAKE | BBC |  |  | 14 | MAKE | ACTOM |  |
|  | kW | 2150 |  |  |  | kW | 500 |  |
|  | POLE | 6 |  |  |  | POLE | 4 |  |
|  | VOLTS | 6600 |  |  |  | VOLTS | 3300 |  |
|  | AMPS | 224 |  |  |  | AMPS | 106 |  |
|  | RPM | 993 |  |  |  | RPM | 1481 |  |
|  | FRAME SIZE/TYPE | QLGY 710 IA6 |  |  |  | FRAME SIZE/TYPE | UDX355/125 |  |
|  | DE BEARINGS | WHITE BEARING | METAL |  |  | DE BEARINGS | ROLLER BEARING |  |
|  | NDE BEARINGS | WHITE BEARING | METAL |  |  | NDE BEARINGS | BALL BEARING |  |
|  | WEIGHT | 11 400 KG |  |  |  | WEIGHT | 3260 |  |

| ITEM NO |  | ALLOCATION | OVERLAND CONVERYOR DRIVE MTR |  | ITEM NO |  | ALLOCATION | PA FAN MOTOR |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 15 |  | MAKE | HAWKER SIDLEY |  | 16 |  | MAKE | BBT |
|  | kW |  | 500 |  |  | kW |  | 2350 |
|  | POLE |  | 4 |  |  | POLE |  | 6 |
|  | VOLTS |  | 3300 |  |  | VOLTS |  | 6600 |
|  | AMPS |  | 112 |  |  | AMPS |  | 244 |
|  | RPM |  | 1482 |  |  | RPM |  | 993 |
|  | FRAME SIZE/TYPE |  | ME355M28 |  |  | FRAME SIZE/TYPE |  | QWG 630 KB6 |
|  | DE BEARINGS |  | NU322 |  |  | DE BEARINGS |  | WHITE METAL BEARING |
|  | NDE BEARINGS |  | 6322 |  |  | NDE BEARINGS |  | WHITE METAL BEARING |
|  | WEIGHT |  | 5000 KG |  |  | WEIGHT |  | 8990 KG |

| ITEM NO | ALLOCATION | PA FAN MOTOR |  | ITEM NO | ALLOCATION | T1 CONVEYOR MOTOR |
| --- | --- | --- | --- | --- | --- | --- |
| 17 | MAKE | ABB |  | 18 | MAKE | ACTOM |
|  | kW | 2395 |  |  | kW | 820 |
|  | POLE | 6 |  |  | POLE | 4 |
|  | VOLTS | 6600 |  |  | VOLTS | 3300 |
|  | AMPS | 243 |  |  | AMPS | 169 |
|  | RPM | 993 |  |  | RPM | 1485 |
|  | FRAME SIZE/TYPE | BQWGH630/6-183 |  |  | FRAME SIZE/TYPE | 2LM3852-01 |
|  | DE BEARINGS | WHITE METAL BEARING |  |  | DE BEARINGS | 100MM SLEEVE |
|  | NDE BEARINGS | WHITE METAL BEARING |  |  | NDE BEARINGS | 100MM SLEEVE |
|  | WEIGHT | 10 040 KG |  |  | WEIGHT | 3 620 KG |

| ITEM NO | ALLOCATION | T1 CONVEYOR MOTOR |  | ITEM NO | ALLOCATION | T8 INCLINE CONVEYOR MOTOR |
| --- | --- | --- | --- | --- | --- | --- |
| 19 | MAKE | GEC |  | 20 | MAKE | HAWKER SIDLEY |
|  | kW | 820 |  |  | kW | 260 |
|  | POLE | 4 |  |  | POLE | 4 |
|  | VOLTS | 3300 |  |  | VOLTS | 3300 |
|  | AMPS | 172 |  |  | AMPS | 56 |
|  | RPM | 1481 |  |  | RPM | 1486 |
|  | FRAME SIZE | UD355/100 |  |  | FRAME SIZE | D355L |
|  | DE BEARINGS | 100MM SLEEVE |  |  | DE BEARINGS | NU324 |
|  | NDE BEARINGS | 100MM SLEEVE |  |  | NDE BEARINGS | 6324 |
|  | WEIGHT | 8 200 KG |  |  | WEIGHT | 2600 KG |

| ITEM NO | ALLOCATION | S1 CONVERYOR MOTOR |  | ITEM NO | ALLOCATION | S2 CONVERYOR MOTOR |
| --- | --- | --- | --- | --- | --- | --- |
| 21 | MAKE | HAWKER SIDLEY |  | 22 | MAKE | HAWKER SIDLEY |
|  | kW | 700 |  |  | kW | 200 |
|  | POLE | 4 |  |  | POLE | 4 |
|  | VOLTS | 3300 |  |  | VOLTS | 3 300 |
|  | AMPS | 163.3 |  |  | AMPS | 48.5 |
|  | RPM | 1485 |  |  | RPM | 1 488 |
|  | FRAME SIZE | NA355L34 |  |  | FRAME SIZE | D315L6 |
|  | DE BEARINGS | NU322 |  |  | DE BEARINGS | N318 |
|  | NDE BEARINGS | 6322 |  |  | NDE BEARINGS | 6318 |
|  | WEIGHT | 7000 KG |  |  | WEIGHT | 2000 KG |

| ITEM NO | ALLOCATION | S3 CONVERYOR MOTOR |  | ITEM NO | ALLOCATION | S4 CONVERYOR MOTOR |
| --- | --- | --- | --- | --- | --- | --- |
| 23 | MAKE | HAWKER SIDLEY |  | 24 | MAKE | HAWKER SIDLEY |
|  | kW | 275 |  |  | kW | 320 |
|  | POLE | 4 |  |  | POLE | 4 |
|  | VOLTS | 3300 |  |  | VOLTS | 3300 |
|  | AMPS | 60 |  |  | AMPS | 70 |
|  | RPM | 1489 |  |  | RPM | 1 488 |
|  | FRAME SIZE | D355/32 |  |  | FRAME SIZE | D335/34 |
|  | DE BEARINGS | N224 |  |  | DE BEARINGS | 224 |
|  | NDE BEARINGS | 6224 |  |  | NDE BEARINGS | 6224 |
|  | WEIGHT | 2750 KG |  |  | WEIGHT | 3200 KG |

| ITEM NO | ALLOCATION | S5 CONVERYOR MOTOR |  | ITEM NO | ALLOCATION | SHIFTABLE 25 CONVEYOR DRIVE MTR |
| --- | --- | --- | --- | --- | --- | --- |
| 25 | MAKE | HAWKER SIDLEY |  | 26 | MAKE | HAWKER SIDLEY |
|  | kW | 250 |  |  | kW | 250 |
|  | POLE | 4 |  |  | POLE | 4 |
|  | VOLTS | 3300 |  |  | VOLTS | 3 300 |
|  | AMPS | 50 |  |  | AMPS | 55.9 |
|  | RPM | 1489 |  |  | RPM | 1 488 |
|  | FRAME SIZE | D355/30 |  |  | FRAME SIZE | D355M |
|  | DE BEARINGS | N3224 |  |  | DE BEARINGS | NU322C3 |
|  | NDE BEARINGS | 6224 |  |  | NDE BEARINGS | 6322C3 |
|  | WEIGHT | 2500 KG |  |  | WEIGHT | 2500 KG |

| ITEM NO | ALLOCATION: | FORCED COOLING COMPRESSOR |
| --- | --- | --- |
| 1 | MAKE | MITSUBISHI ELECTRIC |
|  | kW | 475 |
|  | POLE | 4 |
|  | VOLTS | 3300 |
|  | AMPS | 97 |
|  | RPM | 2970 |
|  | FRAME SIZE | 400LL |
|  | DE BEARINGS | NU318C3 |
|  | NDE BEARINGS | 6318C3 |
|  | WEIGHT | 3040 KG |

MOTOR ADDITIONAL SPECIFICATION

| Description | ID | FD | PA | Mill |
| --- | --- | --- | --- | --- |
| Standard DE Journal size (mm) | 260 | 190 | 170 | 190 |
| Standard NDE Journal size (mm) | 260 | 190 | 150 | 190 |
| Standard DE Bearing size (mm) | 260.257 | 190.199 | 170.191 | 190.21 |
| Standard NDE Bearing size (mm) | 260.257 | 190.199 | 150.168 | 190.21 |
| Minimum DE Bearing/Journal Clearance | .257 | .199 | .191 | .213 |
| Minimum NDE Bearing/Journal Clearance | .257 | .199 | .168 | .213 |
| Maximum DE Bearing/Journal Clearance | .367 | .284 | .273 | .305 |
| Maximum NDE Bearing/Journal Clearance | .367 | .284 | .241 | .305 |

Dismantling

Dismantling of the motor should not commence until the required checks and test have been carried out by repairer and accepted by Eskom representative.

Testing

Approved qualified personnel are used for testing and inspection. The test report before and after repair, form part of the quality documentation of repair. All test certificates to be supplied on delivery of motors to site, otherwise motor will not be accepted on site.

Test to be performed at the repair workshop before disassembly and after assembly:

The high voltage test will only be performed after the stator passed the polarization index test (refer to the acceptance criteria). All high voltage tests to be authorised by the employer prior to testing. (Test subject to employer’s request and approval)

MV motors to be repairs/refurbish as per the following Eskom documents;

240-89217674 Refurbishment and Repair of Power Station Electrical Motors Work Instruction Rev 2.

240-87739380 Motor Repair and Refurbishment Assessment Form (Rev 2).

## Engineering Services as Required by Eskom Generation Standard

The Contractor is responsible for engineering services, material and labour as follows:

Verify the performance matching requirements of the power supply and driven machine.

- Inspection and testing of the motor prior to and after repairs, recording, reporting and making recommendations and providing the necessary information where applicable.

- The contractor is required to provide detailed breakdown report for each motor clearly stating the contributory and root causes of motor failure.

- Evaluate of parts for possible re-use.

- Select, design and procurement of new components, ensuring that replacement insulation system and other material are compiled with the existing materials. If the replacements parts are not exactly as the originals, the contractor demonstrate that the replacement meets or exceeds the capability of the original in all essential requirements.

- The contractor must ensure that the employer (Contract Manager) and others (Motor System Engineer) are present during dismantling, testing and assessment to inspect any evidence of failure or aspects of defective design or workmanship uncovered. Ensure that correct photographic records are made.

- Establish the suitability of the motor for rewinding to achieve the life extension required by the Employer. Perform all tests, investigations and calculation required for these purpose.

- Redesigning to eliminate weaknesses. Submitting a written report recording the defects and detailing the extent of repair and work required to achieve the life extension specified by the Employer. Obtaining the Employer’s prior agreement in writing for the extent of repair and work to be done.

- Design replacement stator windings when necessary or specified, with the required wedging (by means of using new poromat type of wedges which are porous, swellable, rigid and made of glass mat) and coil end-winding support systems, including means of tightening if looseness develops. The means of tightening is agreed with the Employer.

- Design a replacement system for stator temperature monitoring, if necessary or specified by the Employer.

- Design the supply and installation of bus couplers for on-line partial discharge monitoring, if specified.

- Design the supply and installation of slot couplers for on-line partial discharge monitoring, if specified.

- Where changes to the design or rating are necessary, carrying out design review and validation of the rating and suitability of the motor for the applicable environment and cooling arrangements. Where changes are introduced, carrying out design calculations of motor capability and appropriate settings for over-current protection, repeated start protection, stall protection, voltage unbalance protection, and other protection applied or required. Submission of design results and proposed protection settings to the Employer for agreement.

- Where changes to the design are made, producing details of the design, working drawings, repair and rewinding instructions and procedures, as well as all necessary amendments to operating and maintenance manuals) producing agreed procedures for works inspection and tests, and site commissioning and testing, all with details of acceptance criteria to be attained. Producing quality plans for the activities concerned before commencing work. Producing progress reports as required periodically by the Employer.

- Submit details of the redesign and all drawings and documentation in quadruplicate to the Employer for agreement.

- Produce a consolidated report on all aspects of the work, incorporating all reports, data, acceptance criteria, and quality assurance records.

- GB Bearings (Pty) Ltd has been approved as an Eskom Sole source supplier for white metal bearings. The contractor is required to have all bearing work done by GB Bearings (Pty) Ltd unless as alternative competent and registered supplier is available. (Subject to approval by Eskom)

Program

- A detailed program should be provided in the form of bar chart or any software that will specify the plan and progress of repairs.

- A program must be drafted after Assessment has been done and agreed on with the Client.

- The failure report indicating the root cause of the failure to accompany the program for submission.

Site service and procedures

The following technical specification and procedures are applicable to this contract and are available (ESKOM related standards) on requests, only the latest revision to be used.

| TITLE | DOCUMENT NUMBER |
| --- | --- |
| Refurbishment and repair of Power Station electric motors Work Instruction | 240-89217674 |
| New MV motor procurement Standard | 240-50237155 |
| Storage and preservation of power station electric motors Standard | 240-56360387 |
| Transport of power station electric motors Standard | 240-56361435 |
| Electric motor repair and refurbishment assessment form | 240-87739380 |
| Degree of protection provided by enclosure | IEC 60592 |
| Quality control of HV motor and process for repairs outside Eskom | PAM/233/004 |
| MV electrical PI testing | PWM/**M/E/002 |
| Procedure for conducting IR, PI and Tan delta tests | ELEC 175 007 |
| White metal designated WM 90 | SANS124 |

# Quality Management

The Contractor ISO 9001:2000 Registration certificate of compliance must be supplied with tender. If the Contractor is not registered, he will supply with his tender document his quality policy.

The successful contractor will hand over within one week of Contract placement to the Employer the following:

- Contractor’s Quality Assurance and Quality Control

The Contractor compiles, in conjunction with the Employer and the Supervisor, product verification plan. This document shows at which stages during the contract involvement is required, and what types of inspection, testing, hold, witnessing etc. Are carried out to ensure that the requirements of the specifications are met.

- Quality Control Plan

The Quality Control Plan, which should be based on the Eskom procedure, PAM/233/004, consists of the following as a minimum and is accepted by the employer and the Contractor prior to commencement of the work. The final QCP for approval will be endorsed by the Motor System Engineer for acceptance.

A covering page which includes and makes provision for the following:

- Document unique number.

- Revision number

- Page number

- Provision to incorporate all inspection report numbers.

- System worked on

- High level description of work execution

- Provision for review and approval signatures by the Contractor, the Employer Representative and the Supervisor.

- Provision for final releases signatures by the Contractor, Employer Representative

and the Supervisor.

A page which included a logical sequence of work execution, but not detailed.

- Abbreviations.

- Record numbers.

- Procedure numbers.

- Reference document numbers.

- Certificate numbers and references.

The work execution logic and sequence for the fabrication and erection addition to this hold, witness points etc. are also detailed.

A material summary list which includes:

- Material quantities and specifications.

- Material certificate numbers.

- Test reports

Where tests were performed, they are recorded and the positions of measurements are traceable to the specific area of testing against the records. Factory Acceptance Testing certificates to be submitted upon delivery of motor to site.

# Document

The following documents must be supplied to the Employer for each motor that is sent for repairs:

a.     All electrical and mechanical tests performed before and after repairs.

b.     Detailed breakdown report for each motor indicating the cause of the failure.

c.     Balancing certificate

d.     Quality control procedures in accordance with Eskom procedure (on submission of ender)

# Completion

a.     The motor should be stripped immediately when reaching the contractors site of Matimba.

b.	 Delivery of the motor should be within 10 days after instruction to commence work from Employer (Order Number)

# Safety & Environmental Management

a.     The contractor to comply with the safety standards and regulations of Matimba Power Station.

b.     The contractor complies with Environmental Policies and regulations of Matimba Power Station.

# TERMS & CONDITIONS FOR THE REFURBISHMENT OF MATIMBA P/S MOTORS

Before the repairer invites Matimba personnel to inspect the motor and agree with the assessment report, the following should be ready.

a.   All motor components to be at the repairer’s workshop.

b.  Any communication and arrangement for inspections at the Contractor’s premises to be arranged through the   Employers Representative.

c.   The motor should be fully assessed by the repairer before Matimba personnel (Motor System Engineer and Motor Contract Manager) are called out.

Invite/ notify Matimba personnel at least 2 days before inspection.

d.   Pictures of all defective components to be taken and handed over to Employers Representative.

e.   The proposed repair scope of work should be ready and shall be finalized with Matimba personnel (Motor System Engineer) on the same day of assessment/ inspection.

f.   The preliminary quotation to be ready on the day of inspection and should reflect the item numbers and price as agreed on the contract) Matimba personnel will have to agree with this).

g.  All additional items that are not included on the contract, prices should be included on the price column of the quotation and indicated as such.

h.   No quotations shall be blank.

i.    All quotation must be signed prior to been faxed (excluding quotes send via e-mail).

j.    All quotations shall be verified by Motor System Engineer.

k.   No work shall commence before approval and a go ahead from the Employer’s Representative or the personnel acting on his behalf.

## Management strategy and start up.

In the TSC3 the Contractor’s plan is his “design” for performing the service throughout the service period. Section 2 of the conditions of contract describes what the Contractor is to show in his plan both in the core clauses and some additional requirements in each of the main Options.

The extent of the Contractor’s plan will depend on whether the Contractor is required to develop a plan in accordance with the Employer’s broad outline of the service or whether the Employer has provided a plan for the Contractor to follow. Read the TSC3 Guidance Notes pages 21 and 22 for more information on the Contractor’s plan.

Use this section to describe any particulars which must be taken into account by the Contractor in developing his plan as required by clause 21.2. For example information about the order and timing or method of carrying out particular items of work.

List technical reporting and scheduling requirements which are to be incorporated into the Contractor’s plan.

The Contractor’s plan for the service

The conditions of contract (e.g. Clause 16.2) and other sections of the Service Information (e.g. safety risk management) may require that a meeting shall be held.   However the intention of all NEC contracts is that the Parties and their agents use the techniques of partnering to manage the contract by holding meetings designed to pro actively and jointly manage the administration of the contract with the objective of minimising the adverse effects of risks and surprises for both Parties.

Depending on the size and complexity of the service, it is probably beneficial for the Service Manager to hold a weekly risk register meeting (Clause 16.2). This could be used to discuss safety, compensation events, subcontracting, overall co-ordination and other matters of a general nature. Separate meetings for specialist activities such as planning and activities of a technical nature may also be warranted.

Describe here the general meetings and their purpose. Provide particulars of approximate times, days, location, and attendance requirements, stipulating that attendees shall have the necessary delegated authority to make decisions in respect of matters discussed at such meetings.

The following text could be used as a model for this section:

Management meetings

Regular meetings of a general nature may be convened and chaired by the Supply Manager as follows:

| Title and purpose | Approximate time & interval | Location | Attendance by: |
| --- | --- | --- | --- |
| Risk register and compensation events | Weekly on at |  |  |
| Overall contract progress and feedback | Monthly on at |  | Employer, Contractor and |

Meetings of a specialist nature may be convened as specified elsewhere in this Service Information or if not so specified by persons and at times and locations to suit the Parties, the nature and the progress of the service. Records of these meetings shall be submitted to the Service Manager by the person convening the meeting within five days of the meeting.

All meetings shall be recorded using minutes or a register prepared and circulated by the person who convened the meeting. Such minutes or register shall not be used for the purpose of confirming actions or instructions under the contract as these shall be done separately by the person identified in the conditions of contract to carry out such actions or instructions.

State any additional constraining requirements on Contractor’s supervision and key people that are not already stated in other sections such as for Health and Safety. This section could be used to solicit an organogramme from the Contractor showing his people and their lines of authority / communication. This would be essential if the Contractor is a Joint Venture.

Contractor’s management, supervision and key people

### Provision of bonds and guarantees

The form in which a bond or guarantee required by the conditions of contract (if any) is to be provided by the

Contractor is given in Part 1 Agreements and Contract Data, document C1.3, Sureties.

The Employer may withhold payment of amounts due to the Contractor until the bond or guarantee required in terms of this contract has been received and accepted by the person notified to the Contractor by the Service Manager to receive and accept such bond or guarantee. Such withholding of payment due to the Contractor does not affect the Employer’s right to termination stated in this contract.

Specify how documentation will be identified with an alpha numeric which indicates source, recipient, communication number etc. Provide details of any particular format or other constraints; for example that all contractual communications will be in the form of properly compiled letters or forms attached to e mails and not as a message in the e mail itself. State any particular routing requirements but note from TSC3 who issues what to whom.

Documentation control

The Z clauses make reference to invoicing procedures stated here in this Service Information. Also include a list of information which is to be shown on an invoice.

Invoicing and payment

Within one week of receiving a payment certificate from the Service Manager in terms of core clause 51.1, the Contractor provides the Employer with a tax invoice showing the amount due for payment equal to that stated in the Service Manager’s payment certificate.

The Contractor shall address the tax invoice to

and include on each invoice the following information:

- Name and address of the Contractor and the Service Manager;

- The contract number and title;

- Contractor’s VAT registration number;

- The Employer’s VAT registration number 4740101508;

- Description of service provided for each item invoiced based on the Price List;

- Total amount invoiced excluding VAT, the VAT and the invoiced amount including VAT;

- (add other as required)

Add procedures for invoice submission and payment (e. g. electronic payment instructions)

### Contract Change Management

This section is intended to deal with any additional requirements to the compensation event clauses in section 6 of the core clauses; such as the use of standard forms. Not the same thing as documentation control.

If Option C or E applies first read clause 52.2 and then state whether the Contractor is required to keep any other records. Include any other constraint which may be required in regard to format and filing of the records, and whether access for the Service Manager shall be provided in hard copy or electronically.

Could delete if Option A applies unless the Employer requires some form of control over the Contractor’s record keeping for the purpose of compensation event management.

Records of Defined Cost to be kept by the Contractor

  - Insurance provided by the Employer

First read TSC3 Core Clause 86.1 and then add anything necessary for the management of insurance related issues such as a cross reference to where procedures for making claims can be found. Also provide contact details for persons capable of being able to answer any insurance related queries the Contractor may have, as well as to whom the information required by Marine Insurance (if any) may be addressed.

Describe type and frequency of any on job training workshops, as well as any obligation for technology transfer being included as part of the service or at the end of the service period.

Training workshops and technology transfer

On some complex services (e. g. nuclear) it could be in the Parties best interests that some details of the design of Equipment are shared with the Service Manager, not necessarily for his acceptance but as an assurance that the Equipment will be able to allow the Contractor to Provide the Service efficiently and without delay. For example specialised handling Equipment for a particular maintenance operation. Clause

23.1 is always available to the Service Manager if this paragraph is not used.

Also the Employer may wish to exercise constraints or include witness and hold points during manufacture, assembly or delivery of such Equipment. Include these constraints here.

Draft in such a way that there is no doubt that the liability for such design supply and use of the Equipment remains with the Contractor.

Design and supply of Equipment

  - Things provided at the end of the service period for the Employer’s use

The Employer may wish to use some of the Equipment used by the Contractor after the end of the service period. Clause 70.2 requires that details of such requirement be stated in the Service Information. Complete here or if not applicable retain the heading and state ‘None’.

Equipment

#### Information and other things

Clause 70.2 requires that information and other things which the Contractor is to provide at the end of the

service period be stated in the Service Information.

Only use this heading if Option X19 applies to this contract.

In some cases all work may be done in terms of Task Orders in which case it may be logical to move this section closer to the start of this part 2 of the Service Information. In some cases only parts of the service may require to be handled by Task Order, for example a major repair which has become necessary during a continuous maintenance service contract.

Please read Option X19 before drafting requirements here as much of the procedure for the administration of Task Orders is already provided in X19, for example X19.2 specifies what a task Order should include

A Task Order format could be provided in an Annexure to this Service Information.

Many considerations can apply to Task Orders, such as availability of resources, arrangements for emergency work, Task Order reporting (work carried out and service results), assessment of additional Prices for service not included in the Price List etc.

Clause X19.6 requires information which should be included on a Task Order programme.

Further requirements for Task Orders include things to be provided by the Employer under a Task Order and the conditions under which the Employer or Others are to work.

Management of work done by Task Order

## Health and safety, the environment and quality assurance

In addition to the requirements of the laws governing health and safety, Eskom may have some additional requirements particular to the service and the Affected Property for this contract. The text below provides for these being attached as an Annexure to this Service Information. PLEASE ALSO READ CORE CLAUSE

27.4 TOGETHER WITH Z7 IN THE ADDITIONAL CONDITIONS OF CONTRACT TO MAKE SURE THAT WHATHEVER IS INCLUDED IN THE ANNEXURE FOLLOWS ON FROM THOSE CLAUSES.

The Divisional/Regional Safety Risk Manager or his representative having jurisdiction over the service must provide the relevant safety, health and environmental (SHE) criteria for incorporation into this Service Information. The SHE specification / scope must be signed off by the Divisional/Regional Safety Risk Manager or his representative confirming that the applicable safety criteria have been taken into account.

The Commodity Manager / Buyer must refer the tender to the Divisional/Regional Safety Risk Manager or his representative in order to evaluate against enquiry-specific safety criteria.

The Divisional Safety Risk Managers who will be responsible for the allocation of resources to assist P&SCM with the above processes are as follows:

·

·

·

·

·

Generation: Roley McIntyre Transmission: Tony Patterson Distribution: Alex Stramrood Enterprises: Jace Naidoo Corporate: Kerseri Pather

Health and safety risk management

The Contractor shall comply with the health and safety requirements contained in Annexure	to this Service Information.

Describe or cross refer to environmental constraints applicable to the Contractor’s plan and his activities on the Affected Property and how they should be managed. Include here or cross refer to an Annexure to the Service Information.

Environmental constraints and management

The Contractor shall comply with the environmental criteria and constraints stated in Annexure

Specify minimum requirements for the Contractor’s Quality Plan and Work Procedures or provide the Employer’s Quality Plan if that is to be used. Make sure witness and hold points are identified generally and describe any particular requirements for QA outside the Affected Property. Indicate how the Contractor’s QA documentation is to be submitted for acceptance and any conditions that need to be imposed relating to acceptance. State whether ISO compliance is a condition and if so which ISO standard shall apply.

Quality assurance requirements

## Procurement

There is a cross reference from the core clause 11.2(6) definition of Disallowed Cost to the Service Information regarding procurement procedures. This part of the Service Information MUST include any such procedures to be able to administer Disallowed Cost.

Specify any constraints relating to people employed to Provide the Service; for example permits for foreigners, training (other than H & S), use of labour from designated areas and industrial relations.

Minimum requirements of people employed

Specify constraints which Contractor must comply with after contract award in regard to any Broad Based Black Economic Empowerment (B-BBEE) or preferencing scheme measures.

BBBEE and preferencing scheme

If the ASGI-SA requirements are to be included in this contract specify constraints which Contractor must comply with after contract award in regard to any ASGI-SA requirements. The ASGI-SA Compliance Schedule completed in the returnable tender schedules is reproduced here. If ASGI-SA does not apply, delete this paragraph.

Accelerated Shared Growth Initiative – South Africa (ASGI-SA)

The Contractor complies with and fulfils the Contractor’s obligations in respect of the Accelerated and Shared Growth Initiative - South Africa in accordance with and as provided for in the Contractor’s ASGI-SA Compliance Schedule stated below

.

[Insert the agreed ASGI-SA Compliance Schedule here]

The Contractor shall keep accurate records and provide the Service Manager with reports on the Contractor’s actual delivery against the above stated ASGI-SA criteria.    [Elaborate on access to and format of records and frequency of submission etc.]

The Contractor’s failure to comply with his ASGI-SA obligations constitutes substantial failure on the part of the Contractor to comply with his obligations under this contract.

### Subcontracting

TSC3 does not make use of nominated subcontracting, but the Employer may list which subcontractors or suppliers the Contractor is required to enter into subcontracts with. This is usually only required where specialist services need to be obtained from a particular supplier or group of suppliers in order to comply with operational standards.

Preferred subcontractors

    - Subcontract documentation, and assessment of subcontract tenders

Specify any constraints on how the Contractor is to prepare subcontract documentation, whether use of the NEC system is compulsory or not (compulsory is recommended) and how subcontract tenders are to be issued, received, assessed (using a joint report?) and awarded.

The Employer may require that the Contractor must subcontract certain specialised work, or that the

Contractor shall not subcontract more than a specified proportion of the whole of the contract.

Limitations on subcontracting

State requirements for attendance on Subcontractors, if any

Attendance on subcontractors

### Plant and Materials

Plant and Materials are defined as items intended to be included in the Affected Property. This will refer to replacement of worn or defective parts, routine replacement as part of regular preventative maintenance and supply of spare parts. Quality is usually designed in or specified in the technical specifications. However to cover circumstances where quality may not be prescribed, this sub-paragraph could also be used to state an overarching default requirement – fitness for purpose etc.

Either specify here or provide a list of the applicable specifications and attach them as Annexure or state where they can be obtained from.

Specifications

State any constraints when dealing with defective Plant and Materials such as how repairs are carried out - can the item be fixed up or must it be replaced by a new one.

Correction of defects

Specify any constraints on how the Contractor is to order, codify, expedite, freight, import, transport to the Affected Property and any other requirements for delivery and storage before installation. The Employer may require warranties from suppliers to be in favour of the Employer and not just to the Contractor. The Employer may also need schedules of vendor data for his own use after the end of the service period.

Contractor’s procurement of Plant and Materials

Core Clause 41.1 makes reference to the Service Information stating which Plant and Materials are to be inspected and tested before delivery. Specify any requirements particularly if such tests and inspections are to be carried out by agents of the Employer overseas.

Tests and inspections before delivery

List any Plant and Materials which are to be provided by the Employer.

State arrangements for collection by Contractor or delivery by others on behalf of the Employer, off loading, inspection, storage, care custody and control, return of unused Plant and Materials, etc. Always include a statement to the effect that ‘all other Plant and Materials are to be provided by the Contractor’.

Plant & Materials provided “free issue” by the Employer

State whether cataloguing is applicable, if it is, reference the requirements for cataloguing that need to be satisfied by the Contractor (consult Procurement Instruction Number 1 of 2018 – Incorporating Cataloguing into the Procurement Environment, Unique Identifier 240-1289988974).

Cataloguing requirements by the Contractor

## Working on the Affected Property

This part of the Service Information addresses constraints, facilities, services and rules applicable to the

Contractor whilst he is doing work on the Affected Property.

### Employer’s site entry and security control, permits, and site regulations

Sites such as Koeberg Nuclear Power Station have very strict entrance requirements which tendering contractors need to allow for in their prices, and the Contractor has to comply with. State these or similar requirements here.

In addition to the above there may be other restrictions once on the site, plus rules relating to roads, walkways and the provision of barricades

Restrictions and hours of work may apply on some sites. It is very important that the Contractor keeps records of his people working on the Affected Property, including those of his Subcontractors. State that the Service Manager shall have access to them at any time. These records may be needed when assessing compensation events.

People restrictions, hours of work, conduct and records

Section 3 deals with contractual H & S requirements in addition to those of the OHSA Act.   This section allows the Employer to state what measures are to be taken on the Affected Property by describing where First Aid facilities provided by the Employer are located and any other emergency arrangements. Do not use if already addressed in 2.3.

Health and safety facilities on the Affected Property

This sub-paragraph may not be required in a service contract or if these matters are dealt with in the general environmental requirements referred to in section 3 above.

Environmental controls, fauna & flora

This sub-paragraph could be used to deal with two issues.

- The cross reference from core clause 25.1 about cooperation generally as well as details about Others with whom the Contractor may be required to share the Affected Property. See clause 11.2(9) for the definition of Others.

- Requirements for liaison with and acceptance from statutory authorities or inspection agencies.

Cooperating with and obtaining acceptance of Others

  - Records of Contractor’s Equipment

This sub-paragraph is intended to address how records are to be kept of Equipment on Site including whether it is owned or hired. Include any constraints about scaffolding, rigs, heavy lifts and cranes, including removal from the Affected Property.

Provide details of equipment (e.g. overhead cranes) made available for use by the employer and set out conditions relating thereto.

Equipment provided by the Employer

### Site services and facilities

This is a mandatory cross reference form clause 25.2 in TSC3. State what the Employer will provide in the way of power, water, waste disposal, telecomms, ablutions, fire protection and lighting (etc) on the Affected Property.   Give hook up locations and any constraints on how the hook up is to be done.   Always conclude by stating that the Contractor shall provide everything else necessary for Providing the Service.

Provided by the Employer

Describe what the Contractor is to provide in the way of accommodation, laboratories, storage, vehicles and office equipment for the Service Manager and any restrictions or minimum requirements concerning the Contractor’s own facilities. Also state what happens to these facilities upon completion of the contract.

Provided by the Contractor

State requirements, if any.

Control of noise, dust, water and waste

State any constraints

Hook ups to existing works

### Tests and inspections

Describe the tests and inspections to be carried out by the Contractor and the Service Manager and others [40.1].

Description of tests and inspections

State what materials facilities and samples for tests and inspections the Contractor and the Employer are to provide, per core clause 40.2.

Materials facilities and samples for tests and inspections

# Supporting clauses

## Purpose

The purpose of this scope is to define the refurbishment and repair requirements for Matimba Power Station MV induction motors.  It is imperative that each supplier aligns their organisation fully to the systems and requirements laid down in this document.

## Scope

The scope of this contract is applicable to all MV induction associated with Matimba Power Station.

## Applicability

This scope is applicable to Matimba Power Station.

## Normative/Informative References

Parties using this document shall apply the most recent edition of the documents listed in the following paragraphs.

### Normative

              - Occupational Health and Safety Act, 85 of 1993.

              - ISO 9001:2008: Quality management systems.

              - SANS IEC 60034-1 to 30: Rotating electrical machines.

              - SANS IEC 60085: Electrical insulation- Thermal classification.

              - ISO 10816: Vibration severity standard.

              - Eskom 240-89217674: Refurbishment and repair of power station electrical motors Work instruction.

              - Eskom 240-56361435: Transport of Power Station Electric Motors Standard.

              - Eskom 240-56360387: Storage of Power Station Electric Motors Standard.

              - Eskom 240-50237155: New MV Motors Procurement Specification.

              - Eskom 240-95138097: Standard Electric Motor Test Certificate.

### Informative

ISO 1940-1:2003: Mechanical vibration- Balance quality requirements for rotors in a constant (rigid) state- part 1: Specification and verification of balance tolerance.

## Definitions

| Definitions | Explanations |
| --- | --- |
| Contractor | Service provider contracted for supply specific service to Eskom Matimba power station. |
| Employer | Eskom or Eskom Matimba power station representative appointed in writing. |
| Induction Motor | Electric motor in which the electric current in the rotor needed to produce torque is obtained by electromagnetic induction from the magnetic field of the stator winding |
| Medium Voltage | Any AC voltage exceeding a 1000V |
| Outage | A planned or unplanned shutdown project related to one or more of the Employer’s Power Station units |

## Abbreviations

| Abbreviations | Explanation |
| --- | --- |
| AC | Alternating Current |
| DC | Direct Current |
| DE | Drive End |
| GWh | Gigawatt hour |
| IBI | Integrated Business Improvement Model |
| KPA | Key performance area |
| KPI | Key performance indicators |
| MCR | Maximum Continuous Rate |
| MM | Material Management |
| MV | Medium Voltage |
| NCR | Non-Conformance Report |
| NDE | Non- drive end |
| OEM | Original Equipment Manufacture |
| PPE | Personal protective equipment |
| QC | Quality control |
| QCP | Quality Control Plan |
| SHEQ | Safety, Health, Environment and Quality |
| SOS/SOW | Scope of service/ Scope of work |

## Process for Monitoring

## Technical KPIs

| Item | KPI | Targets |
| --- | --- | --- |
| 1 | Breakdown or emergency reaction time | Within 12 hours |
| 3 | Delivery on emergency work (Overhaul) | 3 weeks |
| 5 | Delivery on emergency work (Rewind) | 6 weeks |

# Site Visit

- Clarification meeting and site visit is compulsory for all contractors.

- Procurement officer to form part of the site visit team.

- Invited contractors to bring own PPE during site visits.

- All official communication will be in the form of writing.

- A register will be signed by all in attendance and kept as record.

- Contractor who does not attend and goes to site visit won’t be considered.

List the contact information of the end users.

# Requirements

Appropriate specifications, procedures and work instructions are used. In the absence of the manufacture’s specifications, or Eskom specifications, IEC 60034 shall be used, as appropriate for the class of the motor. Whether using Eskom specifications, national or international specifications, instructions for the testing to be done on each motor are required.

Deficiencies and modifications

No modifications shall be done on the motor without the approval of the employer.

Turnaround time

The maximum turnaround time per motor for assessment shall be three (3) working days. The repair work will depend on the scope of work, which shall be agreed beforehand between Eskom and the supplier, and the scope must indicate timelines per task. When necessary, the employer may request, by telephone or email.

Painting

At least one primer coat and two finish coats of compatible outdoor paint shall be applied in accordance with the paint manufacturer’s instructions. Two-part epoxy-type paint is required because of its toughness and durability. (Examples: DuPont’s Variprime 615S and 616S). Unless otherwise specified on the Refurbishment form and check sheet, the finish colour shall be emerald grey (G29) on external metal. Coatings: coatings shall be applied in accordance with the manufacture’s procedures. Details of coating requirements can be obtained from purchaser’s technical contact, if there are not clearly defined on the check sheet.

Record keeping

The supplier will keep originals of the test results, quality and any other documents used on the motor for the period of the contract plus three (3) years.

The Employer shall be given the copy of the tests results.

## Data pack

The motor shall be returned to site only if it is accompanied with a data pack comprising as a minimum on the following:

- Failure analysis report.

- Results of the tests specified on the scope of work.

- Warranty Certificate/ document.

## Warranty

Any refurbished motor shall have a 1-year warranty granted by the supplier to the Employer. Warranty shall commence on the day the motor is delivered on site.

## Transport

The supplier is responsible and accountable for transporting the motors from Matimba Power Station to their sites and from their sites to Matimba Power Station. All motors shall be transported as per Eskom 240-56361435: Transportation of power station electric motors standard.

## Quality

The supplier provides a complete Quality Control Plan in accordance with the requirements of ISO 9001:2008 to the Employer for approval. This plan must ensure an integrated quality service as part of the contract. All quality hold point and witness point must be done in the presence of an Eskom employee. Quality documents to be handed over to the Employer. The final motor test at the factory test bay must be done with the employer’s representative present.

## Adherence to Eskom generic policies

The supplier employees shall comply with Eskom’s policies and site regulations, including but not limited to, use of cell phones in restricted areas, adherence to Eskom’s lifesaving rules, smoking policy, zero tolerance on alcohol usage etc. These requirements will be detailed during the induction training process.

## Quality control standards

Quality control plan shall be produced, maintained and implemented per task as agreed by the employer. The QCP must be discussed with the employer for approval. This QCP shall comply with ISO 9001:2008 standards. Any amendments to the QCP shall be discussed with the employer for approval.

## Special tests and investigations

The supplier will perform special tests, investigations and recordings of all findings. The findings shall be shared with the Employer.

## Insurance

All motors insurance shall be covered by the supplier as from the time they leave Employer’s site until delivered back on the Employer’s site.

## Quotations

All quotations shall be given in South African Rands (ZAR).

## Industrial Relation

Any industrial relations issues from the supplier should be discussed with the contract manager.

## Program

A detailed program should be drafted in the form of bar chart or any software that will specify the plan and progress of repairs and be submitted to the contract manager together with the quotation. Contract manager and System Engineer must have opportunity to influence the bar chart for holding points. Employer can send any personnel to witness holding points and if it happens that the witness cannot be done, the supplier will only proceed after approval from the Employer.

## Deviations

Non-compliance from the agreement will result in NCR being issued to the supplier and when the third NCR is issued, the supplier will be referred to the supplier reconciliation committee.