| RFB No: | RFB 3182-2025 |
| --- | --- |
| Description | Request for the Appointment of a service provider to supply, install and commission diesel generators at Beta Data Centre for a period of 36 months. |
| Publication Date | 20 November 2025 |
| Compulsory Virtual Briefing Session | Compulsory Virtual Briefing Session will be held as follows: Date: 02 December 2025 Time: 11H00am Venue: Online (MS Teams). Bidders are requested to indicate in writing to the below email address of their intension to attend the briefing session, following which a link will be shared via email to allow attendance of the briefing session: Mpfareleni.Muneri@sita.co.za Intension to attend the compulsory briefing to be sent before close of business 01 December 2025 @ 16h00pm (Link will not be shared on the day of briefing) |
| Closing Date for questions / queries | 08 December 2025 at 16:00pm |
| Bid Response Submission Address | Tender Office, Pongola in Apollo 459 Tsitsa Street, Erasmuskloof, Pretoria, 0048 |
| RFB Closing Details and Time | Date: 16 January 2026 Time: 11:00am (South African Time) |
| RFB Validity Period | 200 Days from the closing date |

# Contents

1.	Introduction and background	3

1.1.	Purpose	3

1.2.	Background	3

2.	Scope of Bid	3

2.1.	Scope of Work	3

2.2.	Delivery addresses	3

3.	Requirements	4

3.1.	Solution Requirements	4

4.	Bid Evaluation Stages	6

4.1.	Mandatory Administrative responsiveness (Stage 1)	6

4.1.1.	Attendance of briefing session	6

4.1.2.	Registered Bidder	7

4.1.3.	Bid Submission Instructions	7

4.2.	Technical Returnable Documents	8

4.2.1.	Instruction and evaluation criteria	8

4.2.2.	Technical Mandatory Responsiveness (Stage 2)	8

4.3.	Special Conditions of Contract Verification (Stage 3)	12

4.3.1.	Special Conditions of Contract	12

4.3.2.	Declaration of compliance and acceptance SCC	27

Annex A: Bidder Substantiating Evidence	39

5.	Technical Mandatory Requirement Evidence	39

5.1.	Bidder Certification / Affiliation Requirements	39

5.2.	Bidder Experience and Capability Requirements	39

5.3.	CIDB Registration Requirements	40

5.4.	Key Personnel Qualification: Project Manager	40

5.5.	Installation Electrician Requirement	41

5.6.	Diesel Mechanic Technician Requirements	41

5.7.	Equipment Data Sheets	42

5.8.	Special Conditions of Contract	42

5.9.	Preference Points Preferential Goals Evidence	42

Annex B: CIDB Registration Requirement	44

Annex C: Technical Information	45

6.	Technical Information	45

6.1.	Project Drawings	45

6.2.	Project Specifications	45

6.3.	Project Data Sheets	45

Annex D: Local Content Requirements	46

7.	Local Content Requirements:	46

7.1.	The bidder must confirm compliance to the Local Content requirements.	46

7.2.	The following documents are attached to guide guidance in completing the Local Content requirements:	46

7.3.	The Bidder must complete, sign and submit the following documents at bid closure:	46

Annex E: CIDB Basic Guide General Conditions of Contract for Construction Works (GCC 2004)	47

# Introduction and background

## Purpose

The purpose of this RFB is to invite Suppliers (hereinafter referred to as “bidders”) to submit bids for the “Supply, Installation and Commissioning of Diesel Generators at SITA Beta including maintenance for a construction period of twelve (12) months and followed by twenty-four (24) months maintenance period with total contract period of 36 months.

## Background

The diesel generators upgrade to the critical equipment will make the SITA Beta flexible achieve higher level reliability and availability of the electrical power supply to the critical computer environments. The existing diesel generators have reached end of life with the current diesel engines starting to experience fluid leaks that are no longer repairable. Even though the leaks are minor, they will become critical if this generator units are continued to be used which will then increase the risk of unplanned downtime during the period of municipal power supply interruption.

# Scope of Bid

## Scope of Work

The scope of work by the bidders is to Supply, Installation and Commissioning of Diesel Generator Sets at SIAT Beta which includes:

- 3x Data Centre Continuous Diesel Generator sets of minimum net output power of 1350 kW per set at alternator terminals, after accounting for all parasitic loads (cooling fan, battery charger, jacket water heater) and alternator losses. The genset is inclusive of mounting frames, radiator with expansion tank and all auxiliaries including, exhaust system. Sound attenuation, controllers and panels, including breaker control, generator control, load control, with communication ports and cards to connect the system for full monitoring, fault alarms and control to a separate TCP/IP network via DDC and GSM.

- Diesel Engines should be Mitsubishi MGS, and the electric alternator should be Leroy Somer.

- Site Establishment, Preliminary and General works

- Factory Acceptance Testing of all three generators.

- Disconnection and removal of the existing generators.

- 3x2000 litres day tank with side glass/gauge, drip tray, electronic fuel level sensor, isolating valves and all auxiliaries.

- Provision for busbar trunking system to suit the position and configuration of the new installed generator control panel.

- Provision for cabling and terminations.

- Provision of fire clearance certificate for the completed installation.

- 24 Months Maintenance and Service.

## Delivery addresses

Table 1: Delivery Addresses

| No | Site Name | Physical Address |
| --- | --- | --- |
| 1 | SITA Beta | 222 Johannes Ramokhoase, Pretoria |

# Requirements

## Solution Requirements

This solution design, manufacture, delivery to site, craneage, off-loading and setting into position, re-assembly where required, connection, testing and commissioning, and integrated systems testing of diesel generator set as a complete system with sound attenuation, cooling, exhaust systems and 2000 litres day tank.

This will include but not be limited to the following:

(a)	Site Establishment, Preliminary and General works

(b)	3x Data Centre Continuous Diesel Generator sets of minimum net output power of 1350 kW per generator set at alternator terminals, after accounting for all parasitic loads  (cooling fan, battery charger, jacket water heater) and alternator losses inclusive of, mounting frames, radiator with expansion tank, sound attenuation, lagged stainless steel exhaust system, 2000 litres day double skinned tank and all auxiliaries for minimum requirement as detailed in the following documents. All generators for this project shall be identical.

- eSDHS-01299 SITA Generator Technical Specification

- eSDHS-01355_SITA Electrical Technical Specification

- Diesel Generator Datasheet - General Requirements

(c)	The engine cooling system radiators shall be fitted with, cooling fans, expansion tanks, drainage valves, side level gauges and electronic level sensors to determine the different levels of coolant in the system. For protection the genset to be interlocked to shut down on low-low coolant levels.

(d)	Each installation shall be capable of the lift required from the day tank to the engine fuel inlet.

(e)	The new generators shall be designed and installed as standalone units. The first installed generator to be installed shall initially be configured as a stand-alone unit to supply the site while the remaining generators are removed and the new units installed.

(f)	The 2000 litre day tank shall be double skinned coated steel equipped with side glass/level gauge, electronic level sensor, motorised valve, mechanical float valve, isolation ball valve, breathers, pipe connection and spin-on diesel filter with clear plastic water trap and permanent resin coated stainless steel screen to remove free and suspended water. Fuel piping shall be stainless steel suitably sized and SANS compliant.

(g)	Each day tank shall be equipped with a motorized valve on the inlet, controlled by the generator controller such that the value will be opened and closed to fill the day tank at levels to be programmed during commissioning.  The valves shall be 24vDC and shall have an isolation ball valve installed before the motorized valve.

(h)	The outlet piping from the day tank to the generator shall be fitted with inline water trap filter and low-low level sensor.

(i)	The Exhaust System shall have:

- Required for design, including back pressure calculation, factory testing and final installation.  System to be manufactured of suitably sized stainless-steel silencer and piping, fully lagged and weatherproof extended to above roof level including all fixing, mounting brackets and weatherproof top hat if required.

- Weatherproof flashing, sleeves and acoustic seals shall be provided where the exhaust system penetrates the wall.

- The exhaust line shall be graded away from the engine to drainage pockets or suitable drainage outlets.

- Exhaust pipes and silencers shall be cladded with 304 stainless steel.

(j)	On completion of installation the generators will temporarily be configured as a synchronised set to the existing synchronization board and cabling. Provision made for additional cabling to the existing synchronization board.

(k)	Each generator set shall have minimum net output power of 1350 kW at alternator terminals, after accounting for all parasitic loads (cooling fan, battery charger, jacket water heater) and alternator losses.

(l)	The diesel generators shall comply with ISO 8528-5 performance class G3 and can supply unattended continuous clean sinusoidal AC power to the load.

(m)	Generators shall be Data Centre Continuous (DCC) rated and documented as such, at the ambient design conditions and as installed. The generator shall provide full rated output for all loads ranging from 0.9 leading to 0.8 lagging power factor.

(m)	The supplier shall state the guaranteed time from start-up to load connection. The maximum allowable time shall not exceed 10 Seconds. The heater jacket system shall be sufficient to keep engine at a high enough temperature so that it can accept load < 10 seconds. The heater jacket system shall be equipped with the continuous operation circulating pump.

(n)	Batteries, chargers and all related power supplies required for a fully functional installation, including cabling, pipes, connectors and connection to all systems, vibration dampers.

(o)	Automatic by dual 24VDC redundant starter motors and battery systems. Each starter system shall be provided with its own dedicated batteries and battery charger system. The starting systems shall include a selector switch as flows:

- A starter system

- B starter system

- Auto

(p)	Each generator set be equipped with controllers and panels, including breaker control, generator control, load control, and alternator output circuit breaker. The electrical boards shall be IEC 61439-1 compliant. All protection related equipment including CT’s, voltage sensing, LV breakers, contactors, monitoring and controlling devices and related wiring, containment and panels, etc.

(q)	Onset fuel (including all fuel required for FAT of all three generators), oil and air filters, and all liquids and lubricants required.

(r)	Acoustic treatment (intake air, exhaust air and cooling system), Lagged Stainless Steel Silencers and Flue pipes. Acoustic performance:

- Intake -65 dBA at 1m distance from intake louver

- Discharge/ exhaust = 65 dBA at 1m distance from exhaust louver

(s)	Each generator set be equipped with controllers and panels, including breaker control, generator control, load control, and alternator output circuit breaker. The electrical boards shall be IEC 61439-1 compliant. All protection related equipment including CT’s, voltage sensing, LV breakers, contactors, monitoring and controlling devices and related wiring, containment and panels, etc.

(t)	The generator controllers shall come with modem with communication ports and cards to connect the system for full monitoring, fault alarms and control to a separate TCP/IP network via DDC and GSM. The generator controller shall have capability to synchronise with the mains supply, mains failure and remote automatic transfer switch operation capabilities.

(u)	Provision for Supply and install LV cables including terminations and earthing conductor from the generators to the generator control panel.

(v)	Provision Supply and install LV Busbar Trunking including terminations from the generators to the generator control panel. The existing busbar trunking is KH Busbar Trunking type.

(w)	Hangers, fixing material, cable ways, insulation material (heat and sound) etc. for the complete generator and associated installation within the room with provision for additional cable trays and hangers.

(x)	Disconnection and removal of the existing generators. The existing generators are 730kVA units with Siemens alternator. The bidder to offer buyback amount that will be discounted in the total bid price.

(y)	Reprogramming of the existing generator synchronization panel.

(z)	Factory Acceptance Testing of all three generator sets according to ISO 8528-5 performance class G3.

(aa)	Provision of fire clearance certificate for the completed installation.

(bb)	24 Months Maintenance and Service.

# Bid Evaluation Stages

The bid evaluation process consists of several stages, according to the nature of the bid. A bidder must qualify for each stage to be eligible to proceed to the next stage of the evaluation.

The stages are:

Table 2: Bid Evaluation Stages

| Stage | Description | Applicable for this bid YES/NO |
| --- | --- | --- |
| Stage 1 | Mandatory Administrative Responsiveness | YES |
| Stage 2 | Technical Mandatory Responsiveness | YES |
| Stage 3 | Special Conditions of Contract Verification | YES |
| Stage 4 | Costing and Preference Points Evaluation | YES |

## Mandatory Administrative responsiveness (Stage 1)

### Attendance of briefing session

- A Compulsory Virtual Briefing session will be held. The bidder has to sign the briefing session attendance register using the same information (bidder company name, bidder representative person name and contact details) as submitted in the bidder’s response document.

Note (1):	Bidder who wishes to attend the Compulsory Virtual Briefing Session needs to notify the responsible Specialist indicated in the Bid Document of attending the session. The link to the Compulsory Virtual Briefing Session will then be sent to those Bidders.

Note (2):	Non-compulsory site visit will be arranged on request.

Note (3):	Any bidder who fails to attend the compulsory briefing session will be disqualified.

### Registered Bidder

- Only responses from bidders who are registered as a Bidder on National Treasury’s Central Bidder Database (CSD) in terms of National Treasury’s Instruction Note 4A of 2016/17 will be considered for award on this RFB.

- In the case of joint ventures or consortiums the bidder must demonstrate that at least one of the parties to the bid response attended the briefing session.

- Bidders need to complete all the SBD documents which needs to be submitted as stated in the Invitation to Bid Document.

### Bid Submission Instructions

Note that a Two Envelope process will be followed and therefore bidders must submit as follows:

- Envelope 1: RFB Document and Technical / Functionality Response

# The following must be included and submitted in a in a separate envelope:

  - One (1) original file excluding pricing; and

  - One (1) hard copy excluding pricing; and

  - One (1) electronic copy on USB memory stick/ flash drive in Portable Document Format (PDF) of the RFB Document and Technical / Functionality Response.

- Envelope 2: Price Response

# The following must be included and submitted in a in a separate envelope:

  - One (1) original file excluding Technical / Functionality Response; and

  - One (1) hard copy excluding Technical / Functionality Response; and

  - One (1) electronic copy on USB memory stick/ flash drive in Portable Document Format (PDF) of pricing only.

- It is the Bidder’s responsibility to ensure that the information and contents on the electronic copies is the same as in the hard copies.

- To ensure that the electronic copies are not damaged, the bidder must submit the USB’s (memory stick/ flash drive) in a sealed padded envelope and be clearly marked.

- Bidders shall submit Bid responses in accordance with the prescribed manner of submission as specified above. Failure to comply with the above instructions on submitting a proposal will lead to disqualification.

- The RFB Responses (hard and electronic copies) must be clearly marked as follows: Bidder’s Name & Contact Details, RFB Number, RFB Description, and Closing Date.

- All Bids in this regard shall only be accepted if they have been placed in the tender box before or on the closing date and stipulated time.

- Late bids shall not be considered.

- The Bid response must be signed by an authorised employee, agent or representative of the bidder. The Bid response Bid must bear the initials of the signatory at the bottom of every page as an indication that the bidder has familiarised itself with the terms and conditions of this RFB document.

- Faxed or e-mailed bids will not be accepted.

- Bidders shall submit Bid responses in accordance with the prescribed manner of submission as specified in this document. Failure to comply with the bid submission requirements will lead to disqualification.

- Bidders are required to submit all returnable documents/information together with their Bids/proposals on or before the closing time and date of the Bids/proposals.

- All services supplied in accordance with the bidder’s proposal must be in accordance with all applicable legal requirements in terms of South African law, policies and regulations.

## Technical Returnable Documents

### Instruction and evaluation criteria

- The Bidder must comply with ALL the requirements as per the Technical Mandatory Requirements below by providing substantiating evidence in the form of documentation or information, failing which it will be regarded as “NOT COMPLY”.

- The Bidder must provide a unique reference number (e.g. binder/folio, chapter, section, page) to locate substantiating evidence in the bid response.

- The Bidder must comply with ALL the TECHNICAL MANDATORY REQUIREMENTS in order for the bid response to proceed to the next stage of the evaluation.

### Technical Mandatory Responsiveness (Stage 2)

Table 3: Technical Mandatory Requirements

| Mandatory Requirements |  | Substantiating evidence of compliance (used to evaluate bid) |  | Evidence reference (to be completed by bidder) |
| --- | --- | --- | --- | --- |
| 1. Bidder Certification/ Affiliation Requirements |  |  |  |  |
| The Bidder must be registered as an Electrical Contractor with the Department of Labour. |  | Attach to ANNEX A copy of valid letter from the Department of Labour as evidence that the bidder is registered as an Electrical Contractor. NOTE (1): SITA reserves the right to verify the information provided. |  | <provide a unique reference to locate substantiating evidence in the bid response – see Annex A, par 5.1> |
| 2. Bidder Experience and Capability Requirements |  |  |  |  |
| The bidder must have executed two (2) projects of Supply, Installation and Commissioning of Diesel Generators with minimum of single unit capacity of 1350kVA a Data Centre or equivalent High Availability Environment (Health Facility, Airport, Bank, Industrial Plant) to at least two (2) customers/projects in the past five (5) years from publication date of this Bid. |  | The Bidder must complete table 10 in Annex B by providing reference details from two (2) customers/projects to whom of Supply, Installation and Commissioning of Diesel Generators with minimum unit capacity of 1350kW a Data Centre or equivalent High Availability Environment (Health Facility, Airport, Bank, Industrial Plant) was successfully delivered in the past five (5) years from publication date of this Bid. - Company name; and - Reference Person Name, Tel and/or email; and - Project Scope of Work; and - Project Start and end date. NOTE (1): The Bidder must provide all of the following information when completing table 10 NOTE (2): Failure to comply fully with the abovementioned requirements will result in disqualification. NOTE (3): SITA reserves the right to verify the information provided. NOTE (4): Projects/installations that used multiple smaller units to achieve the minimum capacity will not be accepted. |  | <provide a unique reference to locate substantiating evidence in the bid response – see Annex A, par 5.2, table 10> |
| 3. CIDB Registration Requirement |  |  |  |  |
| The Bidder must be registered with the Construction Industry Development Board (CIDB) and have a minimum rating of 7EB or 7EP or higher. |  | The Bidder must complete and sign ANNEX B as evidence that the Bidder, is registered with the CIDB with a minimum rating or higher of 7EB, or 7EP NOTE (1): SITA reserves the right to verify the information provided. |  | <provide a unique reference to locate substantiating evidence in the bid response – see Annex A, par 5.3 and Annex B> |
| 4. Key Personnel Qualification: Project Manager |  |  |  |  |
| The Bidder must provide a qualified Project Manager with a minimum of five (5) years’ post professional registration. The professional registration be either one (1) of the following: - ECSA, Professional Engineer (Pr Eng), or - ECSA, Professional Certificated Engineer , or - ECSA, Professional Engineering Technologist, or - ECSA, Professional Engineering Technician, or - PMI, Project Management Professional (PMP), or - SACPCMP, Professional Construction Project Managers. |  | Attach to ANNEX A copy of a valid Registration Certificate indicating that the Project Manager has been registered as a professional for a minimum of five (5) years of professional post registration. The professional registration be either two (2) of the following: - ECSA, Professional Engineer (Pr Eng), or - ECSA, Professional Certificated Engineer, or - ECSA, Professional Engineering Technologist, or - ECSA, Professional Engineering Technician, or - PMI, Project Management Professional (PMP), or - SACPCMP, Professional Construction Project Managers. NOTE (1): SITA reserves the right to verify the information provided. NOTE (2): SITA reserves the right to verify the consent from the registered person. NOTE (3): The Bidder must also provide registered person contact details by completing table 11. NOTE (4): The Bidder’s registered professional shall act as the Project/Contracts Manager for the full duration of the construction phase |  | <provide unique reference to locate substantiating evidence in the bid response – see Annex A, section 5.4 par table 11> |
| 5. Installation Electrician Requirement |  |  |  |  |
| The Bidder must provide a qualified Electrician with five (5) years’ experience post trade test certificate | Attach to ANNEX A copy of valid Trade certificate indicating that the electrician is qualified with five (5) years of experience post trade test certificate. NOTE (1): SITA reserves the right to verify the information provided. NOTE (2): SITA reserves the right to confirm consent of submission from the electrician NOTE (3): The Bidder must also provide registered person contact details by completing table 12. |  | <provide unique reference to locate substantiating evidence in the bid response – see Annex A, section 5.5 par table 12 |  |
| 6. Diesel Mechanic Requirement |  |  |  |  |
| The Bidder must provide a qualified Diesel Mechanic with five (5) years’ experience post-trade test certificate. |  | Attach to ANNEX A copy of valid Trade Test Certificate indicating that the Diesel Mechanic is qualified with five (5) years of experience post-trade test certificate. NOTE (1): SITA reserves the right to verify the information provided |  | <provide unique reference to locate substantiating evidence in the bid response – see Annex A, section 5.6 par table 13 |
| 7. Equipment Data Sheets |  |  |  |  |
| The Bidder must comply with the specifications by completing and submitting signed equipment data sheets listed in Annex C. |  | Attach to Annex A completed and signed Data Sheet as per ANNEX C: NOTE (1): SITA reserves the right to verify the information provided. NOTE (2): Failure to complete the Data Sheets fully will result in disqualification. |  | <provide a unique reference to locate substantiating evidence in the bid response – see Annex A, par 5.7> |
| 8. Special Conditions of Contract |  |  |  |  |
| Bidder must accept ALL the Special Conditions of contract. |  | The Bidder must accept ALL the Special Conditions of Contract by completing and signing the declaration of Acceptance in the Declaration of Compliance and acceptance under the Special Conditions (Section 4.3.1). Note (1): Failure to accept ALL the Special Conditions of Contract will result in disqualification. |  | <provide unique reference to locate substantiating evidence in the bid response – see Annex A, section 5.8 |

## Special Conditions of Contract Verification (Stage 3)

- The successful Bidder will be bound by Government Procurement: General Conditions of Contract (GCC) as well as this Special Conditions of Contract (SCC), which will form part of the signed contract with the successful Bidder. However, SITA reserves the right to include or waive the condition in the signed contract.

- SITA reserves the right to:

  - Negotiate the conditions; or

  - Automatically disqualify a bidder for not accepting these conditions; or

  - Award to multiple bidders; or

  - Not to award; or

  - To do a partial award.

- In the event that the bidder qualifies the proposal with own conditions and does not specifically withdraw such own conditions when called upon to do so, SITA will invoke the rights reserved in accordance with subsection 4.3. (b) above.

### Special Conditions of Contract

#### Contracting Conditions

- Formal Contract - The Bidder must enter into a formal written contract (agreement) with SITA.

- Right of Award - SITA reserves the right to award the contract for required goods or services to multiple Bidders.

- Right to Audit - SITA reserves the right, before entering into a contract, to conduct or commission an external service provider to conduct a financial audit or probity to ascertain whether a qualifying bidder has the financial wherewithal or technical capability to provide the goods and services as required by this tender.

#### Delivery Address

- The Bidder must deliver the required products or services at as indicated in Section 2.2, Delivery Address

#### Delivery Schedule

  - The scope of work (Section 2.1) and Section 3 (Requirements) must be completed within 26 weeks after the contract has been awarded for decommission, supply, install and commissioning of the new equipment.

  - Construction period will be limited to a period 12 months. The 24 months maintenance and service period will commence immediately after handover and commissioning of the last generator set with total contract period of 36 months.

  - The Bidder is responsible for performing the work as outlined in the following Work Breakdown Structure (WBS):

Table 4: Work Breakdown Structure (WBS)

| WBS | Statement of Work | Delivery Timeframe |
| --- | --- | --- |
|  | (a) 3x Data Centre Continuous Diesel Generator sets of minimum net output power of 1350 kW per set at alternator terminals, after accounting for all parasitic loads (cooling fan, battery charger, jacket water heater) and alternator losses, mounting frames, radiator with expansion tank and all auxiliaries including, exhaust system. Sound attenuation, controllers and panels, including breaker control, generator control, load control, with communication ports and cards to connect the system for full monitoring, fault alarms and control to a separate TCP/IP network via DDC and GSM | 12 Months |
|  | Site Establishment, Preliminary and General works | 8 Weeks |
|  | 3x Supply, Installation and commissioning Controllers and panels, including breaker control, generator control, load control, with communication ports and cards to connect the system for full monitoring, fault alarms and control to a separate TCP/IP network via DDC and GSM. | 12 Months |
|  | Factory Acceptance Testing of all three generators according to ISO 8528-5 performance class G3 | 12 Months |
|  | Disconnection and removal of the existing generator sets. The bidder to offer buyback amount that will be discounted in the total bid price. | 12 Months |
|  | Supply, Installation and commissioning of 3x 2000 litres day tank with side glass/gauge, drip tray, electronic fuel level sensor, isolating valves and all auxiliaries. | 12 Months |
|  | - Acoustic performance: - Intake = 65 dBA at 1m distance from intake louvre - Discharge/ exhaust = 65 dBA at 1m distance from exhaust louvre | 12 Months |
|  | 24 Months Maintenance and Service |  |

#### Penalties

- A penalty of 15% of the monthly contract value or any specific deliverable may be imposed if it is found that the Service Provider failed to meet agreed deliverables, and such failure was not caused by a failure of the client to comply with its obligations.

- Where penalties are imposed, the relevant monthly invoice will be reduced by the penalty amount or a credit note for the penalty amount will be submitted to SITA within 2 (two) months of the target not being met.

SITA reserves the right to enforce these penalties, or not, depending on the merit of each case.

#### Services and Performance Metrics

  - During Warranty and Maintenance periods the Bidder is responsible to provide the following services as specified in the Service Breakdown Structure (SBS):

Table 5: Service Breakdown Structure

| SBS | Service Element | Service Level |
| --- | --- | --- |
|  | Emergency Contact during warranty and maintenance periods | 24h x 7days x 52weeks |
|  | Incident Response during warranty and maintenance periods | Maximum 60-minutes |

#### Maintenance Requirements

During Warranty and Maintenance periods the Bidder is responsible to provide the following services:

- Periodic Generator Testing, including Utility Mains Fail Testing and Monthly Inspections, including travel, labour, material, tools, and consumables and provide the specified report. SITA will give notice three business days before the intended utility mains failure simulation, with final confirmation at least one business day in advance. The services will include:

  - The Grid power failure simulations are usually performed on weekend (Saturdays or Sundays) for a period not exceeding 3 (three) hours.

  - In the absence of the mains failure generator test, the Off-load generator test must be performed monthly. This periodic generator set test run can lubricate engine components, improving starting reliability, preventing oxidation of circuit joints, and preventing fuel deterioration. This work may only be done during a SITA-approved Change window. This work may be done during normal hours. The genset can run for a minimum of 15 minutes. When running, check:

    - Whether the generator has abnormal vibrations.

    - Excessive exhaust gases.

    - Excessive noise or coolant.

    - Fuel, coolant and lubricant leakages.

    - Monitor and record the operating parameters, e.g. voltage, frequency, speed, charging voltage, etc.

  - A report detailing the status of the electrical plant during the duration of the test to be submitted, and relevant job card must be signed by SITA representative upon the completion of the test. The job card will form part of the monthly report.

- Routine generator set and plant maintenance: Technical teams will perform routine detailed inspections of all generator sets and plant maintenance. The work will include travel to the relevant site.  The work will also include materials, tools, and any other tools and equipment needed to perform the job. The services will include:

  - Check fuel, coolant and lubricant leakage, whether they are leaking.

  - Check the engine coolant heater. If the temperature is too low, the heater may not work, resulting in engine heating failure. Replace faulty components.

  - Check generator lubricants and coolants and top if necessary.

  - Check and measure battery voltage and CCA (Cold Cranking Current) values.

  - Check the resistance value of the air filter.

  - Check whether the radiator becomes less crowded and leakage.

  - Clean radiator coils.

  - Check fuel elevation and delivery system status.

  - Check the battery connections.

  - Check Battery condition status.

  - Check whether the exhaust system leaks or has excessive resistance and discharge condensate liquid.

  - Check the resistance of intake ventilation of the generating set.

  - Check engine lubricating oil quality and branch filter.

  - Clean or change the crankcase and ventilation filter.

  - Check whether the oil hose is damaged and replace it if necessary.

  - Check electrical safety control equipment and alarm.

  - Remove grease, lubrication, dust and other sediments from the generator set.

  - Check transmission line connectors, circuit breakers and switching switches.

  - Check fan blades, pulleys and water pumps.

  - Fixture bolts of related parts of the generator set.

  - Clean generator output and control box, check and tighten all line connections, and measure and record generator winding resistance.

  - Check the operation of the fuel polishing system and rectify it if required.

  - Check the operation of the automatic re-fuelling system.

  - Check and inspect the condition of the tanks and piping system for leaks and rectify if necessary.

- Engine Oil, Filters Change and Service: This work includes travelling, labour, lubricating oil, oil filters, material/spares, consumables, and tools. This task is to be completed after oil sampling tests.  The services will include and not limited to:

  - Check oil level: measure the current oil level to assess if it has been low.

  - Assess oil condition, colour, viscosity, and odour to check for signs of contamination or excessive wear.

  - Inspect the oil filter and check for clogs, leaks, or any visible issues with the oil filter.

  - Drain old oil and warm up the engine: Run the engine briefly to warm the oil, allowing for easier and more complete drainage.

  - Remove and replace the oil filter and refill the engine with new oil.

  - Check the oil level, confirm the oil level and top off if necessary.

  - Start the engine and check for leaks.

  - Run the engine briefly to circulate the new oil.

  - Inspect for leaks, check the oil filter area for any leaks ensuring the new filter is secure.

  - Recheck the oil level after the engine has been shut off and the oil has settled; check the level again to confirm accuracy.

# Note (1) The bidder responsible for the number of oil filters and amount of oil required to complete the service for each generator set.

- Fuel and Air Filters Change and Service. This work includes travelling, labour, 1x Inline Water Trap Filter, Fuel Filters, Air Filters, material/spares, consumables, and tools. The services will include and not limited to:

  - Inspect Air Filter: Check for dirt, dust, and debris buildup that can restrict airflow to the engine.

  - Remove Old Air Filter: Take out the old air filter from the air filter housing.

  - Clean Air Filter Housing: Remove any debris or dust in the filter housing to prevent contaminants from entering the engine.

  - Install New Air Filter: Place the new air filter in the housing, ensuring a proper fit, and secure it.

  - Test Airflow: Start the engine to ensure that airflow is unobstructed and the filter is seated correctly.

  - Inspect Fuel Filter: Check for signs of clogging, corrosion, or other damage that could restrict fuel flow.

  - Depressurize Fuel System: Release any pressure in the fuel system to prevent fuel spray when removing the filter.

  - Remove Old Fuel Filters: Disconnect the old fuel filter, typically found along the fuel line between the gas tank and the engine.

  - Install New Fuel Filters: Connect the new fuel filter, ensuring proper orientation to maintain fuel flow.

  - Check for Leaks: Start the engine briefly and inspect for any fuel leaks.

# Note (1) The bidder responsible for the number of fuel and air filters required to complete the service for each generator set.

- Engine Coolant Change: This work includes travelling, labour, ready-mix coolant, material/spares and tools. The coolant specification should be compatible and approved as per equipment.

- Starter Battery Replacement: This work includes travelling, labour, Starter Batteries, material/spares, consumables, and tools.

- Diesel Engine Major Service, including travel, labour, material, tools, and consumables, provides the specified report. The services will include a combination of activities as listed above and not limited to:

  - Routine generator set and plant maintenance.

  - Engine Oil and Oil Filters, Change and Service.

  - Fuel and Air Filters, Change and Service.

  - Coolant Change and Service.

  - Starter Battery Replacement.

- Engine Oil Test. This includes travelling to the relevant site, labour, and collecting samples, materials/spares, consumables, and tools. An engine oil lubricant sample is to be taken from the oil pan drain and sent to an accredited laboratory for analysis in accordance with SANS specifications. Provide a full test report on the sample, indicating but not limited to:

  - Dilution of lubricants.

  - Misapplication of lubricants.

  - Elements Analysis.

  - Contaminations.

  - Viscosity and physical properties.

  - Wear Metals.

  - Additives.

  - Water Content

- Engine Coolant Test. This includes travelling to the relevant site, labour, and collecting samples, materials/spares, consumables, and tools. A coolant sample to be taken from the radiators/expansion tank, and sent to an accredited laboratory for analysis in accordance to SANS specifications. Provide a full test report on the sample, indicating but not limited to:

  - Metal corrosion.

  - Combustion gas leaks.

  - Contamination e.g Fuel and Oil.

  - Electrical ground problems and conductivity.

  - Foaming.

  - Localized overheating.

  - Chemical breakdown.

- Diesel Fuel Test. This includes travelling to the relevant site, labour, and collecting samples, materials/spares, consumables, and tools. A coolant sample to be taken from the radiators/expansion tank, and sent to an accredited laboratory for analysis in accordance to SANS specifications (SANS 342). Provide a full test report on the sample, indicating but not limited to:

  - Flash Point

  - Viscosity

  - Particulate Matter

  - Sulphur Content

  - Water Content

  - Density

  - Checks for contamination

  - Water and Haze Rating

#### Bidder Performance Reporting

- The Bidder will report to SITA monthly during the design and manufacturing phase of the project; monthly written reports will be presented to SITA on the progress until delivery of the equipment.

- The Bidder will report to SITA/Client on a bi-weekly basis during the installation and implementation phase of the project; bi-weekly written reports will be presented to the SITA/Client on the progress of the preceding week until the installation process has been completed.

- Quarterly meetings to be scheduled between SITA/Client and service provider during warranty and maintenance periods.

- The Bidder is required to generate regular reports as outputs during the maintenance and support cycle within the following service levels (the report type will drive the service level agreement; definition of the content of each report type will be finalised at the time of concluding the contracted service level agreement).

#### Certification, Expertise and Qualification

  - The Bidder must be registered at the Department of Labour as an Electrical Contractor

  - The bidder must have executed two (2) projects of Supply, Installation and Commissioning of Diesel Generators with minimum unit capacity of 1350kVA a Data Centre or equivalent High Availability Environment (Health Facility, Airport, Bank, Industrial Plant or similar High Availability Environments to at least two (2) customers/projects in the past five (5) years.

  - The Bidder must be registered with the Construction Industry Development Board (CIDB) with a minimum rating of 7EB or 7EP.

  - The Bidder must provide a qualified Project Manager with a minimum of five (5) years’ post professional registration. The professional registration be either one (1) of the following:

    - ECSA, Professional Engineer (Pr Eng), or

    - ECSA, Professional Certificated Engineer Technician, or

    - ECSA, Professional Engineering Technologist, or

    - ECSA, Professional Engineering Technician, or

    - PMI, Project Management Professional (PMP), or

    - SACPCMP, Professional Construction Project Managers.

  - The Bidder must provide a qualified Installation electrician - Wiremans Licence with five (5) years’ experience post registration.

  - The Bidder must provide a qualified Diesel Mechanic with five (5) years’ experience post-trade test certificate.

  - The Bidder must comply with the specifications by completing and submitting signed equipment data sheets listed in Annex C.

  - The Bidder represents that,

    - it has the necessary expertise, skill, qualifications and ability to undertake the work required in terms of the Statement of Work or Service Definition and;

    - it is committed to provide the Products or Services; and

    - perform all obligations detailed herein without any interruption to the Customer.

  - The Bidder must provide the service in a good and workmanlike manner and in accordance with the practices and high professional standards used in well-managed operations performing services similar to the Services;

  - The Bidder must perform the Services in the most cost-effective manner consistent with the level of quality and performance as defined in Statement of Work or Service Definition;

  - Original Equipment Manufacturer (OEM).

    - The Bidder must ensure that work or service for the commissioning of the new equipment is performed by a person who is certified by Original Equipment Manufacturer and the certification will be included in the commissioning reports and handover documents. This will include all the work activities for the new installed switchgear assembly.

    - The bidder must be able to access to the control system for service diagnostics and possible repairs. The bidder must have the latest software as approved by OSM.

#### Logistical Conditions

  - Hours of work, 08h00 – 16h30.

  - Provision to be made for work which will be Saturday and Sunday or weekday after hours.

  - Provision for the installation and commissioning of the equipment to be made during scheduled downtime which will be from Friday midnight to Sunday midnight for at least one weekend. The Supplier to make sure all the resources, tools and equipment are available to work continuously during that period to complete all the scheduled tasks during that period. The downtime period will be limited to 48 Hours. This will be including for overtime and night shift over the allocated time

  - It must be noted that the Data Centres are live/active sites, and downtimes are limited. All site the services will have to be restored at the end of the scheduled downtime.

  - The installation and commissioning activities that does not require downtime, those can be completed during hours in 8(a) or per arrangement as per 8(b).

  - In the event that SITA grants the Bidder permission to access SITA's Environment including hardware, software, internet facilities, data, telecommunication facilities and/or network facilities remotely, the Supplier must adhere to SITA's relevant policies and procedures (which policy and procedures are available to the Supplier on request) or in the absence of such policy and procedures, in terms of, best industry practice.

  - Tools of Trade: The Supplier must bring their necessary tools of trade in order for them to perform their duties adequately.

  - On-site and Remote Support: The Supplier must give off-site and remote support, and only when off-site support is not sufficient, then on-site support will be required upon approval by SITA representative.

  - Support and Help Desk. After hours helpdesk support is required for the period of the first three months per site during weekdays including weekends and public holidays.

  - Equipment Design and Approvals. Equipment detail design drawings and specifications shall be submitted for approval before manufacturing may start. And,

      - The diesel generators shall be designed to facilitate servicing, testing, monitoring and commissioning. The design shall be so that all parts can be reached and replaced easily. It shall be possible to electrically isolate any part of the plant to permit safe servicing without affecting the remainder of the installation.

      - The base shall have all necessary structural strength to allow each generator and its components to be transported and craned into position as a single item.

      - The failure of any individual unit or its control system shall not impact the operation of any other diesel generator or their respective downstream systems.  Each generator shall have its own controller.

      - The start signal for the diesel generator shall be a fail-safe signal, whereby a break in the cable shall call the generator to start and take its load.

      - All control signals for the diesel generator controls and for the control of the associated switchboards shall be via low level interface.

  - Manufacture and Supply. Manufacture and delivery to Site is included in the SOW. The Service Provider shall be responsible for all transport risks and arranging for the necessary site access permits.

  - Factory Acceptance Testing. On completion and approval of all pre-FAT documentation, the supplier will commence with the functional testing. SITA will be notified at least 2 weeks in advance before FAT commences to allow the employer or their representative to witness these tests. Once these tests are completed, the SITA will verify the test results and request to witness specific items.

- Carry out testing according to ISO 8528-5 performance class G3 on all units. The Service Provider to make allowance for the facility and auxiliaries (load banks, power logging, cabling e.t.c) required to complete the tests.

- Provide a list of all testing that is to be carried out as part of the manufacturer’s routine testing for inspection prior to carrying out.

- Provide completed copies of the manufacturers signed or stamped certificate’s prior to shipping.

- Manufacturers routine test certificates shall be provided for inspection prior to commencement of factory testing and included as part of the submitted O&M Manuals.

- Witnessed factory testing shall be carried out at the manufacturer’s local premises preferably within local metropolitan area.

- The testing shall be led by a factory technician with clear technically capable English language skills. If necessary, a translator shall be provided to facilitate communications and technical queries from the witnessing client representatives.

- Testing shall include all nominated tests above and allow for any reasonable additional testing requests made by the witnessing engineer during the testing.

- The following specific tests shall be carried out during witnessed factory testing including all other tests that might be specified by the Commissioning Agent or Commissioning Manager and the following specific tests shall be carried out during witnessed site acceptance testing

  - Delivery of Diesel Generator: The supply, delivery and installation of all systems related to the generator installation to ensure a complete and fully functional system shall be allowed for. The shipment from the factory and delivery to site, installation and transport insurance of:

- Complete Diesel Generators.

- Battery charger and batteries

- Piping, cladding brackets etc.

  - Pre-Installation documentation: Provide the engine interfacing details for design of the installation of:

- Fuel pipe connection details

- Engine fluid cooling circuit details, pipe size, flow rates, temperature differential, pressure requirements

- Machine airflow requirements, flow, temperature differential, pressure, etc.  Confirmation that existing intake and exhaust openings are sufficient.

- Generator room layout drawings and sections indicating installation position of existing generators as well the position of the new generators.

- Machine noise data (full spectrum)

- Prepare cable schedules indicating the cable type, origin and destination of each cable required for integration of the unit.

- Prepare cable termination schedules indicating each the terminal at each end of every core in every cable

- Prepare full control system diagrams and SOO.

  - Commissioning Requirements. The Service Provider shall provide experienced test personnel as well as an experienced and competent test Engineer to undertake and supervise all the commissioning tests.  The test Engineer shall work in conjunction with the Employer’s representatives on site and shall co-operate at all times with these representatives. The preparation of the engine for first run shall include, as a minimum, the following:

- Oil drain and fill

- Fuel flush and fill

- Cooling system flush and fill

- Component, system and point to point tests to bring the diesel generator online to prove operation.

- Integrated system testing with other systems in the facility.

- Noise recording during normal working hours and between 12:00am and 01:00 am.

- Presentation of Test results.

  - Completion

- Operation and Maintenance manuals.

- Defects liability period and warranty for 12 months from project completion.

- Operational and maintenance personnel training.

  - Cold Commissioning Requirements. The tests shall include, but not be limited to the following:

    - Verification of schematic diagrams and cable & termination schedules.

    - Verification of accuracy of nameplate information and application.

    - Test reports & checklists.

    - Testing of earth continuity to substation earth bar.

    - Check list for cleaning of equipment

  - Hot Commissioning Requirements: The Service Provider shall provide experienced test personnel as well as an experienced and competent test Engineer to undertake and supervise all the commissioning tests.  The test Engineer shall work in conjunction with the Employer’s representatives on site and shall always co-operate with these representatives.

    - Check list for cleaning of equipment

    - All operational tests will be verified by the SITA representatives to ensure that the tests have been performed, and the results were acceptable.

    - Measure the current unbalance, monitor system voltages.

    - Sign-Off documentation for the tests.

#### Skills Transfer and Training

  - The Bidder must provide training on the proposed solution to technical staff and operators to enable SITA to operate and support the product or solution after implementation. The training would be informal.

  - The Bidder to submit all the necessary documentation such as COCs, commissioning sheets, record drawings (as built), operation and maintenance manuals for all the equipment.

#### Regulatory, Quality and Standards

- The Bidder must for the duration of the contract ensure compliance with ISO/IEC General Quality Standards, and Protection of Personal Information Act (POPIA).

- The Bidder must for the duration of the contract ensure compliance with General Quality Standards, ISO 9001.

- The Bidder must for the duration of the contract ensure compliance with the project specification and listed standards:

  - eSDHS-01299 SITA Generator Technical Specification

  - eSDHS-01355_SITA Electrical Technical Specification

#### Company and Personnel Security Requirements

  - Company security screening: The supplier may be required to undergo a company security screening conducted by the State Security Agency (SSA). Should the SSA find the supplier not suitable after the conduct of the security screening, the business relationship will be terminated. The following documentation will be required for the company security screening process to be conducted:

    - Copy of company registration documentation;

    - Copy(ies) of identity documentation of Director(s), Member(s) or Trustee(s);

    - Copy of valid tax clearance certificate.

  - Security suitability check for individuals: SITA may, at its own discretion and in line with its policies and procedures, require employees of the supplier to be subjected to a security suitability check before commencement of a project or delivering of a service. The security suitability check is conducted by SITA in order to ensure that individuals meet the minimum security requirements and also to verify personal information. The supplier will be required to replace any employee(s) who is found to be not suitable after the conduct of the security screening. The following documentation will be required for the security suitability check:

    - Copy of identity document;

    - Copy(ies) of qualification(s) if SITA requires verification thereof;

    - Fingerprints – will be taken electronically;

    - Signed consent form for the conduct of background checks.

  - Security clearance: A security clearance, issued by either the SSA or Defence Intelligence (DI) is required if any employee of the supplier will have or may gain access to classified information throughout the duration of the project or in the process of delivering a service. The level of security clearance required – Confidential, Secret or Top Secret, will be determined at the sole discretion of SITA. The supplier will have to replace any employee who do not qualify for a security clearance or is found not suitable by the SSA or DI. The following documentation will be required for the security clearance process:

    - Completed Z204 or DD1057 security clearance application form;

    - Fingerprints;

    - Personal documentation of the applicant, including but not limited to, identity document, passport, marriage certificate (if applicable), divorce order (if applicable), qualifications, salary advice and bank statements.

#### Confidentiality and non -disclosure conditions

- The Bidder, including its management and staff, must before commencement of the Contract, sign a non-disclosure agreement regarding Confidential Information

- Confidential Information means any information or data, irrespective of the form or medium in which it may be stored, which is not in the public domain and which becomes available or accessible to a Party as a consequence of this Contract, including information or data which is prohibited from disclosure by virtue of:

  - the Promotion of Access to Information Act, 2000 (Act no. 2 of 2000);

  - being clearly marked "Confidential" and which is provided by one Party to another Party in terms of this Contract;

  - being information or data, which one Party provides to another Party or to which a Party has access because of Services provided in terms of this Contract and in which a Party would have a reasonable expectation of confidentiality;

  - being information provided by one Party to another Party in the course of contractual or other negotiations, which could reasonably be expected to prejudice the right of the non-disclosing Party;

  - being information, the disclosure of which could reasonably be expected to endanger a life or physical security of a person;

  - being technical, scientific, commercial, financial and market-related information, know-how and trade secrets of a Party;

  - being financial, commercial, scientific or technical information, other than trade secrets, of a Party, the disclosure of which would be likely to cause harm to the commercial or financial interests of a non-disclosing Party; and

  - being information supplied by a Party in confidence, the disclosure of which could reasonably be expected either to put the Party at a disadvantage in contractual or other negotiations or to prejudice the Party in commercial competition; or

  - information the disclosure of which would be likely to prejudice or impair the safety and security of a building, structure or system, including, but not limited to, a computer or communication system; a means of transport; or any other property; or a person; methods, systems, plans or procedures for the protection of an individual in accordance with a witness protection scheme; the safety of the public or any part of the public; or the security of property; information the disclosure of which could reasonably be expected to cause prejudice to the defence of the Republic; security of the Republic; or international relations of the Republic; or plans, designs, drawings, functional and technical requirements and specifications of a Party, but must not include information which has been made automatically available, in terms of the Promotion of Access to Information Act, 2000; and information which a Party has a statutory or common law duty to disclose or in respect of which there is no reasonable expectation of privacy or confidentiality;

- Notwithstanding the provisions of this Contract, no Party is entitled to disclose Confidential Information, except where required to do so in terms of a law, without the prior written consent of any other Party having an interest in the disclosure;

- Where a Party discloses Confidential Information which materially damages or could materially damage another Party, the disclosing Party must submit all facts related to the disclosure in writing to the other Party, who must submit information related to such actual or potential material damage to be resolved as a dispute;

- Parties may not, except to the extent that a Party is legally required to make a public statement, make any public statement or issue a press release which could affect another Party, without first submitting a written copy of the proposed public statement or press release to the other Party and obtaining the other Party's prior written approval for such public statement or press release, which consent must not unreasonably be withheld.

#### Guarantee and Warranties

The Bidder warrants that:

- as at Commencement Date, it has the rights, title and interest in and to the Product or Services to deliver such Product or Services in terms of the Contract and that such rights are free from any encumbrances whatsoever;

- the Product is in good working order, free from Defects in material and workmanship, and substantially conforms to the Specifications, for the duration of the Warranty period;

- during the Warranty period and Extended Warranty periods any defective item or part component of the Product be repaired or replaced within 3 (three) days after receiving a written notice from SITA;

- the Products is maintained during its Warranty Period and Extended Warranty periods at no additional expense to SITA;

- the Product possesses all material functions and features required for SITA’s Operational Requirements;

- the Product remains connected or Service is continued during the term of the Contract;

- all third-party warranties that the Bidder receives in connection with the Products including the corresponding software and the benefits of all such warranties are ceded to SITA without reducing or limiting the Bidder’s obligations under the Contract;

- no actions, suits, or proceedings, pending or threatened against it or any of its third-party Bidders or sub-contractors that have a material adverse effect on the Bidder’s ability to fulfil its obligations under the Contract exist;

- SITA is notified immediately if it becomes aware of any action, suit, or proceeding, pending or threatened to have a material adverse effect on the Bidder’s ability to fulfil the obligations under the Contract;

- any Product sold to SITA after the Commencement Date of the Contract remains free from any lien, pledge, encumbrance or security interest;

- SITA’s use of the Product and Manuals supplied in connection with the Contract does not infringe any Intellectual Property Rights of any third party;

- the information disclosed to SITA does not contain any trade secrets of any third party, unless disclosure is permitted by such third party;

- it is financially capable of fulfilling all requirements of the Contract and that the Bidder is a validly organized entity that has the authority to enter into the Contract;

- it is not prohibited by any loan, contract, financing arrangement, trade covenant, or similar restriction from entering into the Contract;

- the prices, charges and fees to SITA as contained in the Contract are at least as favourable as those offered by the Bidder to any of its other customers that are of the same or similar standing and situation as SITA; and any misrepresentation by the Bidder amounts to a breach of Contract

#### Intellectual Property Rights

  - SITA retains all Intellectual Property Rights in and to SITA's Intellectual Property. As of the Effective Date, the Bidder is granted a non-exclusive license, for the continued duration of this Contract, to perform any lawful act including the right to use, copy, maintain, modify, enhance and create derivative works of SITA's Intellectual Property for the sole purpose of providing the Products or Services to SITA pursuant to this Contract; provided that the Bidder must not be permitted to use SITA's Intellectual Property for the benefit of any entities other than SITA without the written consent of SITA, which consent may be withheld in SITA's sole and absolute discretion. Except as otherwise requested or approved by SITA, which approval is in SITA's sole and absolute discretion, the Bidder must cease all use of SITA's Intellectual Property, at of the earliest of:

    - termination or expiration date of this Contract;

    - the date of completion of the Services; and

  - the date of rendering of the last of the Deliverables.

  - If so required by SITA, the Bidder must certify in writing to SITA that it has either returned all SITA Intellectual Property to SITA or destroyed or deleted all other SITA Intellectual Property in its possession or under its control.

  - SITA, at all times, owns all Intellectual Property Rights in and to all Bespoke Intellectual Property.

  - Save for the license granted in terms of this Contract, the Bidder retains all Intellectual Property Rights in and to the Bidder’s pre-existing Intellectual Property that is used or supplied in connection with the Products or Services.

  - Provide SITA with the compliant safety file.

#### General

- The parties in this Agreement agree that the offer price of all the equipment shall be at the wholesale price or below wholesale price as agreed with the OEM. Should, at any time during the existence of the agreement that the offered price which is higher than the wholesale price or as agreed with the OEM, SITA client shall be entitled to such wholesale price with the exclusion of the mark-up which the reseller may have charged”.

NOTE: These conditions will form part of the contract obligations and Bidders are expected to comply in order for SITA to conclude an agreement with the potential Bidders. Failure to comply during finalisation of a contract may result to disqualification.

#### Counter Conditions

- Bidders’ attention is drawn to the fact that amendments to any of the Bid Conditions or setting of counter conditions by bidders may result in the invalidation of such bids.

#### Fronting

- The SITA supports the spirit of Broad Based Black Economic Empowerment and recognizes that real empowerment can only be achieved through individuals and businesses conducting themselves in accordance with the Constitution and in an honest, fair, equitable, transparent and legally compliant manner. Against this background the SITA will not condone any form of fronting.

- The SITA, in ensuring that bidders conduct themselves in an honest manner will, as part of the bid evaluation processes, conduct or initiate the necessary enquiries/investigations to determine the accuracy of the representation made in bid documents. Should any of the fronting indicators as contained in the Guidelines on Complex Structures and Transactions and Fronting, issued by the Department of Trade and Industry, be established during such enquiry/investigation, the onus will be on the bidder / contractor to prove that fronting does not exist. Failure to do so within a period of 14 days from date of notification may invalidate the bid / contract and may also result in the restriction of the bidder/contractor to conduct business with the public sector for a period not exceeding ten (10) years, in addition to any other remedies SITA may have against the bidder/contractor concerned.

#### Business Continuity and Disaster Recovery Plans

- The bidder confirms that they have written business continuity and disaster recovery plans that define the roles, responsibilities and procedures necessary to ensure that the required services under this bid specification is in place and will be maintained continuously in the event of a disruption to the bidder’s operations, regardless of the cause of the disruption.

#### Bidder Due Diligence

- SITA reserves the right to conduct Bidder due diligence prior to final award or at any time during the Contract period and this may include pre-announced / non-announced site visits. During the due diligence process the information submitted by the bidder will be verified and any misrepresentation thereof may disqualify the bid or Contract in whole or parts thereof.

#### Preference Goal Requirements conditions

- The Bidder’s commitment for the Preference Goal Requirements in this tender will be legally binding and the Bidder needs to perform against their commitment for the duration of the contract which will form part of the Contractual Agreement.

- The Bidder must sustain, or improve the company’s BBBEE Level for the duration of the contact which will form part of the Contractual Agreement.

- Performance of Preference Goal Requirements will be determined annually. Bidders must submit their Preference status report indicating progress against the Bidder’s Preferential commitments within 30 days of the yearly anniversary of the contract.

- Bidders need to keep auditable substantive records / evidence and upon request by SITA/Department must be made available for audit and, or due diligence purposes.

- SITA reserves the right to require from a Bidder, either before a bid is adjudicated or at any time subsequently, to substantiate any claim with regards to preferences, in any manner required by SITA.

- SITA reserves the right to verify information / evidence provided by the Bidder.

- SITA/Department reserves the right to introduce a penalty of 1% of the overall annual year spent by SITA/Department for the prior year if the Bidder fails to comply to paragraphs (a), (b) and (c) above.

### Declaration of compliance and acceptance SCC

I (we), the bidder hereby declare that I (we) accept ALL the Special Conditions of Contract as specified in par 4.3.1 above and shall comply with all stated obligations:

Name of Bidder: _____________________________	Signature: _________________________

Date: ______________

  - Costing and Preference Points Evaluation (Stage 4)

    - 4.4.1 Costing and Preference Evaluation

- In terms of the SITA Preferential Procurement Policy (PPP), the following preference point system is applicable for this Bid:

  - the 80/20 system (80 Price, 20 Specific Goals) for requirements with a Rand value of up to R50 000 000 (all applicable taxes included); or

  - the 90/10 system (90 Price and 10 Specific Goals) for requirements with a Rand value above R50 000 000 (all applicable taxes included).

- The Bidder must complete either the 80/20 or 90/10 preference point system based on the offer submitted by the Bidder and submit proof of documentation required in terms of this tender.

- SITA reserve the right to apply either the 80/20, or 90/10 preference point system based on the following conditions:

  - If the lowest acceptable bid price is up to and including R50 000 000 (all applicable taxes included) then the 80/20 preferential point system will apply to all acceptable bids; or

  - If the lowest acceptable bid price is above R50 000 000 (all applicable taxes included) then the 90/10 preferential point system will apply to all acceptable bids;

- Points will be allocated for each of the Preferential Goal Requirements for this tender as indicated in table 6.

- Points for this tender shall be awarded for:

  - Price; and

  - Preference points for specific goals.

Table 6: Points allocation

| Description | Points | Points |
| --- | --- | --- |
| Price | 80 | 90 |
| Preference points for specific goals | 20 | 10 |
| Total points for Price and preference points for specific goals | 100 | 100 |

    - 4.4.2 Costing and Pricing Conditions

- South African Pricing

# The total price must be VAT inclusive and be quoted in South African Rand (ZAR).

- Total Price

  - All quoted prices are the total price for the entire scope of required services and deliverables to be provided by the bidder.

  - All additional costs as well as cost of delivery, labour, S&T, overtime, etc. must be included in this bid.

  - All services, accessories, upgrades and options required by the solution or specified by the client must be included in the quoted price. If not included, Bidders will be required to supply these accessories at no cost to the client.

  - The total bid price is based on estimated quantities; however, payments shall be made based on actual measured quantities supplied, used, or installed on site.

  - Any additional items not included in the original schedule of quantities shall be subject to prior written approval and rate agreement before execution. Payment shall be based on approved rates and measured quantities.

  - The bidder must indicate a proposed buyback amount for the existing generators. The final buyback value will be negotiated and confirmed during contracting and will be applied as a discount to the total contract price.

  - All maintenance service costs are inclusive of traveling, labour, material and tools. The Rate must include the specified service pack, and to perform the specified services.

  - All the maintenance services will be on work order basis and actual quantities might change.

  - The indicative corrective maintenance unit rates will be used for payments of corrective/remedial maintenance.

  - Percentage mark-up on materials and outsourced services to be purchased for corrective/remedial maintenance during 24(twenty-four) months maintenance period may not exceed 15%.

  - SITA reserves the right to negotiate pricing with the successful bidder prior to the award as well as envisaged quantities

- These conditions will form part of the Contract between SITA and the bidder. However, SITA reserves the right to include or waive the condition in the Contract.

- The bidder must complete the declaration of acceptance as per par 4.5 below by marking with an “X” either “ACCEPT ALL”, or “DO NOT ACCEPT ALL”, failing which the declaration will be regarded as “DO NOT ACCEPT ALL” and the bid will be disqualified.

    - 4.4.3 Bid Pricing Schedule

  - Bidders must complete the bid pricing schedule in the Excel spreadsheet format provided and upload this as part of their submission. The Excel spreadsheet consist of (3) three Sheets:

    - Sheet 1: NEW EQUIPMENT (EXCL VAT)

    - Sheet 2: MAINTENANCE (EXCL VAT)

    - Sheet 3: TOTALS BID PRICING.

Note:

Bidders must complete and submit bid pricing in the provided Excel spreadsheet format, and any pricing schedule submitted in a different format will not be considered.

  - Declaration of Acceptance

|  | ACCEPT ALL | DO NOT ACCEPT ALL |
| --- | --- | --- |
| - The bidder declares to ACCEPT ALL the Costing and Pricing conditions as specified in par 4.4.2 above by indicating with an “X” in the “ACCEPT ALL” column, or - The bidder declares to NOT ACCEPT ALL the Costing and Pricing Conditions as specified in par 4.4.2 above by - - Indicating with an “X” in the “DO NOT ACCEPT ALL” column, and; - Provide reason and proposal for each of the condition not accepted. |  |  |
| Comments by bidder: Provide the condition reference, the reasons for not accepting the condition. |  |  |

  - Preference Requirements

- The bidder must complete in full all the PREFERENCE requirements.

- Allocation of points per requirements: The points allocation of bidders’ responses to the requirements will be determined by the completeness, relevance and accuracy of substantiating evidence.

- Points will be allocated for each PREFERENCE requirement as per the criteria set in table 9A or table 9B  based on the offer submitted by the Bidder.

- The bidder must provide a unique reference number (e.g. binder/folio, chapter, section, page) to locate substantiating evidence in the bid response. During evaluation, SITA reserves the right to treat substantiation evidence that cannot be located in the bid response, as “NOT COMPLY”. The evidence needs to be attached to Annex A.

- Preference Goal Requirements

  - The Bidder must complete either the 90/10 or 80/20 preference point system based on the offer submitted by the Bidder and submit proof or documentation required in terms of this tender.

  - The specific Preferential Goal Requirements for this tender is indicated in table 7 or table 8 below.

  - The Bidder must indicate their commitment to claim points for each of the preference points by signing at par 4.5 in the Invitation to Bid document.

  - The Bidder must indicate how they claim points for each of the preference points.

  - Failure on the part of a bidder to submit proof or documentation required in terms of this tender to claim preference points for the Preference Goal Requirements for this tender, will be interpreted to mean that preference points are not claimed.

  - The Bidder’s commitment for the Preference Goal Requirements in this tender will be legally binding and the Bidder needs to perform against their commitment for the duration of the contract which will form part of the Contractual Agreement.

  - The Bidder must sustain, or improve the company’s BBBEE Level for the duration of the contact which will form part of the Contractual Agreement.

  - Performance of Preference Goal Requirements will be determined annually. Bidders must submit their Preference status report indicating progress against the Bidder’s Preferential commitments within 30 days of the yearly anniversary of the contract.

  - Bidders need to keep auditable substantive records / evidence and upon request by SITA must be made available for audit and, or due diligence purposes.

  - SITA reserves the right to require from a Bidder, either before a bid is adjudicated or at any time subsequently, to substantiate any claim with regards to preferences, in any manner required by SITA.

  - SITA reserves the right to verify information / evidence provided by the Bidder.

  - SITA reserves the right to introduce a penalty of 1% of the overall annual year spent by SITA for the prior year if the Bidder fails to comply to paragraphs (g), (h) and (i) above.

Table 7: Preference Goal Requirements for (80/20) system (Specific Goals)

| Preference Goal Requirement # | Preferential Goal Requirements | Preferential Goal Requirements for (80/20) system |  |  |
| --- | --- | --- | --- | --- |
|  | Preferential Goal Requirements allocated for this tender | Number of points allocated (80/20) system (To be completed by the organ of state) | Substantiating evidence and evidence reference to be completed by bidder. Evaluation per requirement: Each requirement indicated in the table below must be completed and points will be allocated based on the evidence required below for the (80/20) system | Evidence reference for the (80/20) system |
|  | B-BBEE Requirements |  |  |  |
| 1) | B-BBEE Requirements: Promotion of Transformational Objectives. | 10,0 | Evidence: The Bidder must provide a copy of the following relevant evidence for the Preferential Goal points which the Bidder qualifies for: - Columns A, B, C and D in table 9A # Copy of relevant proof of the following to confirm the B-BBEE status of the contributor as defined in the Broad-Based Black Economic Empowerment Act: - B-BBEE certificate (from a SANAS Accredited Agency/thedtic); # or # Sworn affidavit in the format provided by CIPC - Applicable to EMEs and QSEs only; - Column D in table 9A # Copy of South African Identification Document (ID); and/ or - Column E in table 9A # Copy of Medical Certificate clearly indicating the disability in line with the B-BBEE status claimed as defined in the Broad-Based Black Economic Empowerment Act. Note: The CIPC (Companies and Intellectual Property Commission) registration documents will also be used as evidence to confirm compliance to the Preferential procurement requirements as part of the evaluation process. Points allocation: Points will be allocated for bidders that meets the requirements as indicated in table 9A in section 4.6. | <provide unique reference to locate (80/20) system substantiating evidence in the bid response – Annex A, section 5.9> |
|  | Specific Goals: | 10,0 |  |  |
| 2) | The promotion of Local Products in line with the PPP. In line with the promotion of Local Products SITA will allocate Preference Points to Bidders whose products contain Local Content and production for Electrical and Telecom cables. | 10,0 | Evidence: Bidder must complete, sign and submit the Local Content Requirements as indicated in Annex D. Points allocation: 0 points = Zero % Local Content; 10 points = 90 % or greater Local Content. | <provide unique reference to locate (80/20) system substantiating evidence in the bid response – Annex A, section 5.9> |
|  | Total Point Allocation: | 20,0 |  |  |

Table 8: Preference Goal Requirements for (90/10) system (Specific Goals)

| Preference Goal Requirement # | Preferential Goal Requirements | Preferential Goal Requirements for (90/10) system |  |  |
| --- | --- | --- | --- | --- |
|  | Preferential Goal Requirements allocated for this tender | Number of points allocated (90/10) system (To be completed by the organ of state) | Substantiating evidence and evidence reference to be completed by bidder. Evaluation per requirement: Each requirement indicated in the table below must be completed and points will be allocated based on the evidence required below for the (90/10) system | Evidence reference for the (80/20) system |
|  | B-BBEE Requirements |  |  |  |
| 1) | B-BBEE Requirements: Promotion of Transformational Objectives. | 5,0 | Evidence: The Bidder must provide a copy of the following relevant evidence for the Preferential Goal points which the Bidder qualifies for: - Columns A, B, C and D in table 9B # Copy of relevant proof of the following to confirm the B-BBEE status of the contributor as defined in the Broad-Based Black Economic Empowerment Act: - B-BBEE certificate (from a SANAS Accredited Agency/thedtic); # or # Sworn affidavit in the format provided by CIPC - Applicable to EMEs and QSEs only; - Column D in table 9B # Copy of South African Identification Document (ID); and/ or - Column E in table 9B # Copy of Medical Certificate clearly indicating the disability in line with the B-BBEE status claimed as defined in the Broad-Based Black Economic Empowerment Act. Note: The CIPC (Companies and Intellectual Property Commission) registration documents will also be used as evidence to confirm compliance to the Preferential procurement requirements as part of the evaluation process. Points allocation: Points will be allocated for bidders that meets the requirements as indicated in table 9B in section 4.6. | <provide unique reference to locate (90/10) system substantiating evidence in the bid response – Annex A, section 5.9> |
|  | Specific Goals: | 5,0 |  |  |
| 2) | The promotion of Local Products in line with the PPP. In line with the promotion of Local Products SITA will allocate Preference Points to Bidders whose products contain Local Content and production for Electrical and Telecom cables. | 5,0 | Evidence: Bidder must complete, sign and submit the Local Content Requirements as indicated in Annex D. Points allocation: 0 points = Zero % Local Content; 10 points = 90 % or greater Local Content. | <provide unique reference to locate (90/10) system substantiating evidence in the bid response – Annex A, section 5.9> |
|  | Total Point Allocation: | 10,0 |  |  |

Table 9A: B-BBEE Points as part of the Preference Goal requirements (Preferential Goal Requirements for (80/20) system)

Note: Bidder to select the section for points they wish to claim (Mark as Y=Yes) in the table below.

|  |  |  |  | Ownership of at least 51% of People who are: |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Reference # | Contributor Level as defined in the Broad-Based Black Economic Empowerment Act | Local Entity | EME/QSEs | Woman Owned | Youth Owned | Owned by People living with disabilities | Score | Bidder to select the section for points they wish to claim (Mark as Y= Yes) |
|  | (A) | (B) | (C) | (D) | (E) | (F) | (G) |  |
| 1 | Level 1 | 0 | 2 | 4 | 3 | 1 | 10 |  |
| 2 | Level 1 | 0 | 2 | 4 | 3 | 0 | 9 |  |
| 3 | Level 1 | 0 | 2 | 4 | 0 | 0 | 6 |  |
| 4 | Level 2 and 3 | 0 | 1 | 2 | 1 | 1 | 5 |  |
| 5 | Level 2 and 3 | 0 | 1 | 2 | 1 | 0 | 4 |  |
| 6 | Level 2 and 3 | 0 | 1 | 2 | 0 | 0 | 3 |  |
| 7 | Level 4 and 5 | 0 | 0.,5 | 1 | 0,5 | 0,5 | 2,5 |  |
| 8 | Level 4 and 5 | 0 | 0,5 | 1 | 0.5 | 0 | 2 |  |
| 9 | Level 4 and 5 | 0 | 0,5 | 1 | 0 | 0 | 1.5 |  |
| 10 | Level 6 | 0 | 0 | 0 | 0 | 0 | 0 |  |
| 11 | Level 7 | 0 | 0 | 0 | 0 | 0 | 0 |  |
| 12 | Level 8 | 0 | 0 | 0 | 0 | 0 | 0 |  |
| 13 | Non-Contributor | 0 | 0 | 0 | 0 | 0 | 0 |  |
| Total Maximum Score Allocation: |  |  | 10 |  |  |  |  |  |
| G= A+B+C+D+E+F |  |  |  |  |  |  |  |  |

Table 9B: B-BBEE Points as part of the Preference Goal requirements (Preferential Goal Requirements for (90/10) system)

Note: Bidder to select the section for points they wish to claim (Mark as Y=Yes) in the table below.

|  |  |  |  | Ownership |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Reference # | Contributor Level as defined in the Broad-Based Black Economic Empowerment Act | EME/QSEs | Black Owned | Black Woman Owned | Youth Owned | Owned by People living with disabilities | Score | Bidder to select the section for points they wish to claim |
|  |  |  |  | (BO) | (BWO) |  |  |  | (Mark as Y= Yes) |
|  |  |  |  | (51% or more) | (More than 30%) |  |  |  |  |
|  |  |  | (A) | (B) | (C) | (D) | (E) | (F) |  |
|  | 1 | Level 1 | 0,75 | 1,5 | 1,25 | 1 | 0,5 | 5 |  |
|  | 2 | Level 1 | 0,75 | 1,5 | 1,25 | 1 | 0 | 4,5 |  |
|  | 3 | Level 1 | 0,75 | 1,5 | 1,25 | 0 | 0 | 3,5 |  |
|  | 4 | Level 1 | 0,75 | 1,5 | 0 | 0 | 0 | 2,25 |  |
|  | 5 | Level 2 and 3 | 0,5 | 1 | 0,5 | 0,25 | 0,25 | 2.5 |  |
|  | 6 | Level 2 and 3 | 0,5 | 1 | 0,5 | 0,25 | 0 | 2,25 |  |
|  | 7 | Level 2 and 3 | 0,5 | 1 | 0,5 | 0 | 0 | 2 |  |
|  | 8 | Level 2 and 3 | 0,5 | 1 | 0 | 0 | 0 | 1,5 |  |
|  | 9 | Level 4 and 5 | 0,25 | 0,5 | 0,25 | 0,125 | 0,125 | 1,25 |  |
|  | 10 | Level 4 and 5 | 0,25 | 0,5 | 0,25 | 0,125 | 0 | 1.125 |  |
|  | 11 | Level 4 and 5 | 0,25 | 0,5 | 0,25 | 0 | 0 | 1 |  |
|  | 12 | Level 4 and 5 | 0,25 | 0,5 | 0 | 0 | 0 | 0.75 |  |
|  | 13 | Level 6 | 0 |  | 0 | 0 | 0 | 0 |  |
|  | 14 | Level 7 | 0 |  | 0 | 0 | 0 | 0 |  |
|  | 15 | Level 8 | 0 |  | 0 | 0 | 0 | 0 |  |
|  | 16 | Non-Contributor | 0 |  | 0 | 0 | 0 | 0 |  |
|  | Total Maximum Score Allocation: |  | 5 |  |  |  |  |  |  |

|  | F= A+B+C+D+E |  |  |
| --- | --- | --- | --- |

Bidder Substantiating Evidence

# Technical Mandatory Requirement Evidence

## Bidder Certification / Affiliation Requirements

Attach a copy of valid letter from the Department of Labour as evidence that the bidder is registered as an Electrical Contractor here.

NOTE (1):

SITA reserves the right to verify information provided.

## Bidder Experience and Capability Requirements

Complete table below, noting that:

The Bidder must complete table 10 by providing reference details from two (2) customers/projects to whom of Supply, Installation and Commissioning of Diesel Generators with minimum unit capacity of 1350kW a Data Centre or equivalent High Availability Environment (Health Facility, Airport, Bank, Industrial Plant) was successfully delivered  in the past five (5) years from publication of this Bid.

Scope of work must be related

NOTE (1):

The Bidder must provide all of the following information when completing table 10:

  - Company name; and

  - Reference Person Name, Tel and/or email; and

  - Project Scope of Work; and

  - Project Start and End-date.

Project end-date must be current or not older than Five (5) years from date this bid is advertised.

NOTE (2):

Failure to comply fully with the abovementioned requirements will result in disqualification.

NOTE (3):

SITA reserves the right to verify the information provided.

Table 10: References

| # No | # Company Name | # Contact person, telephone and/or e-mail address | # Project Scope of Work | # Project start and end date |
| --- | --- | --- | --- | --- |
| # 1 | # <Company name> | # <Person Name> # <Tel> # or # <email> | < Provide scope details was executed> | # Start Date: # End Date: |
| # 2 | # <Company name> | # <Person Name> # <Tel> # or # <email> | < Provide scope details was executed> | # Start Date: # End Date: |

## CIDB Registration Requirements

The Bidder must complete and sign ANNEX B as evidence that the Bidder is registered with the CIDB with a minimum rating or higher of 7EB or 7EP and attach it here.

## Key Personnel Qualification: Project Manager

Attach to ANNEX A copy of a valid Registration Certificate indicating that the Project Manager has been registered as professional for a minimum five (5) years post professional registration.

The professional registration be either two (2) of the following:

- ECSA, Professional Engineer (Pr Eng), or

- ECSA, Professional Certificated Engineer Technician, or

- ECSA, Professional Engineering Technologist, or

- ECSA, Professional Engineering Technician, or

- PMI, Project Management Professional (PMP), or

- SACPCMP, Professional Construction Project Managers.

NOTE (1):

SITA reserves the right to verify the information provided.

NOTE (2):

SITA reserves the right to verify the consent from the registered person.

NOTE (3):

The Bidder must also provide registered person contact details by completing table 11.

- Attach a copy of the Professional registration certificate here and contact details of the professional registered person:

Table 11: Registered Person Contact Details

| No | Contact person, telephone and/or e-mail address |
| --- | --- |
| 1 | <Person Name> <Tel> or <email> |

## Installation Electrician Requirement

Attach to ANNEX A copy of valid Trade and Wiremans certification indicating that the Installation electrician is qualified with five (5) years of experience post registration.

NOTE (1):

SITA reserves the right to verify the information provided.

NOTE (2):

SITA reserves the right to confirm consent of submission from the electrician person

NOTE (3):

The Bidder must also provide registered person contact details by completing table 12.

Table 12: Electrician Contact Details

| No | Contact person, telephone and/or e-mail address |
| --- | --- |
| 1 | <Person Name> <Tel> or <email> |

## Diesel Mechanic Technician Requirements

Attach to ANNEX A copy of valid Trade Test Certificate indicating that the Diesel Mechanic is qualified with five (5) years of experience post-trade test certificate.

NOTE (1):

SITA reserves the right to verify the information provided

NOTE (2):

SITA reserves the right to confirm consent of submission from the Diesel Generator Technician.

NOTE (3):

The Bidder must also provide registered person contact details by completing table 13.

Table 13: Diesel Mechanic Contact Details

| No | Contact person, telephone and/or e-mail address |
| --- | --- |
| 1 | <Person Name> <Tel> or <email> |

## Equipment Data Sheets

Attach the following completed and signed Data Sheet here listed in Annex C:

NOTE (1):

SITA reserves the right to verify the information provided.

NOTE (2):

Failure to complete the Data Sheet fully will result in disqualification.

## Special Conditions of Contract

The Bidder must accept ALL the Special Conditions of Contract by completing and signing the declaration of Acceptance in Declaration of compliance and acceptance under the Special Conditions (Section 4.3.1).

Note (1):

Failure to accept ALL the Special Conditions of Contract will result in disqualification.

# Preference Points Preferential Goals Evidence

The Bidder must provide the following Preference Goal Requirements evidence and attach it here:

          - B-BBEE Requirements:

# Promotion of Transformational Objectives

          - Bidder to select the section for points they wish to claim (Mark as Y=Yes) in either tables 9A or 9B in section 4.6, dependant on which preference system the Bidder selects in line with section 4.6; and

          - Provide a copy of the following relevant evidence for the Preferential Goal points which the Bidder qualifies for as set out in table 7 or 8 in section 4.6 and attach it here:

    - Columns A, B, C and D in tables 9A or 9B:

Copy of relevant proof of the following to confirm the B-BBEE status of the contributor as defined in the Broad-Based Black Economic Empowerment Act:

- B-BBEE certificate (from a SANAS Accredited Agency);

or

- Sworn affidavit in the format provided by CIPC - Applicable to EMEs and QSEs only;

and/ or

    - Column D in tables 9A or 9B:

Copy of South African Identification Document (ID):

and/ or

    - Column E in tables 9A or 9B:

Copy of Medical Certificate clearly indicating the disability in line with the B-BBEE status claimed as defined in the Broad-Based Black Economic Empowerment Act.

Note(3):

The CIPC (Companies and Intellectual Property Commission) registration documents will also be used as evidence to confirm compliance to the Preferential procurement requirements as part of the evaluation process.

          - The promotion of Local Products in line with the PPP.

In line with the promotion of Local Products SITA will allocate Preference Points to Bidders whose products contain Local Content and production for Electrical and Telecom cables.

          - Bidder to select the section for points they wish to claim (Mark as Y=Yes) in either tables 9A or 9B in section 4.6, dependant on which preference system the Bidder selects in line with section 4.6; and

          - Provide a copy of the following relevant evidence for the Preferential Goal points which the Bidder qualifies for as set out in tables 7 or 8  in section 4.6 and attach it here:

# Evidence:
Bidder must complete, sign and submit the Local Content Requirements as indicated in Annex D.

# (3)	Indicate their commitment to claim points for each of the preference points by signing at par 4.5 in the Invitation to Bid document.

NOTE (1):

Failure on the part of a bidder to comply to paragraphs (1) and (2) and (3) above, will be interpreted to mean that preference points are not claimed.

CIDB Registration Requirement

The Bidder needs to complete and sign ANNEX B to confirm that the Bidder, is registered with the Construction Industry Development Board (CIDB) with a minimum rating or higher of 7EB, or 7EP.

      - The Bidder needs to indicate the CIDB rating by ticking next to the relevant CIDB rating in the table below:

| Service and Support (Milestones) | CIDB Rating | Bidder to Indicate the Bidder’s rating here |
| --- | --- | --- |
| CIDB Rating | 7EB |  |
|  | 7EP |  |
|  | Higher |  |

      - The Bidder needs to provide the Bidder’s CRS number in the space in the table below:

| Requirement | Bidder’s CRS Number |
| --- | --- |
| Bidder CRS number relating to the minimum rating of 7EB |  |
| Bidder CRS number relating to the minimum rating of 7EP |  |
| Bidder’s CRS number relating to the higher rating of EB or EP |  |

      - The Bidder confirms and will ensure compliance to the CIDB Basic Guide General Conditions of Contract for Construction Works (GCC 2004) as referred to in Annex E for the Bid Specification Scope of work for the duration of the contract.

NOTE 1:

SITA reserves the right to verify the information.

I, the Supplier (Full names) …………………………………………………. Representing (company name) …………………………………………………………….. hereby confirm that the Bidder is registered with Construction Industry Development Board (CIDB) and understand that it will form part of the contract and is legally binding.

Thus, done and signed at ……………………………………. On this………day of……………….20….

__________________

Signature

Designation:

Technical Information

# Technical Information

## Project Drawings

- 1001668_ZUT_DRG_EL_601.

- 1001668-0000-DRG-EE-SCH-006.

- 1001668-0000-DRG-EL-122-GEN.

## Project Specifications

- eSDHS-01299 SITA Generator Technical Specification.

- eSDHS-01355_SITA Electrical Technical Specification.

## Project Data Sheets

- Diesel Generator Datasheet - General Requirements.

# Local Content Requirements

# Local Content Requirements:

## The bidder must confirm compliance to the Local Content requirements.

## The following documents are attached to guide guidance in completing the Local Content requirements:

- Document 01:	Guidance Document for the Calculation of Local Content.

- Document 02:	South African National Standard:  Local goods, services and work –

Measurement and verification of local content.

## The Bidder must complete, sign and submit the following documents at bid closure:

- Document 03:	SBD 6.2 Declaration Certificate for Local Production and content for

Designated Sectors.

- Document 04:	Annexure C: Local Content Declaration.

The following Annexures should not be submitted by the bidder, however be kept by the by the bidder and be provide the documents upon request.

- Document 05: 	Annexure D: Imported Content Declaration.

- Document 06: 	Annexure E: Local Content Declaration.

NOTE: Failure to complete, sign and submit the documents as requested in section 7.3 above at bid closing will result in disqualification.

CIDB Basic Guide General Conditions of Contract for Construction Works (GCC 2004)

Refer to Attached document.