{"text_format":"3","workbook":"xls","n_sheets":31,"sheets":["Cover","Preamble","Prov Sum","PS Coll","ELECTRICAL BoQ","EL Coll","B of Q T","TI Coll","B of Q PA","PA Coll","BofQCCTV","CCTV Coll","B of Q MS","MS Coll","B of Q NC","NC Coll","BofQ TV","TV Coll","B of Q LP","LP Coll","BofQ UPS","UPS Coll","BofQ DCS","DC Coll","BofQ S","SI Coll","FDE Bill1","FDE Bill2","Collect","FINAL SUMMARY","COLLECTION PAGES"],"not_rendered":{"external_links":1,"defined_names":31,"comments":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Cover","index":0,"n_rows":17,"n_cols":3,"rows_kept":17,"flags":["formulas_cached_only"]}
{"$rows_empty":7}
["SECTION 3"]
[]
[]
[null,null," "]
[]
[]
["GENERAL ELECTRICAL INSTALLATION"]
[]
[]
["BILLS OF QUANTITIES"]

{"sheet":"Preamble","index":1,"n_rows":29,"n_cols":5,"rows_kept":29,"flags":["formulas_cached_only"]}
["PORT SHEPSTONE REGIONAL HOSPITAL"]
["NEW PSYCHIATRIC WARD"]
["PORT SHEPSTONE REGIONAL HOSPITAL "]
["NEW PSYCHIATRIC WARD"]
[]
["PREAMBLE"]
[]
["These Bills of Quantities form part of the Contract Documents, together with the drawings and are to be read in conjunction therewith. It shall be completed and returned upon tender closing date."]
[]
["A price or rate shall be entered against each item in the Bills of Quantities, whether quantities are stated or not.  Items which are not priced shall be considered as covered by other prices or rates in this Bills of Quantities. ",{"$nulls":3}," "]
[]
["Provisional cost amounts shall be treated as stated in the Conditions of Contract and in the "]
["Bills of Quantities."]
[]
["The Quantities in the Bills of Quantities are to be regarded as approximate and not necessarily the actual quantities of work  to be done."]
[]
["The unit rates entered into the Bills of Quantities shall include the cost of all smaller items of installation according to the requirements of the Specification and generally required for the Electrical and Associated Installations."]
[]
["The exact net quantity of measured work shall be taken as the basis for payment to the Contractor. The Contractor must allow in the rates for all cutting and waste."]
[]
["No alteration, additions or erasure may be made to the text of the Bills.  If such an alteration, addition or erasure is made, it shall not be acknowledged and the original wording of the text shall apply."]
["The unit rate entered under the heading \"unit rate\" shall be taken as the correct rate tendered for the execution of the Work.  Should there be any difference between the grand total of the Bills rates and the Tender prices, the Electrical Engineer shall have the right to make adjustments to individual prices as may be deemed necessary in order to reconcile the grand total of the Bills of Quantities with the Tender Price. In such an event the contractor will be consulted , but failing to reach an agreement between the two parties, the decision of the Electrical shall be final and binding.  "]
["General directions and descriptions of work and material given in the Specification are not necessarily repeated in the Bills of Quantities."]
["The Contractor shall refer to the Specification for this information."]
[]
["The final Contract Value for the completed contract shall be calculated from the actual measured material used and work done priced against the unit rate tendered for the various items in the Bills of Quantities."]
[]
["All prices and tariffs completed herein shall be net, VAT shall be added to the sub total to give an inclusive Final Contract Value."]
["EP"]

{"sheet":"Prov Sum","index":2,"n_rows":54,"n_cols":6,"rows_kept":54,"flags":["formulas_cached_only"]}
[null,"PORT SHEPSTONE REGIONAL HOSPITAL, NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"PROVISIONAL SUM"]
[1,"Allow a provisional sum for the recovery"]
[null,"of non- indeterminable Works related to the"]
[null,"Demolishment of Structures during "]
[null,"the construction process on site",{"$nulls":3},{"v":40000,"d":"40,000.00"}]
[]
[]
[null,"Profit and Attandance"]
{"$rows_empty":36}
[null,"Carried to following Page",null,null,"R",{"v":40000,"d":"40,000.00"}]
[]
[]
[null,null,"PS6/1"]

{"sheet":"PS Coll","index":3,"n_rows":48,"n_cols":4,"rows_kept":48,"flags":["formulas_cached_only"]}
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL NEW PSYCHIATRIC WARD"]
[]
[null,"ELECTRICAL INSTALLATIONS  (CPAP Work Group No. 160)"]
[]
[null,"PROVISIONAL SUM"]
[]
[null,"COLLECTION PAGE"]
[]
[""]
[]
[{"$nulls":3},"AMOUNT"]
[]
[]
[null,"Total brought forward from pages","PS6/1",{"v":40000,"d":"R 40,000.00"}]
{"$rows_empty":29}
[null,"Total Carried forward to Summary page  (ESP)",null,{"v":40000,"d":"R 40,000.00"}]
[]
[null,null,"PS6/2"]

{"sheet":"ELECTRICAL BoQ","index":4,"n_rows":3096,"n_cols":6,"rows_kept":3096,"flags":["formulas_cached_only"]}
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"PREAMBLES"]
[null,"Refer to attached Specification for the"]
[null,"General Electrical Installation"]
[]
[1,"GUARANTEE AND MAINTENANCE"]
[null,"Guarantee and maintenance for the complete"]
[null,"installation of the General Electrical Installation"]
[null,"including fittings, materials and workmanship for a"]
[null,"period of TWELVE MONTHS after date of"]
[null,"completion","item"]
[]
[2,"TESTING"]
[null,"Allow for testing and commissioning the whole"]
[null,"of the electrical installation as laid down in the"]
[null,"specification, for retesting as may be required"]
[null,"after the making good of all defective work to the"]
[null,"entire satisfaction of the Department  of Works"]
[null,"Works, the Department of Health and the "]
[null,"Electrical Engineer.","Item"]
[]
[3,"AS BUILT DRAWINGS"]
[null,"Provision for the drawings showing all site"]
[null,"cable routes, conduit routes, drawboxes"]
[null,"and positions of outlets, etc.","Item"]
[]
[4,"CERTIFICATES of COMPLIANCE"]
[null,"Provision for the Certificates of Compliance"]
[null,"to be issued on completion of the project","Item"]
[]
[5,"SUPPLY CABLES to BUILDINGS to be"]
[null,"DEMOLISHED"]
[null,"The supply cables to the Existing Buildings to"]
[null,"be Demolished are to be recovered as "]
[null,"directed on site and to be handed over to the "]
[null,"hospital Staff. A schedule of cables removed "]
[null,"is to be compiled, signed the designated "]
[null,"Hospital member and submitted to the "]
[null,"Electrical Engineer ","Item"]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/1"]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[1,"REINFORCED CONCRETE to be "]
[null,"DEMOLISHED"]
[null,"Steel Reinforced Concrete to be Demolished"]
[null,"in order to install Cable Pipes under existing"]
[null,"Pathways Measured in Cubic Metres","M³",4]
[]
[2,"Temporary Supply Cable to Site Office"]
[null,"Allow to Supply and Install a Temporary Supply "]
[null,"to the Site Office consisting of the Supply cable "]
[null,"and Disbordette as per Specification","Item"]
[]
[3,"Repositioning of cable to the Oxygen Storage"]
[null,"Tank Set"]
[null,"The New position of the Oxygen Storage Tank Set"]
[null,"is indicated on the Site Plan Drawing"]
[null,"Noted that the new Road  and Pathways are to be"]
[null,"repositioned and that the Electrical Installations "]
[null,"are to be secured during in the surrounds during "]
[null,"Construction work on Site","Item"]
[]
[4,"SUB STATION UPGRADES"]
[null,"Allow to supply and install the Works described for"]
[null,"upgrades to be undertaken all as Part of the Sub "]
[null,"Station Upgrades including New Main Supply "]
[null,"Switchgear, New Bus Bar Run, New section to be  "]
[null,"added to the Existing West Sub Station Main Low"]
[null,"Tension Switchboard, the New Standby Generator "]
[null,"Set including, New Control panel, alterations and"]
[null,"the essential works related to these upgrades "]
[null,"works related to these upgrades including the "]
[null,"related alterations to existing Installations all as"]
[null,"described and allowed for under the various "]
[null,"applicable sections.It must be noted however that"]
[null,"various of these alterations will have to be carried"]
[null,"out outside of normal working hours, at times "]
[null,"to be arranged with the responsible hospital"]
[null,"personnel.  The contractor must ensure that"]
[null,"full co-operation must be made in this respect"]
[null,"so that there is no undue inconveniences"]
[null,"caused that may unduly affect the normal"]
[null,"function of the Hospital. ","Item"]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/2"]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[1,"EXISTING SWITCHGEAR and INSTRUMENTS    "]
[null,"to be REMOVED from the MAIN "]
[null,"TRANSFORMER SWITCHBOARD"]
[null,"Noted that the switchgear and Instruments are "]
[null,"to be handed over to the designated Hospital Staff"]
[null,"member and that an acceptance document is to"]
[null,"submitted to the Electrical Engineer as soon as"]
[null,"possible after removal","Item"]
[]
[2,"Existing 800Amp 3P MCB feeding the "]
[null,"Main Switchboard in the West Substation","Item"]
[]
[3,"Existing 400Amp 3P MCB feeding the Laundry","Item"]
[]
[4,"The Existing Instruments including Ammeters,"]
[null,"Voltmeters, selector switch and Protection "]
[null,"switchgear","Item"]
[]
[5,"THE EXISTING SUPPLY CABLES to the "]
[null,"WEST SUB STATION"]
[null,"Allow to remove the two 185mm² 4-core PVC SWA "]
[null,"PVC cables routed at high level via the passage "]
[null,"way separating the two Substations"]
[null,"The cables are to be recovered and handed over to "]
[null,"the designated hospital staff member and that an "]
[null,"acceptance document to be submitted to the"]
[null,"Electrical Engineer as soon as possible after "]
[null,"removal","Item"]
[]
[6,"Existing Supply Cable to the Laundry"]
[null,"Allow to recover and divert the existing cable "]
[null,"consisting of a 150mm² 4-core PVC SWA PVC ECC"]
[null,"cable, presently routed via the cable trench to the "]
[null,"existing Transformer Sub Station, to the Main "]
[null,"Switchboard in the West Substation"]
[null,"Noted that the cable has been installed via. the"]
[null,"Service Tunnel and that it is to be repositioned."]
[null,"via new cable pipes to be installed all as part of the "]
[null,"contract","Item"]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/3"]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[1,"The NEW MAIN ACB and INSTRUMENTS"]
[null,"The NEW MAIN ACB and INSTRUMENTS to be "]
[null,"installed into the existing Main Transformer "]
[null,"Switchboard including fabrication of the Existing "]
[null,"Switchboard front Panels to accommodate the "]
[null,"revisions, all as follows:","Item"]
[]
[2,"NEW MAIN ACB "]
[null,"Supply and install a New 1600 Amp Triple"]
[null,"Pole 50kA  Air Circuit Breaker MITSUBISHI "]
[null,"Type AE 2000-SS or other equal and approved type "]
[null,"to be built into existing Sub Station Switchboard"]
[null,"complete with bus bar connections to"]
[null,"existing switchboard bus bars and New"]
[null,"Overhead Bus Bar run supply to existing West"]
[null,"Sub Main Low Tension Switchboard.","No",1]
[]
[3,"NEW INSTRUMENTS (New ACB)"]
[null,"Supply and Install New Instrument Sets:"]
[null,"Three 0 to 2000Amp Ammeters, 0 to 400Volt "]
[null,"Voltmeter, selector Switch to select Voltages "]
[null,"between Phases, Phases to Neutral and Off and "]
[null,"a set of fuse cartridges and Protection fuses ","Item"]
[]
[4,"NEW FRONT PANELS "]
[null,"Supply and install new Fabricated Front Panels"]
[null,"to allow for the revisions as above. The "]
[null,"specification to follow the requirements "]
[null,"described for Distribution boards all as per"]
[null,"detail Specifications. The Front Panels to "]
[null,"all required Labels, consisting of all LEGAL and  "]
[null,"INFORMATION Labels and Nameplates as "]
[null,"per Specification","Item"]
[]
[]
[]
[]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/4"]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[1,"NEW OVERHEAD BUS BAR SUPPLY"]
[null,"Supply and install the New Overhead Bus Bar "]
[null,"Supply System between the New ACB installed"]
[null,"in the Existing Main Low Tension Transformer"]
[null,"Switchboard and the New Main Switch to be"]
[" ","installed in the West Substation Main Low Tension"]
[null,"Switchboard, consisting of a new 2000Amp"]
[null,"Three Phase and Neutral including Earth Bar,"]
[null,"as specified in the Detail Specification","m",28]
[]
[2,"TERMINATIONS for the Bus Bar Run"]
[null,"Allow for Terminations for the above bus bar"]
[null,"System including continuation of bus bars onto"]
[null,"the switchgear terminals and neutral bars"]
[null,"on both ends, including bolting the outer "]
[null,"casing onto the switchboards. Noted that this will"]
[null,"be applicable to both Main Switchboards, in the "]
[null,"East and West Sub Stations","No",2]
[]
[3,"BUS BAR RUN BENDS"]
[null,"Ninety degree (90°) bends consisting of"]
[null,"both lateral and inside bends as indicated"]
[null,"installed as part of the bus bar system","No",5]
[]
[4,"STRUCTURAL SUPPORTS: for BUS BAR RUN"]
[null,"The structural supports consisting of P1000"]
[null,"Galvanised Unistrut Sections and 8mm Diameter "]
[null,"Galvanised Steel Supports bolted to walls "]
[null,"600mm long  8mm in Diameter Galvanised Steel "]
[null,"Hangers, at 800mm intervals along the entire  "]
[null,"length of run","No",30]
{"$rows_empty":8}
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/5"]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[1,"THE EXISTING MAIN WEST SUBSTATION"]
[null,"LOW TENSION SWITCHBOARD "]
[null,"The Revisions consist of a NEW SECTION "]
[null,"and ALTERATIONS TO THE EXISTING "]
[null,"Noted that during the Revision process Power  "]
[null,"Supply to the Hospital Distribution Boards "]
[null,"and Service Control Panels must be maintained"]
[null,"with a minimum interruption of power as possible.","Item"]
[]
[2,"The NEW SECTION to be REPLACED ~NOTE~ "]
[null,"the entire replacement of the Non and"]
[null,"Essential Sections of the Existing Switchboard"]
[null,"Allow to Supply and Install the New Board"]
[null,"all as a part of the sub Local Board as indicated"]
[null,"and detailed on Drawing SL231-SUB1"]
[null,"The New Board is to be accommodated to the "]
[null,"left side of the Existing Switchboard"]
[null,"The New Board to accommodate the \"Detail of "]
[null,"Switchgear\" etc.as specified para. below","Item"]
[]
[3,"NEW MAIN ISOLATOR"]
[null,"New 2000Amp 3phase 50kA Rated ON-LOAD "]
[null,"ISOLATOR MITSUBISHI Type AE 2000-SS range "]
[null,"or other equal and approved type as the","No",1]
[null,"NEW MAIN Switch"]
[]
[4,"NEW INSTRUMENTS (West Sub Main SB) "]
[null,"Supply and Install New Instrument Sets:"]
[null,"Three 0 to 2000Amp Ammeters, 0 to 400Volt "]
[null,"Voltmeter, selector Switch to select Voltages "]
[null,"between Phases, Phases to Neutral and Off, and "]
[null,"a set of fuse cartridges and Protection fuses ","Item"]
[]
[5,"THE EXISTING AND NEW BUS BAR RUNS"]
[null,"Allow to remove the Existing Bus  Bar Runs in the "]
[null,"Non - Essential Section of the Switchboard and re-"]
[null,"place with 4 x 2000Amp Rated Section HDHC Bars"]
[null,"on Suitably sized Cast Resin Bus Bar mounting "]
[null,"supports for the entire estimated 2800mm width  "]
[null,"of the panel. Ie Total Bus Bar length."]
[null,"Allowance as follows","14m"]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/6"]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[1,"ALTERATIONS TO THE EXISTING NON and "]
[null,"ESSENTIAL sections of the Switchboard"]
[null,"Allow for the ALTERATIONS SPECIFIED for the"]
[null,"Existing NON-and ESSENTIAL SECTIONS as indicated"]
[null,"and detailed on Drawing PE231-SUB1"]
[null,"The Panel Section to accommodate the \"Detail of "]
[null,"NE/E Switchgear\" etc.as specified para. below"]
[null,"the removal and refabrication requirements and  "]
[null,"include all relevant connections between new "]
[null,"Bus Bars and Cable connections as required","Item"]
[]
[2,"Removal of the existing of the Existing Switchgear, "]
[null,"Bus Bars and Instruments, all as specified","Item"]
[]
[3,"Supply and Install a New 800Amp 3phase 40kA"]
[null,"Circuit breaker to feed the New Standby Generator"]
[null,"Set Control Panel","No ",1]
[]
[4,"Supply and Install a New 600Amp 3phase 40kA"]
[null,"Circuit breaker to feed the New Psychiatric Ward","No",1]
[]
[5,"Supply and Install a New 400Amp 3phase 35kA"]
[null,"Circuit breaker to feed the Existing Hot Water "]
[null,"Heating Panel","No",1]
[]
[6,"Supply and Install a New 400Amp 3phase 35kA"]
[null,"Circuit breaker to feed the Existing Laundry Main"]
[null,"Distribution Board","No",1]
[]
[7,"Provide the Spare provisions for future Switchgear","Item"]
[]
[8,"Allow to Supply and Install the New Supply cable"]
[null,"from the Specified 800Amp 3phase Circuit Breaker "]
[null,"(refer above) to the New Standby Set control Panel"]
[null,"consisting of 2 x 240mm² PVC SWA PVC cables ","m",20]
[null,"and a 70mm² PVC Insulated Earth Conductor"]
[null,"including overhead support system"]
[]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/7"]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[1,"The New ESSENTIAL Section of the Board"]
[null,"Allow for the NEW BOARD SPECIFIED for the"]
[null,"Existing ESSENTIAL SECTION as indicated"]
[null,"and detailed on Drawing SL231-SUB1"]
[null,"The Panel Section to accommodate the \"Detail of "]
[null,"Essential Switchgear\" etc.as specified para. below"]
[null,"the removal and refabrication requirements and  "]
[null,"include all relevant connections between new   "]
[null,"Bus Bars and Cable connections as required","Item"]
[]
[2,"Removal of the existing of the Existing "]
[null,"existing Switchgear etc."]
[null,"including the existing By-Pass Switch,"]
[null,"Bus Bars and Instruments, all as specified","Item"]
[]
[3,"NEW INSTRUMENTS (New Essential Section)"]
[null,"Supply and Install New Instrument Sets:"]
[null,"Three 0 to 1000Amp Ammeters, 0 to 400Volt "]
[]
[4,"Voltmeter, selector Switch to select Voltages "]
[null,"between Phases, Phases to Neutral and Off and "]
[null,"a set of fuse cartridges and Protection fuses ","Item"]
[]
[5,"Supply and Install a New 1000Amp 3phase 40kA"]
[null,"Main Isolator as Main Switch fed from the New "]
[null,"Standby Generator Set Control Panel","No ",1]
[]
[6,"Supply and Install a New 200Amp 3phase 40kA"]
[null,"Circuit breaker to feed the New Psychiatric Ward","No",1]
[]
[7,"Supply and Install a New 400Amp 3phase 35kA"]
[null,"Circuit breaker to feed the Existing DB.LG "]
[null,"West Block Distribution Board","No",1]
[]
[8,"Provide the Spare provisions for future Switchgear","Item"]
[null,"as indicated"]
[]
[]
[]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/8"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"NEW SITE KIOSK (To replace the Existing)"]
[1,"Allow to Supply and Install a New Site Kiosk."]
[null,"The new position for the Kiosk is shown on the "]
[null,"Main Site plan, the position adjacent to the west "]
[null,"of the existing Roadway and adjacent to the"]
[null,"Main Core Block building."]
[2,"The exsiting Kiosk is to be de-commissioned and "]
[null,"removed from Site"]
[3,"The New Kiosk is be built into the adjacent wall in"]
[null,"position as shown"]
[4,"The New Kiosk shall consist of a 3CR12 Metal Unit"]
[null,"comprising of High Grade Coastal Quality.  "]
[5,"Door locks shall be fitted with a 80mm Padlock"]
[null,"and Keys signed for by a Hospital  Maintenance  "]
[null,"Staff Representive, original to be placed in the"]
[null,"Handover Documentation File."]
[6,"Noted that the existing Kiosk is fed from DB.LG"]
[null,"which is located in the Switchroom in the Adjacent  "]
[null,"West block.  The supply to DB.LG is ESSENTIAL POWER SUPPLY"]
[7,"The Kiosk shall contain the following:"]
[null,"4 x 200A Bus Bars (each 600mm long ) mounted","m",1]
[null,"on Insulated supports plus appropietely sized "]
[null,"Earth Bar"]
[8,"200A TP 15kA MAIN ISOLATOR","No",1]
[9,"0-200A Ammeters and 200/5A CT`s","No",3]
[10,"Voltmeter and 5Amp 7way  Selector Switch","No",1]
[11,"80A TP 15kA MCB`s","No",4]
[12,"60A TP 15kA MCB`s","No",2]
[13,"35A TP 15kA MCB`s","No",5]
[14,"25A TP 15kA MCB`s","No",3]
[15,"20A TP 15kA MCB`s","No",1]
[]
[null,"Allow to Extend the Cables including jont kits, and "]
[null,"cable ends, sizes as follows"]
[16,"70mm2 4-core ECC","No",1]
[17,"25mm2 4-core ECC","No",4]
[18,"16mm2 4-core ECC","No",6]
[19,"6mm2 2-core ECC","No",4]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/9"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"RELOCATION of OXYGEN TANK"]
[]
[null,"Allow to fully engage from the initial stage of the "]
[null,"relocation process iro. the Existing Oxygen Tank  "]
[null,"Installation until final handover. ","Item"]
[]
[null,"Allow to disconnect and for the reinstallation of the"]
[null,"existing Electrical Installation.","Item"]
[]
[null,"The Existing Installation consists of a dedicated"]
[null,"Distribution board that must be replaced with a new "]
[null,"Weatherproof Switch Board "]
[null,"The Board shall be an Outdoor Weatherproof type"]
[null,"secured by means of 4x6mm Dia. Rawlbolts to the  "]
[null,"support structure.","Item"]
[]
[null,"The content of the Board shall consist of the"]
[null,"following:"]
[]
[null,"60 Amp 15kA  3-phase Isolator","No",1]
[null,"25 Amp TP 10kA CB to feed the Main Circuit","No",1]
[null,"10 Amp SP 5kA Mccb`s to feed the Control Circuit","No",2]
[]
[null,"Provide Live Bus Bars and Earth Bar  ","Item"]
[]
[null,"Allow to extend the Exist. Supply Cable consisting "]
[null,"of a 6mm2 4-core PVC SWA PVC ECC and","m",50]
[null,"Control Cable 4mm2 4-core PVC SWA PVC ECC","m",50]
[]
[null,"Allow to supply and install joint kits as follows:"]
[null,"For above cables                     "]
[null,"6mm2 4-core","No",1]
[null,"4mm2 4-core","No",1]
[]
[null,"Allow to finally test and hanover","Item"]
[]
[]
[]
[]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E610"]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"NEW RETICULATION CABLES and Related "]
[null,"External Installations "]
[null,"Allow to Supply and Install the New Power Supply"]
[null,"Cables from the NEW West Sub Station Main"]
[null,"Low Tension Switchboard and the New Psychiatric "]
[null,"Main distribution Board as follows: "]
[null,"NEW MAIN NON - ESSENTIAL LT Supply Cable"]
[1,"Two 240mm² 4-core ECC PVC SWA PVC cables"]
[null,"installed via. the existing Sub Station, the existing "]
[null,"service Tunnel, existing and new cable pipes/"]
[null,"manholes as shown on the Site Plan Drawing"]
[null,"SL231 - ESP1"]
[" ","Two lengths of 162m x 2 x (times) equals 324m","m",324]
[]
[null,"NEW MAIN ESSENTIAL LT Supply Cable"]
[2,"One 185mm² 4-core ECC PVC SWA PVC cable"]
[null,"installed via. the existing Sub Station, the existing "]
[null,"service Tunnel, existing and new cable pipes/"]
[null,"manholes as shown on the Site Plan Drawing"]
[null,"SL231 - ESP1","m",162]
[]
[null,"NEW LIFT  Standby Control Cable"]
[3,"One 4,0mm² 4-core ECC PVC SWA PVC cable"]
[null,"installed via. the existing Sub Station, the existing "]
[null,"service Tunnel, existing and new cable pipes/"]
[null,"manholes as shown on the Site Plan Drawing"]
[null,"SL231 - ESP1","m",262]
[" "]
[null,"Note:  The cable gland ends and cable joints "]
[null,"are to be allowed and included all as part of the"]
[null,"above Reticulation Cable section of these"]
[null,"Bills of Quantities"]
[null,"RETICULATION CABLE TERMINATIONS"]
[null,"Supply and Install cable glands strip back and gland"]
[null,"off with shrouds over the glands and final "]
[null,"connections to terminals using crimping lugs, "]
[null,"cadmium plated bolts, nuts and lock washers. "]
[null,"(All PVC SWA PVC ECC cables)"]
[4,"240mm² 4-core ECC Cable terminations","No",4]
[5,"180mm² 4-core ECC Cable terminations","No",2]
[6,"4mm² 4-core ECC Cable terminations","No",4]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/11"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"MAIN and SUB DISTRIBUTION BOARDS "]
[null,"Supply and Install, delivery to site, storage of "]
[null,"the floor standing , flush and semi-flush mounted"]
[null,"architrave steel type power distribution boards"]
[null,"complete with doors, switchgear mounting"]
[null,"trays, copper bus bars, PVC wiring, labelling"]
[null,"and legend cards including flush trays and"]
[null,"equipment as listed below and in each case "]
[null,"refer to the applicable LINE DIAGRAM DRAWING "]
[null,"as indicated all as follows:"]
[null,"The Fabrication includes the tubular metal structure"]
[null,"of the Distribution Boards and all components, "]
[null,"including removable front and back metal panels,"]
[null,"fixed side panels, doors, base plinths, cable trays, "]
[null,"switchgear mounting trays, etc. and all sundry "]
[null,"items required as an integral part of switchboard "]
[null,"manufacture, all as described fully in the Detail and"]
[null,"supporting Specifications allowing 30% spare "]
[null,"Capacity. Fabrication and Equipment details below:"]
[]
[null,"Parking Level Distribution Boards"]
[null,"NEW MAIN LT DISTRIBUTION BOARD "]
[1,"NEW MAIN LT DISTRIBUTION BOARD to be "]
[null,"installed into the New LT SWITCH ROOM "]
[null,"NEW PSYCHIATRIC WARD: PARKING LEVEL"]
[null,"Allow to Supply and Install the NEW LT DB "]
[null,"equipped as per the Line Diagram on Drawing"]
[null,"SL 231 - ELD1 and fabricated and equipped as"]
[null,"follows, Floor Standing on a 80mm High Metal "]
[null,"Architrave. Allow for fabrication","Item"]
[null,"NON - ESSENTIAL SECTION"]
[2," 4 x 800A Bus Bars plus Earth Rated 25kA  ","m",1]
[3,"1000A TP 35kA MAIN ISOLATOR","No",1]
[4,"0-800A Ammeters and 800/5A CT`s","No",3]
[5,"Voltmeter and 5A 7way  Selector Switch","No",1]
[6,"400A TP 25kA CB","No",1]
[7,"300 TP 15kA CB ","No",1]
[8,"200A TP 15kA CB ","No",1]
[9,"125A TP 15kA CB ","No",1]
[10,"50A TP 15kA CB ","No",2]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/12"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"continued"]
[1,"35A TP 15kA CB`s","No",2]
[2,"25A TP 15kA CB`s ","No",4]
[]
[null,"ESSENTIAL SECTION  (Continued)"]
[3,"4 x 200A Bus Bars plus earth Rated 15kA  ","m",1]
[4,"200A TP  25kA MAIN ISOLATOR","No",1]
[3,"0-200A Ammeters and 200/5A CT`s","No",3]
[4,"Voltmeter and 5A 7way  Selector Switch","No",1]
[5,"80A TP 15kA MCB`s","No",1]
[6,"45A TP 15kA MCB","No",1]
[7,"35A TP 15kA MCB`s","No",5]
[8,"25A TP 15kA MCB`s","No",4]
[9,"20A TP 15kA MCB`s","No",4]
[]
[null,"New Sub DB.PL "]
[10,"New Sub DB.PL - Semi-Flush Wall mounted "]
[null,"with 50mm stand off Metal Architrave located "]
[null,"in the Switch room equipped as per the"]
[null,"Line Diagram on Drawing PE231 - ELD1 "]
[null,"Allow for Fabricated:","Item"]
[]
[null,"NON - ESSENTIAL SECTION"]
[11,"Set of 4 x 60A Bus Bars plus Earth Rated 15kA  ","m",1]
[12,"60A TP 15kA Isolator","No",1]
[13,"25A TP 10kA CB","No",1]
[14,"60A DP 5kA E/L Units","No",1]
[15,"20A SP 5kA MCB`s","No",4]
[]
[null,"ESSENTIAL SECTION"]
[16,"Set of 4 x 60A Bus Bars plus Earth Rated 15kA  ","m",1]
[17,"60A TP 15kA Isolator","No",1]
[18,"15A TP 5kA CB","No",1]
[19,"10A SP 5kA MCB`s","No",16]
[null,"Outside Lights"]
[20,"25A TP 5kA CB","No",1]
[21,"5A SP MCB","No",1]
[22,"30A TP Contactor","No",1]
[23,"10A SP&N 5kA MCB`s","No",2]
[24,"24/7 Timer to operate Contactor for Outside lights","No",1]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/13"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"Parking Bay Lights"]
[1,"35A TP 5kA CB","No",1]
[2,"5A SP MCB","No",1]
[3,"24Hr Time Switch with Battery Reserve ","No",1]
[4,"30A TP Contactors","No",2]
[5,"10A SP&N 5kA MCB`s","No",8]
[6,"25A TP 5kA CB","No",1]
[7,"5A SP MCB for DAY LIGHT SWITCH","No",1]
[]
[null,"New Sub DB.GH "]
[8,"New Sub DB.GH - Semi-Flush Wall mounted "]
[null,"with 50mm stand off Metal Architrave located "]
[null,"in the Guard House equipped as per the"]
[null,"Line Diagram on Drawing SL231 - ELD1 "]
[null,"Allow for Fabricated:","Item"]
[]
[null," ESSENTIAL SECTION"]
[9,"Set of 4 x 60A Bus Bars plus Earth Rated 15kA  ","m",1]
[10,"60A TP 15kA Isolator","No",1]
[11,"25A TP 10kA CB","No",1]
[12,"60A DP 5kA E/L Unit","No",1]
[13,"20A SP 5kA MCB`s","No",4]
[14,"10A SP 5kA MCB`s","No",4]
[]
[null,"New Sub DB.PU - Semi-Flush Wall mounted "]
[15,"New Sub DB.PU - Semi-Flush Wall mounted "]
[null,"with 50mm stand off Metal Architrave located "]
[null,"SERVICE SECTION"]
[null,"Line Diagram on Drawing SL231 - ELD1 "]
[null,"Allow for Fabricated:","Item"]
[]
[null," ESSENTIAL SECTION"]
[16,"Set of 4 x 60A Bus Bars plus Earth Rated 15kA  ","m",1]
[17,"60A TP 15kA Isolator","No",1]
[18,"25A TP 10kA CB","No",2]
[19,"60A DP 5kA E/L Unit","No",1]
[20,"20A SP 5kA MCB`s","No",2]
[]
[]
[]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/14"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"New DB.PLA"]
[1,"New Sub DB.PLA - Surface Wall mounted "]
[null,"located in the Water Storage Room equipped as "]
[null,"per the Line Diagram on Drawing PE231 - ELD1 "]
[null,"Allow for Fabricated:","Item"]
[null,"NON - ESSENTIAL SECTION"]
[2,"Set of 4 x 60A Bus Bars Rated 15kA  ","m",1]
[3,"60A TP 10kA Isolator","No",1]
[4,"60A DP 5kA E/L Units","No",1]
[5,"20A SP 5kA MCB`s","No",2]
[6,"25A TP 10kA MCB","No",1]
[null,"ESSENTIAL SECTION"]
[7,"Set of 4 x 60A Bus Bars Rated 15kA  ","m",1]
[8,"60A TP 15kA Isolator","No",1]
[9,"10A SP 5kA MCB`s","No",3]
[]
[null,"New Lift Supply DB"]
[null,"New Lift Supply  DB - Surface wall mounted in "]
[null,"Lift Shaft as per Line Diagram Drawing on "]
[10,"SL 231 - ELD1 allow for Fabrication","Item"]
[null,"NON-ESSENTIAL SECTION"]
[11,"Set of 4 x 60A Bus Bars Rated 15kA  ","Item"]
[12,"60A TP 10kA Isolator","No",1]
[13,"25A TP 10kA MCB","No",1]
[]
[null,"New Lift DB.L"]
[14,"New Lift DBL - Surface DB mounted in Lift Shaft"]
[null,"Shaft as per Line Diagram Drawing SL 231 - ELD1"]
[null,"Allow for Fabrication","Item"]
[null,"ESSENTIAL SECTION only"]
[15,"60A Bus Bar Rated 5kA  ","Item",1]
[16,"30A DP 5kA Isolator","No",1]
[17,"60A DP 5kA E/L Units","No",1]
[18,"20A SP 5kA MCB","No",1]
[19,"10A SP 5kA MCB","No",1]
[]
[]
[]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/15"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"NEW PUMP SET SUB DB"]
[1,"New PUMP SET Sub DB - Surface and  mounted in the"]
[null,"Pump Set Plant Room equipped to supply power to two"]
[null,"pumps as per Line Diagram Drawing "]
[null,"SL 231 - ELD1 Allow for Fabrication","Item"]
[null,"ESSENTIAL POWER ONLY"]
[2,"Set of 4 x 60A Bus Bars Rated 15kA  ","Item",1]
[3,"60A TP 15kA Isolator","No",1]
[4,"25A TP 15kA CB`s","No",2]
[5,"15A TP 15kA CB`s","No",4]
[]
[null,"NEW DB.VP"]
[6,"New VACUUM PUMP SET Sub DB - Surface and  mounted in the"]
[null,"Pump Set Plant Room equipped to supply power to two"]
[null,"pumps as per Line Diagram Drawing "]
[null,"SL 231 - ELD1 Allow for Fabrication","Item"]
[null,"ESSENTIAL POWER ONLY"]
[7,"Set of 4 x 60A Bus Bars Rated 15kA  ","Item",1]
[8,"60A TP 15kA Isolator","No",1]
[9,"25A TP 15kA CB`s","No",2]
[]
[null,"NEW DB.OP"]
[10,"New OXYGEN PLANT  Sub DB - Surface  mounted in the"]
[null,"Oxygen Plant Room equipped to supply power to "]
[null,"OXYGEN BANK as per Line Diagram Drawing "]
[null,"SL 231 - ELD1 Allow for Fabrication","Item"]
[null,"ESSENTIAL POWER ONLY"]
[11,"Set of 4 x 60A Bus Bars Rated 15kA  ","Item",1]
[12,"60A TP 15kA Isolator","No",1]
[13,"25A SP 15kA CB`s","No",2]
[]
[null,"NEW DB.P"]
[14,"New DB.P  Sub DB - Surface  mounted in Cupboard "]
[15,"Set of 4 x 60A Bus Bars Rated 15kA  ","Item"]
[16,"60A DP 5kA E/L Units","No",1]
[17,"20A SP 5kA MCB`s","No",2]
[18,"10A SP 5kA MCB`s","No",3]
[]
[]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/16"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"New Ground Floor Level Distribution Boards"]
[]
[null,"NEW DB.G"]
[1,"New Main Ground Floor Level Distribution Board"]
[null,"New DB.G Surface Mounted in Cupboard Space "]
[null,"equipped as per Line Diagram on Drawing "]
[null,"SL 231 -  ELD2 , fabricated and equipped as"]
[null,"follows: Allow for Metal Fabrication",null,"ITEM"]
[]
[null,"NON - ESSENTIAL SECTION"]
[2,"2 Sets of 4 x 100A Bus Bars Rated 15kA  ","m",1]
[3,"100A TP 15kA Isolator","No",1]
[4,"25A TP 15kA CB`s for Supply to DB.GA, DB.GB  ","No",5]
[null,"DB.GC, DB.GD and DB.GE"]
[5,"60A TP 5kA SUB Isolator ","No",1]
[6,"60A DP 5kA E/L Units","No",1]
[7,"20A SP 5kA MCB`s","No",1]
[8,"15A SP&N 5kA MCB`s","No",4]
[]
[null,"ESSENTIAL SECTION"]
[9,"2 Sets of 4 x 100A Bus Bars Rated 15kA  ","m",1]
[10,"100A TP 15kA Isolator","No",1]
[11,"25A TP 15kA CB`s supply to DB`s GA,B,C,D &E","No",5]
[12,"60A TP 5kA Isolator ","No",1]
[13,"60A DP 5kA E/L Units","No",3]
[14,"20A SP 5kA MCB`s","No",1]
[15,"20A SP&N 5kA MCB","No",1]
[16,"10A SP MCB`s","No",3]
{"$rows_empty":11}
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/17"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"UPS SECTION  (DB.G Continued)"]
[1,"Set of 4 x 60A Bus Bars Rated 15kA  ","m",1]
[2,"60A TP 15kA Isolator","No",1]
[3,"60A DP 5kA E/L Units","No",3]
[4,"20A SP 5kA MCB`s","No",1]
[5,"20A DP 5kA MCB","No",1]
[]
[null,"New DB.GA"]
[6,"New Sub DB.GA Ground Floor Level Distribution"]
[null,"Board Surface Mounted in Cupboard Space "]
[null,"equipped as per Line Diagram on Drawing "]
[null,"SL 231 -  ELD2. Allow for Fabrication","Item"]
[]
[null,"NON - ESSENTIAL SECTION"]
[7," Set of 4 x 60A Bus Bars Rated 10kA  ","m",1]
[8,"60A TP 10kA Isolator","No",1]
[9,"15A TP 5kA MCB`s","No",2]
[10,"60A DP 5kA E/L Units","No",3]
[11,"20A SP 5kA MCB`s","No",6]
[12,"15A SP&N 5kA MCB`s","No",2]
[]
[null,"ESSENTIAL SECTION"]
[13," Set of 4 x 60A Bus Bars Rated 10kA  ","m",1]
[14,"60A TP 10kA Isolator","No",1]
[15,"60A DP 5kA E/L Units","No",3]
[16,"20A SP 5kA MCB`s","No",9]
[null,"10A SP MCB`s","No",14]
[]
[null,"UPS SECTION  (DB.G Continued)"]
[17,"Set of 4 x 60A Bus Bars Rated 15kA  ","Item"]
[18,"60A TP 15kA Isolator","No",1]
[19,"60A DP 5kA E/L Units","No",1]
[20,"20A SP 5kA MCB`s","No",2]
[21,"20A TP 5kA MCB`s","No",1]
[]
[]
[]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/18"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"New DB.GB"]
[1,"New Sub DB.GB Ground Floor Level Distribution"]
[null,"Board Surface Mounted in Cupboard Space "]
[null,"equipped as per Line Diagram on Drawing "]
[null,"SL 231 -  ELD2.  Allow for fabrication","Item"]
[]
[null,"NON - ESSENTIAL SECTION"]
[2," Set of 4 x 60A Bus Bars Rated 10kA  ","m",1]
[3,"60A TP 10kA Isolator","No",1]
[4,"60A DP 5kA E/L Units","No",1]
[5,"20A SP 5kA MCB`s","No",4]
[6,"15A SP&N 5kA MCB`s","No",2]
[]
[null,"ESSENTIAL SECTION"]
[7," Set of 4 x 60A Bus Bars Rated 10kA  ","m",1]
[8,"60A TP 10kA Isolator","No",1]
[9,"60A DP 5kA E/L Units","No",3]
[10,"20A SP 5kA MCB`s","No",2]
[11,"10A SP MCB`s","No",22]
[]
[null,"UPS SECTION  "]
[17,"Set of 4 x 60A Bus Bars Rated 15kA  ","Item"]
[18,"60A TP 15kA Isolator","No",1]
[19,"60A DP 5kA E/L Units","No",1]
[20,"20A SP 5kA MCB`s","No",2]
[21,"20A TP 5kA MCB","No",1]
{"$rows_empty":14}
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/19"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"New DB.GC"]
[1,"New Sub DB.GB Ground Floor Level Distribution"]
[null,"Board Surface Mounted in Cupboard Space "]
[null,"equipped as per Line Diagram on Drawing "]
[null,"SL 231 -  ELD2.  Allow for fabrication","Item"]
[]
[null,"NON - ESSENTIAL SECTION"]
[2," Set of 4 x 60A Bus Bars Rated 10kA  ","m",1]
[3,"60A TP 10kA Isolator","No",1]
[4,"60A DP 5kA E/L Units","No",6]
[5,"20A SP 5kA MCB`s","No",16]
[6,"15A SP&N 5kA MCB`s","No",2]
[]
[null,"ESSENTIAL SECTION"]
[7," Set of 4 x 60A Bus Bars Rated 10kA  ","m",1]
[8,"60A TP 10kA Isolator","No",1]
[9,"60A DP 5kA E/L Units","No",3]
[10,"20A SP 5kA MCB`s","No",6]
[11,"10A SP MCB`s","No",19]
[]
[null,"UPS SECTION  "]
[17,"Set of 4 x 60A Bus Bars Rated 15kA  ","Item"]
[18,"60A TP 15kA Isolator","No",1]
[19,"60A DP 5kA E/L Units","No",1]
[20,"20A SP 5kA MCB`s","No",2]
[21,"20A TP 5kA MCB","No",1]
{"$rows_empty":13}
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/20"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"New DB.GD"]
[1,"New Sub DB.GB Ground Floor Level Distribution"]
[null,"Board Surface Mounted in Cupboard Space "]
[null,"equipped as per Line Diagram on Drawing "]
[null,"SL 231 -  ELD2.  Allow for fabrication","Item"]
[]
[null,"NON - ESSENTIAL SECTION"]
[2," Set of 4 x 60A Bus Bars Rated 10kA  ","m",1]
[3,"60A TP 10kA Isolator","No",1]
[4,"60A DP 5kA E/L Units","No",6]
[5,"20A SP 5kA MCB`s","No",16]
[6,"15A SP&N 5kA MCB`s","No",2]
[]
[null,"ESSENTIAL SECTION"]
[7," Set of 4 x 60A Bus Bars Rated 10kA  ","m",1]
[8,"60A TP 10kA Isolator","No",1]
[9,"60A DP 5kA E/L Units","No",3]
[10,"20A SP 5kA MCB`s","No",6]
[11,"10A SP MCB`s","No",18]
[]
[null,"UPS SECTION  "]
[12,"Set of 4 x 60A Bus Bars Rated 15kA  ","Item"]
[13,"60A TP 15kA Isolator","No",1]
[14,"60A DP 5kA E/L Units","No",1]
[15,"20A SP 5kA MCB`s","No",2]
[16,"20A TP 5kA MCB","No",1]
{"$rows_empty":15}
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/21"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"New DB.GE"]
[]
[1,"Board Surface Mounted in Cupboard Space "]
[null,"equipped as per Line Diagram on Drawing "]
[null,"SL 231 -  ELD2.  Allow for fabrication","Item"]
[]
[null,"NON - ESSENTIAL SECTION"]
[2," Set of 4 x 60A Bus Bars Rated 10kA  ","m",1]
[3,"60A TP 10kA Isolator","No",1]
[4,"60A DP 5kA E/L Units","No",6]
[5,"20A SP 5kA MCB`s","No",16]
[6,"15A SP&N 5kA MCB`s","No",2]
[]
[null,"ESSENTIAL SECTION"]
[7," Set of 4 x 60A Bus Bars Rated 10kA  ","m",1]
[8,"60A TP 10kA Isolator","No",1]
[9,"60A DP 5kA E/L Units","No",3]
[10,"20A SP 5kA MCB`s","No",6]
[11,"10A SP MCB`s","No",8]
[]
[null,"UPS SECTION  "]
[12,"Set of 4 x 60A Bus Bars Rated 15kA  ","Item"]
[13,"60A TP 15kA Isolator","No",1]
[14,"60A DP 5kA E/L Units","No",1]
[15,"20A SP 5kA MCB`s","No",2]
[16,"20A TP 5kA MCB","No",1]
[]
[null,"New DB.GP"]
[17,"New Sub DB.GP Ground Floor Level Distribution"]
[null,"Board Surface Mounted in Cupboard Space "]
[null,"equipped as per Line Diagram on Drawing "]
[null,"SL 231 -  ELD2  Allow for fabrication","Item"]
[]
[null,"NON - ESSENTIAL SECTION"]
[18," Set of 4 x 60A Bus Bars Rated 10kA  ","m",1]
[19,"60A TP 10kA Isolator","No",1]
[20,"60A DP 5kA E/L Units","No",1]
[21,"20A SP 5kA MCB`s","No",3]
[]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/22"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"ESSENTIAL SECTION (Continued)"]
[1," Set of 4 x 60A Bus Bars Rated 10kA  ","m",1]
[2,"60A TP 10kA Isolator","No",1]
[3,"20A TP 5kA CB","No",4]
[4,"60A DP 5kA E/L Units","No",2]
[5,"20A SP 5kA MCB`s","No",4]
[6,"10A SP MCB`s","No",3]
[null,"EARTH POINT SECTION "]
[7,"Set of 4 x 60A Bus Bars Rated 15kA  ","Item"]
[8,"60A TP 15kA Isolator","No",1]
[9,"60A DP 5kA E/L Units","No",1]
[10,"20A SP 5kA MCB`s","No",3]
[11,"20A TP 5kA CB`s","No",1]
[]
[null,"New First Floor Level Distribution Boards"]
[null,"NEW DB.F"]
[12,"New DB.F New Main First Floor Level Distribution "]
[null,"Board. Surface Mounted in Cupboard Space "]
[null,"equipped as per Line Diagram on Drawing "]
[null,"SL 231 -  ELD3 Allow for Fabrication","Item"]
[null,"NON - ESSENTIAL SECTION"]
[13," 4 x 100A Bus Bars Rated 15kA  ","m",1]
[14,"16A TP 10kA Isolator","No",1]
[15,"25A TP 5kA MCB`s","No",5]
[16,"60A TP 5kA Isolator ","No",1]
[17,"60A DP 5kA E/L Units","No",1]
[18,"10A SP 5kA MCB`s","No",3]
[19,"15A SP&N 5kA MCB`s","No",5]
[null,"ESSENTIAL SECTION"]
[20,"4 x 100A Bus Bars Rated 15kA  ","m",1]
[21,"100A TP 15kA Isolator","No",1]
[22,"30A TP 5kA MCB`s","No",5]
[23,"25A TP 15kA MCB for supply to UPS PANEL ","No",1]
[24,"60A DP 5kA E/L Units","No",2]
[25,"20A SP 5kA MCB`s","No",4]
[26,"20A SP&N 5kA MCB","No",2]
[27,"10A SP MCB`s","No",9]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/23"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"UPS SECTION  "]
[1,"Set of 4 x 60A Bus Bars Rated 15kA  ","Item"]
[2,"60A TP 15kA Isolator","No",1]
[3,"60A DP 5kA E/L Unit","No",1]
[4,"20A SP 5kA MCB`s","No",3]
[]
[null,"NEW DB.FA"]
[5,"New Sub DB.FA First Floor Level Distribution"]
[null,"Board Surface Mounted in Cupboard Space "]
[null,"equipped as per Line Diagram on Drawing "]
[null,"PE 231 -  ELD3.   Allow for Fabrication","Item"]
[]
[null,"NON - ESSENTIAL SECTION"]
[6," Set of 4 x 100A Bus Bars Rated 15kA  ","m",1]
[7,"60A TP 15kA Isolator","No",1]
[8,"60A DP 5kA E/L Units","No",3]
[9,"20A SP 5kA MCB`s","No",11]
[]
[null,"ESSENTIAL SECTION"]
[10," Set of 4 x 60A Bus Bars Rated 10kA  ","m",1]
[11,"60A TP 10kA Isolator","No",1]
[12,"60A DP 5kA E/L Units","No",2]
[13,"20A SP 5kA MCB`s","No",4]
[14,"10A SP MCB`s","No",6]
[]
[null,"UPS SECTION  "]
[15,"Set of 4 x 60A Bus Bars Rated 15kA  ","Item"]
[16,"60A TP 15kA Isolator","No",1]
[17,"60A DP 5kA E/L Unit","No",1]
[18,"20A SP 5kA MCB`s","No",3]
{"$rows_empty":9}
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/24"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"New DB.FB"]
[]
[1,"New Sub DB.FB First Floor Level Distribution"]
[null,"Board Surface Mounted in Cupboard Space "]
[null,"equipped as per Line Diagram on Drawing "]
[null,"PE 231 -  ELD3    Allow for Fabrication ","Item"]
[null,"NON - ESSENTIAL SECTION"]
[2," Set of 4 x 100A Bus Bars Rated 15kA  ","m",1]
[3,"60A TP 15kA Isolator","No",1]
[4,"25A TP 10kA CB"," No",1]
[5,"50A TP 10kA CB"," No",1]
[6,"60A DP 5kA E/L Unit","No",1]
[7,"20A SP 5kA MCB`s","No",2]
[null,"ESSENTIAL SECTION"]
[8," Set of 4 x 60A Bus Bars Rated 15kA  ","m",1]
[9,"60A TP 15kA Isolator","No",1]
[10,"25A TP 5kA CB","No",1]
[11,"5A SP 5kA CB","No",1]
[12,"30A 3P Contactor","No",1]
[13,"10A SP&N 5kA CB`s","No",5]
[14,"60A DP 5kA E/L Units","No",2]
[15,"20A SP 5kA MCB`s","No",4]
[16,"10A SP MCB`s","No",3]
[]
[null,"UPS SECTION  "]
[17,"Set of 4 x 60A Bus Bars Rated 15kA  ","Item"]
[18,"60A TP 15kA Isolator","No",1]
[19,"60A DP 5kA E/L Unit","No",1]
[20,"20A SP 5kA MCB`s","No",3]
{"$rows_empty":10}
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/25"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"New DB.FC"]
[1,"New Sub DB.FC First Floor Level Distribution"]
[null,"Board Semi Flush Mounted in Brick Wall"]
[null,"equipped as per Line Diagram on Drawing "]
[null,"SL 231 -  ELD3  DB to be mounted on a 50mm"]
[null,"Stand-Off metal Architrave  Allow for Fabrication","Item"]
[null,"NON - ESSENTIAL SECTION"]
[2,"Set of 4 x 100A Bus Bars Rated 15kA  ","m",1]
[3,"60A TP 10kA Isolator","No",1]
[4,"60A DP 5kA E/L Units","No",1]
[5,"20A SP 5kA MCB","No",1]
[6,"25A TP 10kA MCB","No",1]
[null,"ESSENTIAL SECTION"]
[7,"Set of 4 x 60A Bus Bars Rated 15kA  ","m",1]
[8,"60A TP 15kA Isolator","No",1]
[9,"60A DP 5kA E/L Units","No",1]
[10,"10A SP 5kA MCB`s","No",3]
[11,"10A SP MCB`s","No",1]
[null,"New DB.FM "]
[12,"New Sub DB.FM, DB.CPFirst Floor Level DB`s"]
[null,"Board Semi Flush Mounted in Brick Wall"]
[null,"equipped as per Line Diagram on Drawing "]
[null,"SL 231 -  ELD3  DB to be mounted on a 50mm","Item"]
[null,"Stand-Off metal Architrave  Allow for Fabrication","Item"]
[null," ESSENTIAL SECTION"]
[13,"Set of 4 x 60A Bus Bars Rated 5kA  ","m",1]
[14,"60A TP 10kA Isolator","No",1]
[15,"60A DP 5kA E/L Units","No",2]
[16,"20A SP 5kA MCB","No",6]
[17,"10A SP 10kA MCB","No",4]
[18,"25A TP 10kA MCB","No",1]
[19,"New DB.CP  Including fabrication"]
[null," ESSENTIAL SECTION"]
[20,"Set of 4 x 60A Bus Bars Rated 5kA  ","m",1]
[21,"60A TP 10kA Isolator","No",1]
[22,"60A DP 5kA E/L Units","No",1]
[23,"20A SP 5kA MCB","No",2]
[24,"10A SP 5kA MCB","No",4]
[25,"25A TP 10kA MCB","No",1]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/26"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"New Sub DB.ACDB1"]
[]
[1,"New Sub DB.ACDB1 First Floor Level Plant Room"]
[null,"Board Surface Floor Standing "]
[null,"equipped as per Line Diagram on Drawing "]
[null,"SL 231 -  ELD3 New Floor Standing DB with "]
[null,"removable Front and Back Panels supported on "]
[".","80mm high Metal Architrave. Allow for fabrication ","Item"]
[]
[null,"NON - ESSENTIAL SECTION"]
[2," 4 x 600A Bus Bars plus Earth Rated 25kA  ","m",1]
[3,"600A TP 25kA Isolator","No",1]
[4,"0-600A Ammeters and 600/5A CT`s","No",3]
[5,"Voltmeter and 5A 7way  Selector Switch","No",1]
[6,"35A TP 15kA CB`s","No",3]
[7,"30A TP 15kA CB ","No",1]
[8,"25A TP 15kA CB`s","No",2]
[9,"15A TP 15kA CB`s ","No",6]
[10,"20A TP 5kA CB","No",1]
[11,"10A SP&N 5kA MCB`s","No",10]
[]
[null,"ESSENTIAL SECTION DB.ACDB1  (Continued)"]
[12," 4 x 150A Bus Bars plus Earth Rated 25kA  ","m",1]
[13,"150A TP 25kA Isolator","No",1]
[14,"0-150A Ammeters and 150/5A CT`s","No",3]
[15,"Voltmeter and 5A 7way  Selector Switch","No",1]
[16,"30A TP 15kA CB ","No",1]
[17,"25A TP 15kA CB`s","No",2]
[18,"20A TP 15kA CB","No",1]
[19,"15A TP 5kA CB`s ","No",10]
[]
[20,"New UPS DB   BRILLIANT BLUE COVER","Item"]
[]
[null,"SUPPLY SECTION ESSENTIAL and RETURN"]
[21," 4 x 60A Bus Bars plus Earth Rated 15kA  ","m",1]
[22,"60A TP 15kA Isolator","No",1]
[23,"20A TP 15kA MCB,s","No",6]
[24,"20A TP 15kA MCB,s","No",6]
[25,"10A SP 5kA MCB,s","No",4]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/27"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[null,"SUPPLY CABLES to DISTRIBUTION BOARDS"]
[null,"Refer Drawing SL 231 - MRD and as per spec."]
[null,"Supply and install Mains & Sub Mains "]
[null,"Essential, Non-Essential and UPS  Power Supply"]
[null,"Cables to be installed in cable pipes, via Sleeves"]
[null," vertical cable ducts, cable ladders, etc. as follows:"]
[]
[1,"185mm² 4-core PVC SWA PVC ECC Cable","m",48]
[]
[2,"150mm² 4-core PVC SWA PVC ECC Cable","m",620]
[]
[3,"120mm² 4-core PVC SWA PVC ECC Cable","m",324]
[]
[4,"95mm² 4-core PVC SWA PVC ECC Cable","m",312]
[]
[5,"70m² 4-core PVC SWA PVC ECC Cable","m",20]
[]
[6,"50mm² 4-core PVC SWA PVC ECC Cable","m",120]
[]
[7,"35mm² 4-core PVC SWA PVC ECC Cable","m   ",138]
[]
[8,"25mm² 4-core PVC SWA PVC ECC Cable","m",450]
[]
[9,"16mm² 4-core PVC SWA PVC ECC Cable","m",852]
[]
[10,"10mm² 4-core PVC SWA PVC ECC Cable","m",1368]
[]
[11,"6mm² 4-core PVC SWA PVC ECC Cable","m",1306]
[]
[12,"4mm² 4-core PVC SWA PVC ECC Cable","m",1047]
[]
[13,"2,5mm² 4-core PVC SWA PVC ECC Cable","m",664]
[]
[14,"2,5mm² 3-core PVC SWA PVC ECC Cable","m",40]
[]
[15,"2,5mm² 2-core PVC SWA PVC ECC Cable","m",660]
[]
[16,"4mm² 4-core PVC SWA PVC ECC Cable","m",200]
[null,"Signal Cable installed into Ground pipes as required"]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/28"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"CABLE TERMINATIONS on Distribution Boards"]
[null,"Supply and Install cable glands strip back"]
[null,"and gland off with shrouds over the glands"]
[null,"and final connections to terminals using"]
[null,"crimping lugs, cadmium plated bolts, nuts and"]
[null,"lock washers. (All PVC SWA PVC ECC cables)"]
[1,"185mm² 4-core ECC Cable terminations","No",4]
[]
[2,"150mm² 4-core ECC Cable terminations","No",4]
[]
[3,"95mm² 4-core ECC Cable terminations","No",4]
[]
[4,"50mm² 4-core ECC Cable terminations","No",2]
[]
[5,"35mm² 4-core ECC Cable terminations","No",4]
[]
[6,"25mm² 4-core ECC Cable terminations","No",4]
[]
[7,"16mm² 4-core ECC Cable terminations","No",16]
[]
[8,"10mm² 4-core ECC Cable terminations","No",24]
[]
[9,"6mm² 4-core ECC Cable terminations","No",20]
[]
[10,"4mm² 4-core ECC Cable terminations","No",16]
[]
[11,"2,5mm² 4-core ECC Cable terminations","No",10]
[]
[12,"2,5mm² 3-core ECC Cable terminations","No",4]
[]
[13,"2,5mm² 2-core ECC Cable terminations","No",22]
[]
[14,"4mm² 4-core ECC Cable Terminations","No",4]
[null,"(Lift Signals from Standby Set Control Panel)"]
[]
[15,"4mm² 2-core ECC Cable Terminations","No",4]
[null,"Signal Cables"]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/29"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[null,"RETICULATION"]
[]
[null,"CABLE JOINTS"]
[null,"Supply and install \"Scotchcast\" or other "]
[null,"approved cable joint kits for the following"]
[null,"size cables: (All PVC SWA PVC ECC Cables)"]
[]
[1,"185mm² 4-core ECC Cable Joints","No",4]
[]
[2,"150mm² 4-core ECC Cable Joints","No",6]
[]
[3,"95mm² 4-core ECC Cable Joints","No",4]
[]
[4,"70mm² 4-core ECC Cable Joints","No",4]
[]
[5,"50mm² 4-core ECC Cable Joints","No",2]
[]
[6,"35mm² 4-core ECC Cable Joints","No",2]
[]
[7,"25mm² 4-core ECC Cable Joints","No",6]
[]
[8,"16mm² 4-core ECC Cable Joints","No",14]
[]
[9,"10mm² 4-core ECC Cable Joints","No",22]
[]
[10,"6mm² 4-core ECC Cable Joints","No",20]
[]
[11,"4mm² 4-core ECC Cable Joints","No",20]
[]
[12,"2,5mm² 4-core ECC Cable Joints","No",14]
[]
[13,"2,5mm² 3-core ECC Cable Joints","No",4]
[]
[14,"2,5mm² 2-core ECC Cable Joints","No",14]
[]
[]
[]
[]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/30"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"EARTH CONDUCTORS"]
[null,"Supply and install Insulated Earth Conductors"]
[null,"to be extended to the EXISTING Main Low"]
[null,"Tension Switchboard Earth Bar as Main Earth"]
[null,"conductors, etc. (line taps and lugged "]
[null,"terminations measured below):"]
[1,"70mm² earth conductor","m",220]
[]
[2,"50mm² earth conductor","m",164]
[]
[3,"4mm² earth conductor","m",1160]
[]
[4,"2,5mm² earth conductor","m",{"v":13530,"d":"13,530"}]
[]
[null,"EARTH CONDUCTOR JOINTS"]
[null,"Supply and install suitably sized cadmium"]
[null,"plated brass line taps joining earth "]
[null,"conductors of sizes as follows:"]
[]
[5,"70mm² earth conductor joints","No",3]
[]
[6,"50mm² earth conductor joints","No",2]
[]
[7,"4mm² earth conductor joints","No",10]
[]
[null,"EARTH CONDUCTOR TERMINATIONS"]
[null,"Supply and install lugged terminations"]
[null,"including cadmium plated brass bolts,"]
[null,"washes and nuts for the following size"]
[null,"earth conductors:"]
[]
[8,"70mm² earth conductor termination","No",12]
[]
[9,"50mm² earth conductor termination","No",6]
[]
[10,"4mm² earth conductor termination","No",4]
[]
[]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/31"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"RETICULATION"]
[]
[null,"CABLE STRAPPING"]
[null,"Supply and install stainless steel strapping"]
[null,"including buckles for cables along cable"]
[null,"ladders for the following:"]
[]
[1,"150mm² 4-core cable strapping","No",30]
[]
[2,"95mm² 4-core cable strapping","No",22]
[]
[3,"50mm² 4-core cable strapping","No",22]
[]
[4,"35mm² 4-core cable strapping","No",16]
[]
[5,"16mm² 4-core cable strapping","No",72]
[]
[6,"10mm² 4-core cable strapping","No",32]
[]
[7,"6mm² 4-core and smaller cable strapping","No",220]
[]
[]
[null,"PLASTIC STRAPPING"]
[null,"Supply and install plastic strapping"]
[null,"Shurlock\" cable ties or other approved,"]
[null,"for minor cable runs consisting of Telephone,"]
[null,"Public Address, etc., "]
[8,"10mm or less in dia. at max 1000mm centres","No",120]
{"$rows_empty":12}
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/32"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"EXCAVATIONS (Provisional)"]
[null,"(to be re-measured)"]
[null,"General excavation work for cable trenches"]
[null,"along the routes pegged out after the "]
[null,"required co-ordination with other services."]
[]
[1,"Excavation not exceeding 600mm deep in"]
[null,"earth for cables including bedding, back-"]
[null,"filling and compaction.","m³",48]
[]
[2,"Extra Over for excavation in intermediate "]
[null,"materials","m³",12]
[]
[3,"Extra Over for excavation in hard rock","m³",2]
[]
[4,"Ditto in consolidated soil through floor"]
[null,"construction/paving/around buildings including"]
[null,"reinstating of concrete apron","m³",8]
[]
[5,"Imported bedding under and filling around"]
[null,"cables and below interlocking brickwork"]
[null,"comprising of fine sand layers compacted","m³",12]
[]
[6,"Allow for carting away surplus material","m³",6]
[]
[null,"CABLE SLEEVES"]
[null,"(Excavations measured elsewhere)"]
[null,"Supply and Install PVC cable sleeves as"]
[null,"sleeving systems below roadways as entry"]
[null,"sleeve systems to Distribution Boards, cables"]
[null,"in ground, and all other cable services as"]
[null,"required."]
[]
[7,"200mm diameter (uPVC)","m",260]
[]
[8,"110mm diameter (uPVC)","m",400]
[]
[9,"75mm diameter (uPVC)","m",80]
[]
[10,"50mm diameter (uPVC)","m",280]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/33"]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"LARGE RADIUS BENDS"]
[null,"Supply and Install 110 diameter (Long bends)"]
[null,"for entry pipes to Distribution Boards"]
[1,"200mm diameter (uPVC)","No",18]
[2,"110mm diameter (uPVC)","No",28]
[3,"75mm diameter (uPVC)","No",6]
[4,"50mm diameter (uPVC)","No",16]
[]
[null,"CABLE WARNING TAPE (Provisional)"]
[null,"(to be re-measured)"]
[5,"Supply and Install 200mm wide red/yellow"]
[null,"plastic warning tape","m",520]
[]
[null,"MANHOLES"]
[6,"Supply and Install manholes refer Drwg SL231-ESP1"]
[null,"Internal dimensions shall be 1200mm x"]
[null,"1200mm x 1200mm.  Excavate and cast"]
[null,"100mm thick concrete base and build"]
[null,"double skin brick work and cast steel "]
[null,"reinforced concrete roof slab over."]
[null,"Complete manhole to be sealed with USB"]
[null,"Green plastic membrane below base and"]
[null,"between brickwork. (Manhole covers below)","No",8]
[]
[null,"MANHOLE COVERS"]
[7,"Supply and install manhole covers"]
[null,"600 x 600mm x 124 kg type 9D Cast Iron double"]
[null,"seal manhole cover and frame","No",6]
[]
[null,"DRAW WIRES"]
[8,"Supply and Install 1,6mm² diameter galvanised"]
[null,"steel draw wires in cable pipes and conduits","m",8800]
[null,"CABLE LADDERS"]
[null,"Supply and Install cable ladders 2,5mm thick"]
[null,"galvanised perforated steel cable ladder"]
[null,"with 70/157mm high side sections, including"]
[null,"splicing plates as required."]
[9,"600mm wide","m",140]
[10,"300mm wide","m",200]
[11,"200mm wide","m",240]
[12,"100mm wide","m",72]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/34"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"CABLE LADDER \"T\" SECTIONS"]
[null,"Supply and Install cable ladder with 76mm"]
[null,"high sides by 2,5mm thick galvanised"]
[null,"Steel \"T\" section including support"]
[null,"and fixing to cable ladders."]
[]
[1,"600mm wide","No",2]
[2,"300mm wide","No",2]
[3,"200mm wide","No",2]
[4,"100mm wide","No",2]
[]
[null,"CABLE LADDER 90° BENDS"]
[null,"Supply and Install cable ladder with 76mm"]
[null,"high sides by 2,5mm thick galvanised"]
[null,"Steel 90° Bends including support and"]
[null,"fixing to cable ladders."]
[]
[5,"600mm wide","No",8]
[6,"300mm wide","No",4]
[7,"200mm wide","No",4]
[8,"100mm wide","No",2]
[]
[]
[null,"CABLE LADDER 45° BENDS"]
[null,"Supply and Install cable ladder with 76mm"]
[null,"high sides by 2,5mm thick galvanised"]
[null,"Steel 45° Bends including support and"]
[null,"fixing to cable ladders."]
[]
[9,"600mm wide","No",6]
[10,"300mm wide","No",4]
[11,"200mm wide","No",2]
[12,"100mm wide","No",2]
[]
[13,"Support Structure for Cable Ladders"]
[null,"Vertical Supports for Cable Ladders comprising of"]
[null,"OL1000 Olistruts 3000mm high on either side of"]
[null,"Cable Ladder Suppots O-Line OL1041","No",120]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/35"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"CABLE LADDER \"HORIZONTAL CROSS"]
[null,"OVER SECTIONS"]
[null,"Supply and Install cable ladder with 76mm"]
[null,"high sides by 2,5mm thick galvanised"]
[null,"steel horizontal cross over sections "]
[null,"including support and fixing to cable ladders."]
[]
[1,"310mm wide","No",2]
[]
[null,"CABLE LADDER SUPPORT UNISTRUTS"]
[null,"Supply and Install P1000 galvanised steel"]
[null,"Unistrut section above and below Cable"]
[null,"Ladder Runs at 800mm centres specified."]
[null,"including 2x400mm long 8mm diameter"]
[null,"galvanised steel rods"]
[]
[2,"2x620mm long lengths to support 600mm wide"]
[null,"cable ladder.","No",70]
[]
[3,"2x320mm long lengths to support 300mm wide"]
[null,"cable ladder.","No",100]
[]
[4,"2x220mm long lengths to support 200mm wide"]
[null,"cable ladder.","No",90]
[]
[5,"2x120mm long lengths to support 100mm wide"]
[null,"cable ladder.","No",30]
[]
[6,"UNISTRUT RUNS behind DB`s in cupboards"]
[null,"Supply and install Unistrut Spacer Supports"]
[null,"between walls and DISTRIBUTION BOARDS"]
[null,"consisting of P1000 galvanised steel Unistruts"]
[null,"2 x 4000mm long (Provisionally) horizontally "]
[null,"positioned 300mm from the bottom and 300mm "]
[null,"from the top of each DB including 8mm Diameter"]
[null,"Rawlbolts at 800mm centres"]
[null,"Noted that no DB`s are to be mounted directly onto"]
[null,"walls etc.","No",88]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/36"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"UNISTRUTS"]
[null,"Supply and Install galvanised steel"]
[null,"Unistrut runs with all accessories as required,"]
[null,"ie. Splicing plates, spring nuts for bolting,"]
[null,"right angle bends, etc, including galvanised "]
[null,"steel cover plates for Light Fitting installations,"]
[null,"Power Installations, Data Cabling Systems"]
[null,"and Fire Detection & Evacuation Systems "]
[null,"complete, as follows:"]
[]
[1,"P1000 Unistrut (Light Circuits, Power, Fire"]
[null,"Detection & Evacuation, PA Systems etc.)","m",458]
[]
[2,"P2000 Unistrut (Light Circuits, Power, Fire"]
[null,"Detection & Evacuation, PA Systems etc.)","m",600]
[]
[3,"P8000 Unistrut (Fire Detection & Evacuation"]
[null,"Cabling and Lighting Circuits on all Levels","m",80]
[]
[4,"CONDUIT CONNECTIONS ONTO P2000"]
[null,"UNISTRUTS"]
[null,"Supply and install conduit connections "]
[null,"onto P2000 Unistruts, including drilled"]
[null,"openings and conduit terminations, complete"]
[null,"with locknuts and brass bushes.","No",1620]
[]
[5,"5 AMP 3-PIN SOCKET OUTLETS"]
[null,"Supply and Install 5 Amp rated 3-pin  "]
[null,"unswitched socket outlets installed in 75mm"]
[null,"diameter round conduit draw boxes for"]
[null,"supply to light fittings in false ceilings.","No",610]
{"$rows_empty":8}
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/37"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"CONDUIT WORK"]
[]
[null,"PVC CONDUIT"]
[]
[null,"Supply and Install SANS approved plain ended"]
[null,"PVC conduits complete with all required"]
[null,"conduit accessories.  Conduits to be cast into"]
[null,"concrete, built into brick walls, fixed on"]
[null,"surface of brick, concrete or steel surfaces"]
[null,"or fixed inside ceiling spaces below steel"]
[null,"trusses.  All tendered rates must make"]
[null,"allowance for wastage."]
[]
[null,"Cast into Concrete"]
[1,"20mm diameter","m",6]
[2,"25mm diameter","m",12]
[3,"50mm diameter","m",26]
[]
[null,"Built or Chased into Brickwork"]
[4,"20mm diameter","m",6]
[5,"25mm diameter","m",24]
[6,"50mm diameter","m",32]
[]
[null,"In Ceiling Space"]
[7,"20mm diameter","m",12]
[8,"25mm diameter","m",8]
[9,"50mm diameter","m",8]
[null,"Supply and Install SANS approved plain ended"]
{"$rows_empty":11}
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/38"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"GALVANISED CONDUIT"]
[]
[null,"Supply and Install"]
[null,"Galvanised Steel conduits complete with all"]
[null,"required conduit accessories.  Conduits to be"]
[null,"cast into concrete, built into brick walls,"]
[null,"fixed on surface of brick, concrete or steel"]
[null,"surfaces or fixed inside ceiling spaces below"]
[null,"steel trusses.  All tendered rates must make"]
[null,"allowance for wastage."]
[]
[null,"Cast into Concrete"]
[1,"20mm diameter","m",7260]
[2,"25mm diameter","m",284]
[3,"32mm diameter","m",6]
[4,"50mm diameter","m",6]
[null,"Built or Chased into Brickwork"]
[5,"20mm diameter","m",4056]
[6,"25mm diameter","m",162]
[7,"32mm diameter","m",12]
[8,"50mm diameter","m",6]
[null,"In Ceiling spaces, installed Surface, etc "]
[9,"20mm diameter","m",4454]
[10,"25mm diameter","m",136]
[11,"32mm diameter","m",6]
[12,"50mm diameter","m",6]
[null,"Installed surface against wall /"]
[null,"equipment, etc."]
[13,"20mm diameter","m",142]
[14,"25mm diameter","m",116]
[15,"32mm diameter","m",22]
[]
[null,"CONDUIT CONNECTIONS"]
[null,"Connections for large conduits consisting of"]
[null,"galvanised steel socket and male terminating"]
[null,"adaptor onto opening in distribution board"]
[null,"and/or Cast Resin type draw box,etc."]
[]
[16,"32mm diameter","No",6]
[17,"50mm diameter","No",4]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/39"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"FLEXIBLE, PVC COVERED TYPE CONDUIT"]
[null,"Supply and Install conduit work in 1m lengths"]
[null,"complete with termination ends, (both ends)"]
[null,"fixed on surface of timber work in ceiling"]
[null,"space, as connections to appliances and"]
[null,"Panels. "]
[]
[1,"20mm diameter","No",2]
[]
[null,"CONDUIT BOXES"]
[null,"Supply and Install SANS approved 75mm"]
[null,"diameter galvanised steel conduit boxes,"]
[null,"installed in the run of the conduit installations,"]
[null,"cast into concrete and built into brickwork"]
[null,"or flush inside false ceiling spaces, complete"]
[null,"with all required conduit termination "]
[null,"accessories."]
[]
[null,"Shallow type Conduit back entry boxes"]
[2,"20mm 1-way type","No",1280]
[3,"20mm 2-way type","No",244]
[4,"20mm 3-way type","No",122]
[5,"20mm 4-way type","No",106]
[]
[6,"25mm 1-way type","No",6]
[7,"25mm 2-way type","No",10]
[8,"25mm 3-way type","No",4]
[9,"25mm 4-way type","No",6]
[]
[10,"32mm 1-way type","No",6]
[11,"32mm 2-way type","No",4]
[12,"32mm 3-way type","No",6]
[13,"32mm 4-way type","No",2]
[]
[]
[]
[]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/40"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"WALL BOXES (Galvanised Steel)"]
[null,"Supply and Install SANS approved galvanised"]
[null,"pressed steel boxes installed into ceiling voids"]
[null,"for building flush into brickwork or cast into"]
[null,"concrete work."]
[null,"Flush mounted type"]
[1,"100 x 50 x 50mm","No",493]
[2,"100 x 100 x 50mm","No",679]
[3,"100 x 100 x 100mm (extra deep)","No",4]
[4,"200 x 100 x 100mm (with cover plate)","No",8]
[5,"200 x 200 x 100mm (with cover plate)","No",8]
[6,"600 x 400 x 100mm (with cover plate)","No",2]
[7,"600 x 400 x 200mm (with cover plate)","No",4]
[]
[null,"Surface mounted type"]
[8,"100 x 100 x 50mm (with cover plate)","No",14]
[9,"300 x 300 x 100mm (with cover plate)","No",3]
[]
[null,"WALL BOXES (Cast Resin)"]
[null,"Supply and Install \"Cast Resin\" Wall boxes"]
[null,"with vertical slide lid or fixed lid surface and/"]
[null,"or built/chased into brickwork"]
[]
[null,"Slide Lid Type"]
[10,"J2 - 200 x 145 x 80mm","No",4]
[11,"J3 - 115 x 110 x 92mm","No",2]
[12,"J4 - 200 x 200 x 100mm  (Lightning Protection )","No",18]
[13,"U5 - 400 x 300 x 100mm","No",2]
[]
[null,"With Doors and Latches (Main Draw boxes)"]
[14,"600mm high x 300mm wide x 200mm Deep","No ",4]
[]
[null,"BLANK COVER PLATES"]
[null,"Supply and Install over standard wall boxes"]
[null,"white plastic cover plates suitable for"]
[15,"100 x 100mm flush drawboxes","No",16]
[16,"100 x 50mm flush drawboxes","No",20]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/41"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"EXPANSION JOINTS"]
[1,"Supply and Install Expansion drawboxes"]
[null,"for mains and multi conduit runs"]
[null,"(2-4 conduits each)","No",2]
[]
[2,"Conduit sleeve joints for isolated conduit runs","No",8]
[]
[null,"PVC WIRING"]
[null,"Supply and Install SANS approved PVC"]
[null,"insulated stranded copper conductors "]
[null,"installed in conduit runs, unistrut runs, or as"]
[null,"indicated in the detail specification.  The"]
[null,"tendered rates shall make provision for"]
[null,"normal wastage."]
[]
[3,"1,5mm²","m",218]
[4,"2,5mm²","m",32134]
[5,"4,0mm²","m",188]
[]
[null,"FLEXIBLE CONDUCTORS"]
[null,"Supply and Install flexible Cabtyre cable"]
[null,"connections of 800mm lengths, connected"]
[null,"to single and three phase equipment specified"]
[null,"including terminations each end with suitably"]
[null,"sized PVC compression glands."]
[]
[6,"2,5mm² 2-core","No",4]
[7,"4mm² 3-core","No",2]
[8,"2,5mm² 3-core (Lights)","No",5]
[]
[null,"DRAW WIRES for CONDUIT RUNS"]
[]
[9,"Supply and Install 1,6mm diameter galvanised"]
[null,"steel draw wires in conduit runs","m",11370]
[]
[]
[]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/42"]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"STRANDED PVC INSULATED COPPER"]
[null,"EARTH CONDUCTOR"]
[null,"Supply and Install stranded PVC insulated"]
[null,"copper earth conductor along with PVC "]
[null,"conductors in conduits as indicated in the detail"]
[null,"specification.  Tendered rates shall make"]
[null,"provision for wastage."]
[1,"1,5mm²","m",102]
[2,"2,5mm²","m",14260]
[3,"4,0mm²","m",12]
[4,"6,0mm²","m",62]
[5,"10mm²","m",58]
[6,"LIGHT SWITCHES, ETC."]
[null,"Supply and Install SANS approved type 16A"]
[null,"flush and surface type light switches with \"white\""]
[null,"coverplates. Switch modules shall be colour coded"]
[null,"ie. \"white\" for Non-Essential, \"Red\" Essential"]
[null,"and \"Medium Blue\" for UPS. All boxes for flush "]
[null,"mounting measured elsewhere. Surface type shall "]
[null,"be durable white plastic enclosures.  Switches"]
[null,"shall be \"Crabtree\" or other approved, complete "]
[null,"with coverplates as specified and Chromed fixing"]
[null,"screws. All coverplates to be provided with "]
[null,"engraved information as specified with emergency"]
[null,"colour code, ie. \"black\" for Non-Essential, \"red\""]
[null,"for Essential & \"Medium Blue\" for UPS Power","Item"]
[7,"1 Lever 1-way fitted with RED module Switches","No",231]
[null," and White Coverplates"]
[8,"1 Lever 1-way fitted with Black Coverplates and","No",28]
[null,"RED module Switches"]
[9,"1 Lever 2-way fitted with White Coverplates and","No",101]
[null,"RED module Switches"]
[10,"1 Lever 1-Way DP Light Switch for Light/Extract "]
[null,"Fans circuits (Red module Switches)","No",6]
[11,"1 Lever 1-Way Watertight module","No",4]
[12,"1 Lever 1-way electronic type Dimmer "]
[null,"(Seminar Room, Nurses Station,etc)","No",10]
[13,"1 Lever 1-way Mullion Switch"]
[null,"(with White slim line Modules Switches)","No",2]
[14,"1 Lever 1-way Mullion Switch"]
[null,"(with Red slimline Module switches)","No",2]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/43"]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"SOCKET OUTLETS"]
[1,"Supply and Install SANS approved switched"]
[null,"and un-switched type flush mounted type"]
[null,"16A switched socket outlets suitable for"]
[null,"mounting in flush steel wall boxes."]
[null,"Socket outlets shall be \"Crabtree\" or other"]
[null,"approved, colour coded \"white\" for Non-"]
[null,"Essential, \"red\" for Essential and \"Medium"]
[null,"Blue\" for UPS,  complete with \"White\" plastic"]
[null,"coverplates as specified and chromed"]
[null,"fixing screws  Including EURO type Switch socket "]
[null,"outlets, in Flush wall mounted Draw Boxes or/and"]
[null,"Power Skirting Runs all as specified"]
[null,"All coverplates to be provided with engraved"]
[null,"information as specified with emergency"]
[null,"colour code, ie. \"black\" for Non-Essential,"]
[null,"\"Red\" for Essential & \"Medium Blue\" for UPS "]
[null,"Power Circuits","Item"]
[]
[null,"Type P1 Flush switched socket "]
[2,"Single 16A 3-pin \"white\" switch socket "]
[null,"outlets with \"white\" switch module"]
[null,"(Non-Essential Power circuits)","No",98]
[]
[null,"Type P2 Flush switched socket on PS"]
[3,"Single 16A 3-pin \"white\" switch socket outlets "]
[null,"with \"red\" switch module (Essential Power )","No",92]
[]
[null,"Type P3 Double switch socket "]
[4,"Double 16A 3-pin switch socket outlets with "]
[null,"\"Red\" Switch Modules (Essential Power)","No",3]
[]
[null,"Type P4 Combination switch sockets "]
[5,"Combination 16A 3-pin \"white\" switch socket "]
[null,"and EURO Type \"white\" switch module "]
[null,"(Non Essential Power )","No",269]
[6,"Exactly as above ECEPT. Only on POW.  SKIRTs ","N0",211]
[null,"Type P5 Surface switched socket "]
[7,"Single 16A 3-pin socket outlets with \"Red\""]
[null,"switch module in Surface mounted \"York\" S15"]
[null,"type weatherproof enclosure (Essential Power)","No",6]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/44"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"Combination switch sockets Type P6"]
[1,"Combination 16A 3-pin \"white\" switch socket "]
[null,"and EURO Type \"white\" switch module in"]
[null,"Tamper Proof Enclosure fitted with Tamper proof "]
[null,"locking screws"]
[null,"(Non Essential Power )","No",34]
[]
[null,"Floor Mounted \"Cottage Enclosure\" Type P7"]
[2,"Single 16 A 3-pin \"white\"switch socket outlet"]
[null,"and TEL / DATA outlet Point. "]
[null,"(Non Essential Power)","No",4]
[]
[null,"Type P8 Flush switched sockets"]
[3,"Single 16A 3-pin \"White\" switch socket "]
[null,"outlets with \"Medium Blue\" switch module"]
[null,"(UPS Power circuits)","No",28]
[]
[null,"Type P9 Power Skirting switched sockets "]
[4,"Single 16A 3-pin \"white\" switch socket outlets "]
[null,"with \"Medium Blue\" switch module ","No",14]
[null,"(UPS Power circuits )"]
[]
[null,"60 AMP TP&N COMBINATION ISOLATOR/"]
[null,"SOCKET OUTLETS"]
[5,"Allow to supply and install a 60 Amp Triple"]
[null,"Pole and Neutral Isolator and Socket"]
[null,"outlet combination unit complete with"]
[null,"plug top.  The isolator to be mechanically"]
[null,"interlocked so that the isolator can only"]
[null,"be switched on when the plug top has"]
[null,"been properly inserted. For Switch Room and Plant"]
[null,"Rooms. To be used for routine maintenance","No",4]
[]
[null,"5 Amp Socket Outlet modules "]
[6,"To be installed onto Unistruts/Walls/Ceilings etc"]
[null,"as required for Light Fittings all as indicated on "]
[null,"the layout drawings. For all 5Amp Plug Top "]
[null,"and Flexible cord supplies ","No ",591]
[]
[]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/45"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"ON-LOAD ISOLATING SWITCHES"]
[1,"Supply and Install SANS approved on-load"]
[null,"isolating switches suitable for mounting "]
[null,"inside flush or surface mounted type steel"]
[null,"wall boxes complete with cover plates."]
[null,"The colour finishes to the boxes to be equal to that"]
[null,"of the light switches and switched socket outlets."]
[null,"All coverplates are to be provided with"]
[null,"suitable labels.  Labels for galvanised steel"]
[null,"shall be engraved ivorine, plastic coverplates"]
[null,"and shall be engraved - colour coded as"]
[null,"specified - refer Socket and Light Switches","Item"]
[]
[2,"20 Amp Double Pole Isolator complete with"]
[null,"an indicating light module installed into a"]
[null,"100x50x50mm flush draw box for isolating"]
[null,"of hand dryer and fan circuits complete with "]
[null,"white\" coverplates.","No",42]
[]
[3,"30A Triple Pole Isolator installed surface "]
[null,"in Enclosure for supply to appliances"]
[null,"as indicated on the Layout Drawings","No",9]
[]
[4,"50A Double Pole Isolator complete with an"]
[null,"indicating light module installed into a 100 x"]
[null,"100 x 40mm surface extension drawbox"]
[null,"for isolating of Security panel Supply, Nurse Call"]
[null,"Supply Panel, and Fire Panels","No",6]
[]
[5,"60A Triple Pole Isolator installed into a flush"]
[null,"mounted \"Cast Resin\" draw box for supply"]
[null,"to 3-phase Bed Pan Washer."]
[null,"(Draw box measured elsewhere)","No",1]
[]
[]
[]
[]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/46"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"CABLES FOR SUB MAINS SUPPLIES to"]
[null,"AIR HANDLING AC CONTROL PANELS "]
[null,"Supply and install cables for Air Conditioning"]
[null,"Control Panels of sizes and lengths as follows:"]
[]
[1,"16mm² 4-core PVC SWA PVC ECC","m",28]
[2,"10mm² 4-core PVC SWA PVC ECC","m",68]
[3,"6mm² 4-core PVC SWA PVC ECC","m",76]
[4,"4mm² 4-core PVC SWA PVC ECC","m",250]
[5,"2,5mm² 4-core PVC SWA PVC ECC","m",762]
[]
[null,"Terminations for the above"]
[]
[6,"16mm² 4-core PVC SWA PVC ECC","No",4]
[7,"10mm² 4-core PVC SWA PVC ECC","No",8]
[8,"6mm² 4-core PVC SWA PVC ECC","No",6]
[9,"4mm² 4-core PVC SWA PVC ECC","No",18]
[10,"2,5mm² 4-core PVC SWA PVC ECC","No",36]
[]
[null,"FLEXIBLE CONDUCTORS"]
[11,"Supply and Install 2,5mm² 3-core flexible"]
[null,"Cabtyre cable connections of 500mm"]
[null,"length terminated with compression glands "]
[null,"on either end and connected to fittings/"]
[null,"appliances as required.","No",4]
[]
[12,"CABLES FOR POLE LIGHTS"]
[null,"Supply and Install Cabling in Conduits, in cable "]
[null,"pipes and ground for Pole Lights as follows"]
[null,"2,5mm² 4-core PVC SWA PVC ECC cable"]
[null,"(3-Phase, neutral and earth)","m",44]
[]
[13,"TERMINATIONS (Pole Lights)"]
[null,"Supply and Install Cable glands for 2,5mm²"]
[null,"2-core PVC SWA PVC ECC Cable strip back"]
[null,"and gland off with waterproof shrouds"]
[null,"over glands onto Switchgear in pole light "]
[null,"access openings and final connections"]
[null,"to terminals (See specification)","No",5]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/47"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[1,"POWER SKIRTING RUNS"]
[null,"Supply and install power skirting runs,"]
[null,"consisting of 2-channel 3-compartment "]
[null,"section, against the walls/ partitions complete"]
[null,"with all accessories, (eg. joiner pieces, right"]
[null,"angle bends, fish plates, in and outside bends,"]
[null,"end plates, etc.)","m",438]
[]
[null,"Switch Socket modules"]
[2,"Non Essential standard modules "]
[null,"16 Amp 3-pin Non-Essential power switch"]
[null,"socket outlets (with \"white\" switch modules)","No",7]
[]
[3,"Combination Non Essential standard plus Euro "]
[null,"type 16Amp 3-pin outlet plus Euro outlet switch "]
[null,"socket outlets ( both with \"white switch modules)","No",9]
[]
[4,"Essential Standard Modules"]
[null,"16 Amp 2-pin Essential power switch"]
[null,"socket outlets (with \"red\" switch modules)","No",16]
[]
[null,"Telephone Outlets"]
[5,"On Powerskirting Runs","No",29]
[6,"On Walls","No",32]
[]
[null,"Data/Computer Outlets"]
[7,"On Powerskirting Runs","No",20]
[8,"On Walls","No",25]
[null,"Note: Telephone and Computer modules to be"]
[null,"installed on Walls and Power Skirting runs have "]
[null,"have been allowed for in theT telephone Installation "]
[null,"and Computor Installion sections of these B of Q's"]
{"$rows_empty":8}
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/48"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"LIGHT FITTINGS (LF)"]
[null,"Supply, delivery to site, storage and installation"]
[null,"of the below specified light fittings complete "]
[null,"with drivers and lamps .  Allowance must be made"]
[null,"in the rates for all the required fixing materials "]
[null,"and accessories. Fittings to be as per Type & "]
[null,"Detail specified."]
[null,"To be Noted: Samples of all Light Fittings(LF) shall "]
[null,"be provided for approval prior to procurement, one "]
[null,"of each approved LF shall be handed over to the"]
[null,"Electrical Engineer as a sample, no deviations"]
[null,"after approval will be entertained, the fittings shall "]
[null,"be returned timeously before the completion of the "]
[null,"contract"]
[]
[1,"Type A "]
[null,"15W LED Surface mounted round slimeline "]
[null,"Bulkhead type Light Fitting"]
[null,"Rated IP66 with polycarbonate base and diffuser,"]
[null,"vandal proof, Colour white, Enlite Cat No "]
[null,"EN-BH15/40, or equal and approved.","No",30]
[]
[2,"Type B "]
[null,"25W LED Surface mounted Utility Oval"]
[null,"Polycarbonate Bulkhead type Light Fitting"]
[null,"Rated IP66 Enlite Cat No EN-BH220/40, or equal "]
[null,"and approved","No",22]
[]
[3,"Type BH "]
[null,"30W LED Surface wall mounted Utility type "]
[null,"Light Fitting, Rated IP 65, with cast aluminium "]
[null,"Base and Polycarbonate diffuser, Enlite Cat No"]
[null,"EN-WP102/40,or equal and approved","No",27]
[]
[4,"Type C "]
[null,"30W LED Surface mounted Floodlight type "]
[null,"Light Fitting, Adjustable, Rated IP65"]
[null,"Enlite Cat No ENFL30B/40 or equal and approved","No",26]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/49"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[1,"Type CO "]
[null,"25W LED Surface mounted Utility Round "]
[null,"Polycarbonate Bulkhead Light Fitting"]
[null,"Rated IP 65 Enlite Cat. No.EN-BH35/40  or equal "]
[null,"and approved, mounted onto a YORK Type Raised"]
[null,"RL45/P 350x250x120mm, comprising a Reinforced"]
[null,"Poleyester Enclosure. Refer detail on drawing"]
[null,"SL 231 - EL3, or equal and approved","No",74]
[]
[2,"Type C1 4W Recessed Downlight (Body White"]
[null,"Cast Aluminium) type Light Fitting, cast into "]
[null,"concrete slab 140mm square by 125mm high IP65"]
[null,"Rated Slab Box,Swanlight SLS-ACC-/AO - Budbox/"]
[null,"GRP or equal and approved.","No",12]
[]
[3,"Type D "]
[null,"13W LED GIZA EYELID Surface mounted"]
[null,"Bulkhead Light Fitting, Rated IP65, LMG die cast"]
[null,"aluminium housing , with UV stabilized opal acrylic  "]
[null,"acrylic Diffuser, Black Powder Coated, with "]
[null,"Tamper proof stainless steel screws."]
[null,"Regent Cat No. ZHAGA BOARDS, or equal and "]
[null,"approved","No",32]
[]
[4,"Type D1 "]
[null,"10W LED Dimmable Recessed round "]
[null,"Downlighter type Light Fitting, Rated IP44"]
[null,"with integrated Driver, colour White, Enlite Cat No  "]
[null,"EN-DDL   10/40,, or equal and approved.","No",37]
[]
[5,"Type D2 "]
[null,"15W LED Dimmable Surface mounted round "]
[null,"Downlighter type Light Fitting, Rated IP54"]
[null,"with integrated Driver, colour White, Enlite Cat No  "]
[null,"EN-DLSMR15T/40, or equal and approved.","No",8]
[]
[]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/50"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[1,"Type DS"]
[null,"Daylight switches comprising NATIONAL Type"]
[null,"mounted in a Surface Rated  IP 66 Enclosure"]
[null,"Typical to SPAZIO Split type Light Fitting IP54"]
[null,"Coastal quality (without LED Lamps etc. )"]
[null,"or equal and Approved","No",3]
[]
[2,"Type E "]
[null,"7W LED Wall mounted 3Hours maintained "]
[null,"aluminium Emergency EXIT Light Fitting, "]
[null,"Emergency aluminium type Light Fitting, Enlite "]
[null,"Cat No EN-EMLED22 in White frame including "]
[null,"Legend in Green and White EN - LG2D,  "]
[null,"or equal and Approved.","No",11]
[]
[3,"Type EC"]
[null,"14W LED ECLIPSE wall mounted Bulkhead"]
[null,"Light Fitting, Rated IP54, LM 6  die cast and "]
[null,"extruded aluminium housing , with UV stabilized "]
[null,"satine acrylic Diffuser, Black Powder coated"]
[null,"Finnish with tamper Proof stainless steel screws "]
[null,"Regent Cat No. Samsung 2835, or equal and"]
[null," and approved.","No",12]
[]
[4,"Type G"]
[null,"18W LED GIZA  wall mounted Bulkhead"]
[null,"Light Fitting, Rated IP65, LM 6  die cast and "]
[null,"extruded aluminium housing , with UV stabilized "]
[null,"high impact Opal acrylic Diffuser, Black Powder "]
[null,"coated Finnish with tamper Proof stainless steel"]
[null,"screws, Regent Cat No. Samsung 2835, or equal"]
[null," and approved.","No",12]
{"$rows_empty":7}
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/51"]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[1,"Type H"]
[null,"18W LED GIZA  PLATEAU wall mounted"]
[null," Bulkhead Light Fitting, Rated IP65,"]
[null," LM 6  die cast and "]
[null,"extruded aluminium housing , with UV stabilized "]
[null,"high impact Opal acrylic Diffuser, Black Powder "]
[null,"coated Finnish with tamper Proof stainless steel"]
[null,"screws, Regent Cat No. Samsung 2835, or equal"]
[null," and approved.","No",4]
[]
[2,"Type TB"]
[null,"25W Surface Bulkhead Light Fitting, Rated IP 65"]
[null,"with Polycarbonate Body and diffuser, white in"]
[null,"colour, Maximum vandal Resistant fitted with Allen"]
[null,"type stainless steel screws, Enlite Cat No EN-BH25  "]
[null,"or equal and approved.","No",122]
[]
[3,"Type WD"]
[null,"3W LED Dichroic White Recessed Downlight"]
[null,"Type Light Fitting in cast into slab 140mm"]
[null,"square by 125mm IP55 Slab Box fitted with "]
[null,"cover secured with 4 x Allen Key screws"]
[null," or equal  and approved.","No",34]
[]
[4,"Type FT"]
[null,"1,12W LED Recessed Foot Light Fitting, "]
[null,"Rated IP 54, Coastal Quality Stainless Steel Frame "]
[null,"and Perspex Diffuser, Spazio cat No 4474/3038,"]
[null,"or equal and approved","No",21]
[]
[5,"Type I/L"]
[null,"1W LED Indicating Light Fitting, Enlite Cat No "]
[null,"EN-W4104 marker light, mounted into an "]
[null,"extra deep galvanised  steel conduit box  "]
[null,"Fitted with a Red Lens, complete with a350mA Driver Driver installed into a surface enclosure with "]
[null,"ventilation slots to allow free air flow or equal"]
[null,"and approved ","No",20]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/52"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[1,"Type ENT"]
[null,"2x5W LED Wall Mounted Up and Down Light"]
[null,"Fitting, Rated IP44, with Stainless Steel Body,"]
[null,"Spacio Cat No. Paulie DY/5024/39 or equal and "]
[null,"approved","No",26]
[]
[2,"Type RA"]
[null,"15W LED Recessed  CEILING Mounted "]
[null,"Adjustable Downlight Light Fitting, Rated IP44, "]
[null,"with Driver, Spacio Cat No 2479.01 or equal "]
[null,"and approved","No",30]
[]
[3,"Type SH "]
[null,"2 x 17W LED SHUTTLE Wall mounted UP and"]
[null,"DOWN Light Fitting , Rated IP 65, LM6 die cast  "]
[null,"aluminium and extruded aluminium housing , with"]
[null,"4mm Opal glass diffuser, with High Efficiency "]
[null,"realtor , Black powder coated, Regent Cat No "]
[null,"COB CRI 80,or equal and approved.","No",17]
[]
[4,"Type PROC"]
[null,"14W LED Ceiling Mounted Medical Procedure "]
[null,"Light fitting, Hutz Medical Product Code L200 :"]
[null,"Solaris 11 LED 2000, Luminance Output 50,000Lux"]
[null,"at 1000mm, or equal and approved","No",1]
[]
[5,"Type EXAM"]
[null,"12W LED Wall mounted Medical Examination "]
[null,"Light Fitting, Rated IP54, Colour White, Hutz "]
[null,"Medical Product Name: HUGO LED-W, supplied"]
[null,"with 1500mm flexible cable fitted with standard"]
[null,"SANS 3-pin Plug Top, or equal and approved.  "]
[null,"To be mounted against the wall by means of a "]
[null,"Flat 120 x 100 x 10mm stainless steel  mounting "]
[null,"plate fitted to walls by means of 4x6mm diam. "]
[null,"Rawlbolts. The base of the Examination Light "]
[null,"to be secured to the plate in accordance with the "]
[null,"manufacturers fixing specifications, all or equal and"]
[null,"approved ","No",28]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/53"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[1,"Type F1 "]
[null,"50W LED Recessed Light Fitting, 1200x600mm"]
[null,"(5425lm) High Output, installed into a "]
[null,"Fabricated 3CR12 metal Enclosure. Refer Spec."]
[null,"and Detail on Drawing SL 230 - EL5"]
[null,"or Equal and Approved","No",45]
[]
[2,"Type F2 "]
[null,"54W LED 1500mm long Surface type Light"]
[null,"Fitting, Rated IP65 Anti-Corrosion, Vandal Proof,  "]
[", ","Polycarbonate housing and Opal diffuser, "]
[null,"Enlite Cat No. EN-ANTE554/40, or Equal and "]
[null,"Approved","No",134]
[]
[3,"Type F3 "]
[null,"50W LED 1200x600mm Recessed Flat Panel "]
[null,"type Light Fitting, Non-Dimmable, complete with"]
[null,"condensate sealant, Enlite L70 50,000Hours"]
[null,"Cat No. EN-FPRO1260/40, or Equal and Approved,"]
[null," including Flat Panel Cat No EN-CRM1260A","No",2]
[]
[4,"Type F4 "]
[null,"50W LED 1200x600mm Surface Flat Panel type "]
[null,"Light Fitting, Non-Dimmable, Enlite L70 50,000 "]
[null,"Hours Cat No. EN-FPRO1260/40, or Equal and "]
[null,"Approved, including Flat Panel for Surface"]
[null,"mounting Cat No EN-SM106B","No",14]
[]
[5,"Type F5 "]
[null,"50W LED 1200x600mm Recessed Flat Panel "]
[null,"type Light Fitting, Non-Dimmable, Enlite L70 "]
[null,"50,000Hours Cat No. EN-FPRO1260/40, or Equal"]
[null," and Approved, including Flat Panel Cat No "]
[null,"EN-CRM1260A,complete with 5 Amp 3-pin Plug "]
[null,"Top and Flexible Cabtyre Cable","No",591]
[]
[]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/54"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[1,"Type F6 "]
[null,"50W LED 1200x600mm Surface Flat Panel type "]
[null,"Light Fitting, Non-Dimmable, Enlite L70 50,000 "]
[null,"Hours Cat No. EN-FPRO1260/40, or Equal and "]
[null,"Approved, including Flat Panel for Surface "]
[null,"mounting Cat No EN-SM106B with sealant applied"]
[null," to perimeter of fitting","No",56]
[]
[2,"Type F7 "]
[null,"50W LED 1200x600mm Recessed Flat Panel "]
[null,"type Light Fitting, Non-Dimmable, Enlite L70 "]
[null,"50,000Hours Cat No. EN-FPRO1260/40, or Equal "]
[null,"and Approved, including Flat Panel Cat No "]
[null,"EN-CRM1260A,Fitted with 3hour battery "]
[null,"emergency pack, complete with 5 Amp 3-pin "]
[null,"Plug Top and Flexible Cabtyre Cable","No",3]
[]
[3,"Type F8 "]
[null,"50W LED 1200x600mm Surface Flat Panel type "]
[null,"Light Fitting, Enlite L70 50,000 Hours Cat No. "]
[null,"EN-FPRO1260/40EM, or Equal and Approved, "]
[null,"including Flat Panel for Surface mounting "]
[null,"Cat No EN-SM106B, Fitted with 3hour battery "]
[null,"emergency battery pack","No",14]
[]
[4,"Type F9 "]
[null,"30W LED 1200x600mm Recessed Flat Panel "]
[null,"type Light Fitting, Non-Dimmable, Enlite L70 "]
[null,"50,000Hours Cat No. EN-FPRO6060/40, or Equal "]
[null,"and Approved, including Flat Panel Cat No"]
[null," EN-CRM6060A, complete with 5 Amp 3-pin Plug "]
[null,"Top and Flexible Cabtyre Cable","No",22]
[]
[5,"Type F10 "]
[null,"30W LED 600x600mm Surface Flat Panel type "]
[null,"Light Fitting, Non-Dimmable, Enlite L70 50,000 "]
[null,"Hours Cat No. EN-FPRO6060/40, or Equal and"]
[null," Approved, including Flat Panel for Surface"]
[null," mounting Cat No EN-SM103B","No",12]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/55"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[1,"Type F11 "]
[null,"30W LED 600x600mm Recessed Flat Panel type "]
[null,"Light Fitting, Non-Dimmable, Enlite L70 50,000"]
[null,"Hours Cat No. EN-FPRO6060/40, or Equal and "]
[null,"Approved, including Flat Panel Cat No "]
[null,"EN-CRM6060A, complete with 5 Amp 3-pin "]
[null,"Plug Top and Flexible Cabtyre Cable, with "]
[null,"sealant to perimeter of fitting","No",2]
[]
[2,"Type F12 "]
[null,"54W LED 1500mm long Surface type Light"]
[null,"Fitting, exactly as for Type F2, Rated IP65, "]
[null,"Rated IP65 Anti-Corrosion, Vandal Proof,  "]
[null,"Polycarbonate housing and Opal diffuser, "]
[null,"connected in Tandem, including Fabricated "]
[null,"Stainless Steel Reflector the full length of each "]
[null,"fitting and width plus section protruding 100mm "]
[null,"below fitting to provide a reflector to direct light"]
[null,"on Signage on wall as indicated on the Layout "]
[null,"Drawing PE231 - EL3","No",24]
[]
[3,"Type F13 "]
[null,"54W LED 1500mm long Surface type Light"]
[null,"Fitting, exactly as for Type F2, Rated IP65, "]
[null,"Rated IP65 Anti-Corrosion, Vandal Proof,  "]
[null,"Polycarbonate housing and Opal diffuser, "]
[null,"connected in Tandem, below Handrail as indicated"]
[null,"on the Layout Drawing PE231 - EL5","No",36]
{"$rows_empty":11}
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/56"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[1,"Type P"]
[null,"37W LED Post-Top Luminaire, Beka Range,  "]
[null,"4000k, or equal and approved, including "]
[null,"a 4800mm long galvanised Tubular Steel Pole"]
[null,"in accordance with relevant SANS Specifications,"]
[null,"with access window, to compartment containing "]
[null," Driver, Control Gear, 5Amp SP&N CB and Earth"]
[null,"Stud. The Pole installed into a Concrete Base to "]
[null,"relevant SANS specifications. ","No",5]
[]
[2,"Type P1"]
[null,"30W LED Post Mounted Luminaire Regent "]
[null,"Cat No ILANGA Black outer colour."]
[null,"NOTE: The full specification is available for procurement"]
[null,"Refer to the Main Project Specification"]
[]
[3,"Type P2"]
[null,"54W LED Post Mounted Luminaire Regent "]
[null,"Cat No KHANYA ISTRA Black outer colour."]
[null,"NOTE: The full specification is available for procurement"]
[null,"Refer to the Main Project Specification"]
{"$rows_empty":18}
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/57"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"FIXTURES/ APPLIANCES"]
[null,"Supply, delivery to site, storage and install-"]
[null,"ation of the below specified \"Type\" Fixtures /"]
[null,"appliances complete with all necessary "]
[null,"accessories.  Fixtures and appliances to be "]
[null,"as specified or other approved."]
[]
[null,"Procedure Rooms Earth Fault Indicating "]
[null,"Lights"]
[1,"Type - TIL  Indicator Lights for the Procedure"]
[null,"Rooms - \"Red\" flashing 2W LED lamp and"]
[null,"Green\" 2W LED Lamp in flush mounted box"]
[null,"with 200x100mm cover plate","No",2]
[]
[2,"Type - TLN   4 x 2W LED Lamp Indicator Light"]
[null,"Nurses  Station ","No",1]
[]
[3,"Type - PEP  Patient Earth Point for Procedure "]
[null,"Room"]
[null,"including specialized plug point and cord"]
[null,"as specified.","No",1]
[]
[null,"Viewing Screens"]
[4,"Type - XR3 Flush mounted X-Ray viewing"]
[null,"screens three plate, size 1260 x 430mm."]
[null,"to be switched from Procedure Room Control "]
[null,"Switch Box","No",1]
[]
[5,"Type - XR4 Surface mounted X-Ray viewing"]
[null,"screens, three plate, size 1260 x 430mm,"]
[null,"with integrally mounted switch module for the","No",4]
[null,"Treatment Rooms"]
{"$rows_empty":7}
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/58"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[1,"Door Mechanisms / Buzzers, etc."]
[null,"Type - DR  Door Mounted Latch Release "]
[null,"mechanisms to be supplied for access doors ","No",4]
[]
[2,"Type - DRP 20 Amp \"On-Off\" Push Button "]
[null,"Station, flush mounted as specified","No",2]
[]
[3,"Type - DRK Wall mounted 12 digit "]
[null,"programmable release Key Pad station for"]
[null,"five doors, including 2 intercom stations"]
[null,"per door, as specified","No",4]
[]
[4,"Type - DRR  12 Volt Ring Tone Unit including"]
[null,"including intercom units, as specified","No",2]
[]
[5,"Type - BZ Buzzer unit for Electric Door Latch"]
[null,"release, including 2 intercom stations,"]
[null,"as specified.","No",4]
[]
[6,"Type TCB - TRAFFIC CONTROL BOOMS"]
[null,"Allow to Supply and Install Traffic Control "]
[null,"Booms as Specified. "]
[null,"The Booms shall be Automatic Electrically"]
[null,"powered, on both Entrance and Exit lanes. "]
[null,"Supply and Install Main Pedestals and locating "]
[null,"Pedestals on the opposite sides of the roads,"]
[null,"operating a 5000mm long red/white/yellow spiral "]
[null,"painted booms fitted with a STOP and NO-ENTRY "]
[null,"signs respectively identifiable from both sides, "]
[null,"controlled by means of activation by Discs and"]
[null,"Remote Modules, and including Induction Loops to"]
[null,"be installed for both booms as specified including"]
[null,"the supply of 50 Discs and 50 remote Modules, "]
[null,"refer specification"]
[null,"Noted that the there is a South and West Entrance"]
[null,"and both Entrances are to served with Boom Gates","No",2]
[]
[]
[]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/59"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[1,"Type BWC - Battery Operated WALL CLOCKS "]
[null,"Allow to supply and install Battery Operated"]
[null,"Wall clocks comprising 254mm Circular dial "]
[null,"Units to allow time clock adjustments and settings "]
[null,"to be made without having to reseal units for normal"]
[null,"operation","No",8]
[]
[2,"Type - HB 1,5kW 10 litre Wall mounted "]
[null,"\"Hydroboil Unit\" stainless steel with "]
[null,"thermostat.","No",10]
[]
[3,"Type - 2000W Wall Mounted Hand Dryers,"]
[null,"the body to consist of a High Quality Stainless "]
[null,"Steel, controlled by means of a Proximity Switch","No",14]
[]
[4,"Type - BHU1  (Procedure/Treatment Rooms )"]
[null,"Horizontally installed surface mounted"]
[null,"trunking 1500mm wide, equipped with 3 sets"]
[null,"of Oxygen & Vacuum outlets, 3 x Provision"]
[null,"only for Nurse Call Stations, 2 x Emergency"]
[null,"Stations, 3 x 600mm medical rails & 3 sets "]
[null,"2 x 15 Amp 3-pin socket outlets equally "]
[null,"divided between essential power and non-"]
[null,"essential power.","No",2]
{"$rows_empty":16}
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/60"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"EARTHING"]
[1,"Earth Test"]
[null,"Earth Resistivity tests in the location "]
[null,"designated and forwarding results to"]
[null,"determine installation of Mains and Computer"]
[null,"Earthing requirements.  (Positions to be "]
[null,"shown for both the Mains Earthing and "]
[null,"Computer Earthing Systems)","Item"]
[]
[2,"Earth Spikes - Mains Earth"]
[null,"Supply and Install Earth spike 1,5m long"]
[null,"driven into the ground and connected to"]
[null,"distribution board and/or earth stud at the"]
[null,"cable pipe entry to the building, using 50mm²"]
[null,"PVC insulated copper earth wire each 10mm"]
[null,"girth including all cable terminations, etc.","No",5]
[]
[3,"Earth Spikes - Computer Earth"]
[null,"Supply and Install Earth spike 1,5m long"]
[null,"driven into the ground and connected to"]
[null,"distribution board and/or earth stud at the"]
[null,"cable pipe entry to the building, using 50mm²"]
[null,"PVC insulated copper earth wire each 10mm"]
[null,"girth including all cable terminations, etc.","No",14]
[]
[4,"Computer Earth Studs"]
[null,"Supply and install a stand-off Insulated"]
[null,"Earth Stud in 100 x 100 x 100mm cast resin"]
[null,"enclosure on each level as a dedicated"]
[null,"computer earth point (70mm² Earth "]
[null,"Conductor and Lugged terminations measured"]
[null,"under reticulation earthing)","No",2]
[]
[5,"Earthing and Bonding"]
[null,"Earthing and bonding of the installation"]
[null,"including all equipment, water pipes, etc."]
[null,"in compliance with the General Specification,"]
[null,"the Code of Practice and the Local Supply"]
[null,"Authorities as per the Statutory requirements"]
[null,"iro Wiring of Premises","Item"]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"E6/61"]
[]
[null,"(NOTE:  THE RELEVANT DETAIL SPECIFICATION FOR THE GENERAL ELECTRICAL INSTALLATIONS HAS BEEN INCLUDED IN SECTION 1 : PART 3 : PARA 3.44 : PAGE E3/61)"]

{"sheet":"EL Coll","index":5,"n_rows":104,"n_cols":4,"rows_kept":104,"flags":["formulas_cached_only"]}
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
[null,"COLLECTION PAGE"]
[{"$nulls":3},"AMOUNT"]
[]
[]
[null,"Total brought forward from pages","E6/1"]
[null,null,"E6/2"]
[null,null,"E6/3"]
[null,null,"E6/4"]
[null,null,"E6/5"]
[null,null,"E6/6"]
[null,null,"E6/7"]
[null,null,"E6/8"]
[null,null,"E6/9"]
[null,null,"E6/10"]
[null,null,"E6/11"]
[null,null,"E6/12"]
[null,null,"E6/13"]
[null,null,"E6/14"]
[null,null,"E6/15"]
[null,null,"E6/16"]
[null,null,"E6/17"]
[null,null,"E6/18"]
[null,null,"E6/19"]
[null,null,"E6/20"]
[null,null,"E6/21"]
[null,null,"E6/22"]
[null,null,"E6/23"]
[null,null,"E6/24"]
[null,null,"E6/25"]
[null,null,"E6/26"]
[null,null,"E6/27"]
[null,null,"E6/28"]
[null,null,"E6/29"]
[null,null,"E6/30"]
{"$rows_empty":9}
[null,"CARRIED FORWARD TO FOLLOWING PAGE ","R"]
[]
[]
[null,null,"E6/62"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL NEW PSYCHIATRIC WARD"]
[]
[null,"ELECTRICAL INSTALLATIONS  (CPAP Work Group No. 160)"]
[]
[null,"COLLECTION PAGE (cont.)"]
[{"$nulls":3},"AMOUNT"]
[]
[null,"BROUGHT FORWARD FROM PAGE GE 1","R"]
[]
[]
[null,"Totals brought forward from pages","E6/31"]
[null,null,"E63/2"]
[null,null,"E6/33"]
[null,null,"E6/34"]
[null,null,"E6/35"]
[null,null,"E6/36"]
[null,null,"E6/37"]
[null,null,"E6/38"]
[null,null,"E6/39"]
[null,null,"E6/40"]
[null,null,"E6/41"]
[null,null,"E6/42"]
[null,null,"E6/43"]
[null,null,"E6/44"]
[null,null,"E6/45"]
[null,null,"E6/46"]
[null,null,"E6/47"]
[null,null,"E6/48"]
[null,null,"E6/49"]
[null,null,"E6/50"]
[null,null,"E6/51"]
[null,null,"E6/52"]
[null,null,"E6/53"]
[null,null,"E6/54"]
[null,null,"E6/55"]
[null,null,"E6/56"]
[null,null,"E6/57"]
[null,null,"E6/58"]
[null,null,"E6/59"]
[null,null,"E6/60"]
[null,null,"E6/61"]
[]
[]
[]
[]
[null,"Total Carried forward to Summary page  (ESP6)",null,"R"]
[]
[]
[]
[null,null,"E6/63"]

{"sheet":"B of Q T","index":6,"n_rows":98,"n_cols":6,"rows_kept":98,"flags":["formulas_cached_only"]}
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"TELEPHONE INSTALLATIONS (CPAP Work Group No. 160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[1,"TELEPHONE INSTALLATIONS"]
[null,"Allow to supply and install the equipment"]
[null,"and labour in the existing Telephone"]
[null,"Exchange in the existing Hospital to accommo-"]
[null,"date approximately 48 additional extensions"]
[null,"including the connecting of conductors as"]
[null,"may be required.","Item"]
[]
[2,"TELEPHONE INSTRUMENTS"]
[null,"Supply and install clear tone, push button"]
[null,"desk top type, supplied by PLESSIS CC"]
[null,"TELLUMAT M100 Analogue type,  handsets,"]
[null,"tone/pulse switchable with ring, speaker and "]
[null,"volume control, complete with handset."]
[null,"Light grey in colour all as per specification.","No",48]
[]
[3,"TELEPHONE OUTLETS"]
[null,"Supply and Install telephone outlets in"]
[null,"power skirtings and on wall mounted draw"]
[null,"boxes to be equipped with RJ11 type"]
[null,"telephone jack outlets complete with "]
[null,"appropriate cover plates as required","No",48]
[null,""]
[4,"TELEPHONE CABLE"]
[null,"Supply and Install 0,10mm² 100-pair PVC"]
[null,"insulated SANS approved armoured "]
[null,"Telephone Cable installed via Conduits, Cable "]
[null,"Pipes, Cable Trays,  Power Skirting Runs etc."]
[null,"between the New Psychiatric Ward and the"]
[null,"Main MDF at the entrance to the Hospital"]
[null,"situated at the Bazley Street Entrance","m",480]
[]
[5,"Supply and Install 0,10mm²  4-Pair PVC "]
[null,"insulated SANS approved Telephone Cable"]
[null,"installed into conduits and on cable ladders "]
[null,"and connected both ends, all as per "]
[null,"specification, as follows:","m",362]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"TI/1"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL                                     NEW PSYCHIATRIC WARD"]
[]
[null,"TELEPHONE INSTALLATIONS (CPAP Work Group No. 160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[1,"TESTING & COMMISSIONING OF "]
[null,"TELEPHONE INSTALLATION"]
[null,"Allow to Test and Commission the installation"]
[null,"including final programming as per specific-"]
[null,"ation and handing over to the Department's"]
[null,"Representative","Item"]
[]
[]
[2,"GUARANTEE AND MAINTENANCE"]
[null,"Guarantee and maintenance for the complete"]
[null,"installation including fittings, fixtures,"]
[null,"materials and workmanship for a period of"]
[null,"TWELVE MONTHS after date of completion"]
[null,"and handover","Item"]
[]
[]
[3,"OPERATING MANUALS, ETC"]
[null,"Allow to provide sets of Operating and"]
[null,"Instruction Manuals including parts lists,"]
[null,"catalogues, etc.","Sets",4]
{"$rows_empty":17}
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"TI/2"]
[]
[null,"(NOTE:  THE RELEVANT DETAIL SPECIFICATION FOR THE TELEPHONE INSTALLATIONS HAS BEEN INCLUDED IN SECTION 1 : PART 3 : PARA 3.44 : PAGE E3/61)"]

{"sheet":"TI Coll","index":7,"n_rows":55,"n_cols":3,"rows_kept":55,"flags":["formulas_cached_only"]}
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL NEW PSYCHIATRIC WARD"]
[]
[null,"TELEPHONE INSTALLATIONS  (CPAP Work Group No. 160)"]
[]
[null,"COLLECTION PAGE"]
[]
[""]
[]
[]
[]
[]
[null,"Total brought forward from pages","T6/1"]
[]
[]
[null,null,"T6/2"]
{"$rows_empty":36}
[null,"Total Carried forward to Summary page  (ESP6)"]
[]
[null,null,"TI/3"]

{"sheet":"B of Q PA","index":8,"n_rows":109,"n_cols":6,"rows_kept":109,"flags":["formulas_cached_only"]}
[null,"PORT SHEPSTONE REGIONAL HOSPITAL   NEW PSYCHIATRIC WARD"]
[]
[null,"PUBLIC ADDRESS INSTALLATIONS (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"PUBLIC ADDRESS INSTALLATIONS "]
[null,"Allow to Supply and Install the complete Public "]
[null,"Address installations on three levels for the New"]
[null,"PSYCHIATRIC WARD facilty all as indicated on "]
[null,"Drawings and as Specified and connecting "]
[null,"to the existing PA System in the existing Hospital"]
[null,"Hospital, all as follows:."]
[]
[null,"Connecting to the Existing"]
[1,"Allow to incorporate the New PA Speaker System"]
[null,"into the existing System Main Control Panel"]
[null,"situated at the existing Main 24Hr Room at the "]
[null,"Main Entrance to the Hospital off Bazley Street."]
[null,"(The main reticulation cable included below)","Item"]
[]
[2,"SPEAKERS (Internal Recessed)"]
[null,"Supply and Install 10 Watt 400mm Round "]
[null,"recessed mounted speakers complete with "]
[null,"a 10 Watt transformer,suitable for 110V line system "]
[null,"installed in  Suitable Recess Enclosure"]
[null,null,"No",16]
[3,"SPEAKERS (Internal Surface )"]
[null,"Supply and Install 10 Watt 400mm round"]
[null,"Surface mounted speakers complete with a "]
[null,"10 Watt transformers uitable for 110V line system "]
[null,"in Suitable Surface Enclosure","No",4]
[]
[4,"SPEAKERS (External)"]
[null,"Supply and Install 10 Watt 400mm aluminuim "]
[null,"horn speakers complete with a 10 Watt transformer"]
[null,"suitable for 110V line system but externally "]
[null,"mounted","No",2]
[]
[5,"PUBLIC ADDRESS CABLE (universal)"]
[null,"Supply and Install 0,10mm² 4-pair PVC"]
[null,"insulated SANS approved telephone"]
[null,"type cabling installed into conduit runs"]
[null,"and on cable ladders, etc., and connected"]
[null,"to speakers and equipment as specified.","m",290]
[]
[]
[]
[]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,null,"PA6/1"]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL   NEW PSYCHIATRIC WARD"]
[]
[null,"PUBLIC ADDRESS INSTALLATIONS (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[1,"PUBLIC ADDRESS CABLE (External)"]
[null,"Supply and Install 0,10mm² 4-pair PVC"]
[null,"insulated armoured SANS approved "]
[null,"telephone type cable installed in cable"]
[null,"pipes, conduit runs, connected to"]
[null,"speakers and equipment as specified.","m",166]
[]
[2,"PUBLIC ADDRESS CABLE (Connecting"]
[null,"to 24Hr Existing Main Control Panel )"]
[null,"Supply and Install 1,5mm² 4-Core PVC SWA PVC "]
[null,"insulated armoured SANS approved Armoured"]
[null,"type cable installed via Conduit, Cable Pipe and "]
[null,"Unistruts etc.between the New Psychiatric Ward"]
[null,"Building and the existing 24hr main control panel ","m",280]
[]
[3,"TESTING & COMMISSIONING of the "]
[null,"PA SYSTEM INSTALLATION"]
[null,"Allow to test and commission the"]
[null,"installation as per specification and"]
[null,"handing over to the Department's"]
[null,"Representative","Item"]
[]
[4,"GUARANTEE AND MAINTENANCE"]
[null,"Guarantee and maintenance to cover"]
[null,"the work that has been undertaken"]
[null,"and completed as part of this contract"]
[null,"including fittings, fixtures, materials and"]
[null,"workmanship for a period of TWELVE"]
[null,"MONTHS after date of completion and "]
[null,"handover.","Item"]
[]
[4,"OPERATING MANUALS, ETC"]
[null,"Allow to provide sets of Operating and"]
[null,"Instruction Manuals including parts lists,"]
[null,"catalogues, etc., for new equipment","Sets",4]
{"$rows_empty":8}
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,null,"PA6/2"]
[]
[null,"(NOTE:  THE RELEVANT DETAIL SPECIFICATION FOR THE PUBLIC ADDRESS INSTALLATION HAS BEEN INCLUDED IN SECTION 1 : PART 3 : PARA 3.44 : PAGE E3/61)"]

{"sheet":"PA Coll","index":9,"n_rows":55,"n_cols":3,"rows_kept":55,"flags":["formulas_cached_only"]}
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL NEW PSYCHIATRIC WARD"]
[]
[null,"PUBLIC ADDRESS INSTALLATIONS (CPAP Work Group No. 160)"]
[]
[null,"COLLECTION PAGE"]
[]
[]
[]
[null,"Total brought forward from pages","PA6/1"]
[]
[]
[null,null,"PA6/2"]
{"$rows_empty":38}
[null,"Total Carried forward to Summary page  (ESP6)"]
[null,null,0]
[]
[null,null,"PA6/3"]

{"sheet":"BofQCCTV","index":10,"n_rows":217,"n_cols":7,"rows_kept":217,"flags":["formulas_cached_only"]}
[null,"PORT SHEPSTONE REGIONAL HOSPITAL   NEW PSYCHIATRIC WARD"]
[]
[null,"CCTV INSTALLATIONS (CPAP Work Group No. 160)"]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"CCTV INSTALLATIONS"]
[null,"Supply and install the complete the Closed "]
[null,"Circuit  Colour Television Installations for the "]
[null,"New Psychiatric Ward Facility comprising of "]
[null,"Three separate Systems as follows:"]
[]
[null,"A.     The Main Patient Observation"]
[null,"B.     The Surrounding Ward circulation Areas,"]
[null,"                 Ground and First Floor "]
[null,"C.     The Security Surveilance, Parking Level and"]
[null,"                 Externally the Surrounding the Building"]
[]
[null,"Equipment required for each System as follows:"]
[]
[null,"A.     The Main Patient Observation Units"]
[1,"The Main Control Units located on the desks in the "]
[null,"Nurses Staions, including selector Panels"]
[null,"remote control modules, to enable selection of "]
[null,"individual cameras and full screen observation of "]
[null,"all cameras similtaniously."]
[null,"The control units to include Flash Drive / CD Unit "]
[null,"with multi chamber feed recording from selected "]
[null,"or all cameras as may be required."]
[null,"The Units to be supplied with Computer Software"]
[null,"and Training as Specified. ","No",4]
[]
[2,"Closed Circuit Colour High Resolution TV Monitors"]
[null,"consisting of 32cm screen including swivel "]
[null,"mounting brackets","No",4]
[]
[3,"Domed TV colour Cameras with 3,7mm lens, "]
[null,"suitable for internal installations against concrete "]
[null,"and/or suspended ceilings including mounting "]
[null,"brackets","No",18]
[]
[4,"Allow for the installation of the MAIN PATIENT "]
[null,"OBSERVATION System as specified"]
[null,"Noted that the \"cable and terminations\" refer"]
[null,"following Bill pages as measured, conduits with"]
[null,"draw wires installed by the appointed Electrical "]
[null,"Contractor","Item"]
[]
[]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"CCTV6/1"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL   NEW PSYCHIATRIC WARD"]
[]
[null,"CCTV INSTALLATIONS (CPAP Work Group No. 160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"B.     The Surrounding Ward circulation Areas,"]
[null,"                 Ground and First Floor "]
[]
[1,"The Main Control Unit located on Ground Floor "]
[null,"Security including selector Panel,"]
[null,"remote control modules, to enable selection of "]
[null,"individual cameras and full screen observation of "]
[null,"all cameras similtaniously."]
[null,"The control unit to include Flash Drive / CD Unit "]
[null,"with multi chamber feed recording from selected "]
[null,"or all cameras as may be required."]
[null,"The Unit to be supplied with Computer Software"]
[null,"and Training as Specified. ","No",1]
[]
[2,"Closed Circuit Colour High Resolution TV "]
[null,"Surveylance Cameras, with 2,8 - 12.0mm variable "]
[null,"direct dome lens complete with pan, zoom, "]
[null,"controls, including galvanised steel mounting "]
[null,"bracket, all suitable for internal installation "]
[null,"Refer Mounting Details on Drawings PE 231- "]
[null,"CCTV1 and CCTV2","No",28]
[]
[3,"Closed Circuit Colour High Resolution"]
[null,"TV Monitors located on the Security Desk, the"]
[null,"Security Guard Desk and on the Main Nurses "]
[null,"Station Desk, all on Ground Floor Level, "]
[null,"consisting closed Circuit Colour High Resolution"]
[null,"including swivel mount basses.","No",3]
[]
[4,"Allow for the installation of the Surrounding Ward "]
[null,"and Circulation Areas Systems as specified"]
[null,"Noted that the \"cable and terminations\" refered "]
[null,"in the following Bill pages as measured, conduits "]
[null,"including draw wires installed by the appointed"]
[null,"Electrical Contractor. The CCTV sub Contractor is"]
[null,"to engage fully during the installation of the "]
[null,"conduit runs and outlets","Item"]
{"$rows_empty":7}
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"CCTV6/2"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL   NEW PSYCHIATRIC WARD"]
[]
[null,"CCTV INSTALLATIONS (CPAP Work Group No. 160)"]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"C.     The Security Surveilance, Parking Level "]
[null,"           and Externally Surrounding the Building"]
[]
[1,"The Main Control Unit, to be located on the "]
[null,"Security Guard desk at the entrance to the"]
[null,"building, including selector Panel and"]
[null,"remote control modules, to enable selection of "]
[null,"individual cameras and full screen observation of "]
[null,"all cameras similtaniously."]
[null,"The control unit to include Flash Drive / CD Unit "]
[null,"with multi chamber feed recording from selected "]
[null,"or all cameras as may be required."]
[null,"The Unit to be supplied with Computer Software"]
[null,"and Training as Specified. ","Item"]
[]
[2,"Closed Circuit Colour High Resolution TV "]
[null,"Surveylance Cameras, with 2,8 - 12.0mm variable "]
[null,"direct dome lens complete with pan, zoom, "]
[null,"controls, including galvanised steel mounting "]
[null,"bracket, all suitable for internal installation "]
[null,"Refer Mounting Details on Drawings PE 231- ","No",12]
[null,"CCTV1 and CCTV2"]
[]
[3,"Closed Circuit Colour High Resolution TV Monitors"]
[null,"consisting of 80cm Screen including swivel "]
[null,"mounting brackets to be installed on the Security "]
[null,"Desk at the Entrance to the Psychiatric Unit"]
[null,"and a Remotely Insatalled unit in the Security "]
[null,"Building at the South Entrance to the Hospital","No",2]
[]
[5,"UPS POWER PACK FOR EMERGENCY"]
[null,"Power Pack equipment consisting of a 5kVA"]
[null,"UPS with battery capacity to supply power to the"]
[null,"Main Security Panel for a minimum of 2hrs","Item"]
[]
[null,"CABLING FOR THE  CCTV INSTALLATIONS "]
[null,"as SPECIFIED"]
[4,"Closed Circuit TV co-axial cable with connections"]
[null,"to Controls Panels, Cameras and Monitors"]
[null,"including required DC Jack socket outlets."]
[null,"consisting of twisted core shielded cable "]
[null,"in the industry known as (Twisters)","m",1090]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"CCTV6/3"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL   NEW PSYCHIATRIC WARD"]
[]
[null,"CCTV INSTALLATIONS (CPAP Work Group No. 160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT","AMOUNT"]
[]
[1,"SUNDRY ITEMS"]
[null,"All sundry items required for the "]
[null,"complete supply and installation"]
[null,"of the CCTV installations as Specified","Item"]
[]
[2,"TESTING & COMMISSIONING"]
[null,"Allow to test and commission the"]
[null,"installation as per specification"]
[null,"and handing over to the Department","Item"]
[]
[3,"GUARANTEE AND MAINTENANCE"]
[null,"Guarantee and maintenance for the"]
[null,"complete installation including fittings,"]
[null,"fixtures, materials and workmanship"]
[null,"for a period of TWELVE MONTHS"]
[null,"after date of completion and "]
[null,"handover","Item"]
{"$rows_empty":25}
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"CCTV6/4"]
[]
[null,"(NOTE:  THE RELEVANT DETAIL SPECIFICATION FOR THE CCTV INSTALLATIONS HAS BEEN INCLUDED IN SECTION 1 : PART 3 : PARA 3.44 : PAGE E3/61)"]

{"sheet":"CCTV Coll","index":11,"n_rows":57,"n_cols":4,"rows_kept":57,"flags":["formulas_cached_only"]}
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL NEW PSYCHIATRIC WARD"]
[]
[null,"CCTV INSTALLATIONS (CPAP Work Group No.160)"]
[]
[null,"COLLECTION PAGE"]
[]
[]
[]
[{"$nulls":3},"R"]
[]
[]
[null,"Brought forward from page","CCTV6/1"]
[]
[]
[null,null,"CCTV6/2"]
[]
[]
[null,null,"CCTV6/3"]
[]
[]
[null,null,"CCTV6/4"]
{"$rows_empty":32}
[null,"Total Carried forward to Summary page  (ESP6)",null,"R"]
[]
[null,"CCTV6/5"]

{"sheet":"B of Q MS","index":12,"n_rows":52,"n_cols":6,"rows_kept":52,"flags":["formulas_cached_only"]}
[null,"PORT SHEPSTONE REGIONAL HOSPITAL   NEW PSYCHIATRIC WARD"]
[]
[null,"MICROPHONE AND SPEAKER INSTALLATIONS (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"MICROPHONE AND SPEAKER INSTALLATIONS "]
[null,"Supply and install the complete Microphone"]
[null,"and Speaker installations for the Student Training"]
[null,"Room,as indicated on the Power Layout drawing"]
[null,"SL231 - EP4 and as Specified"]
[]
[null,"Amplifier"]
[1,"100 Watt Stereo Amplifier with built in CD Player,"]
[null,"Microphone and Speaker outlets and 2 x USB Ports","No",1]
[]
[null,"Microphone"]
[2,"Uni-directional Microphones on desk mounting"]
[null,"brackets","No",1]
[]
[null,"Speakers"]
[3,"36 Watt Speakers on adjustable ceiling/wall"]
[null,"mounting brackets","No",4]
[]
[null,"MICROPHONE AND LOUDSPEAKER CABLE"]
[4,"Supply and install 0,10mm² 4-pair PVC Insulated"]
[null,"SANS approved from Amplifier to Microphone &"]
[null,"Speaker, cable into conduit and connected both "]
[null,"ends, all as per specification","m",42]
[]
[null,"TESTING & COMMISSIONING OF AMPLIFIER "]
[null,"MICROPHONE & SPEAKER INSTALLATION"]
[5,"Allow to test and commission the installation"]
[null,"as per specification and handing over to"]
[null,"the Department's Representative","Item"]
[]
[null,"GUARANTEE AND MAINTENANCE"]
[6,"Guarantee and maintenance for the complete"]
[null,"installation including fittings, fixtures, materials"]
[null,"and workmanship for a period of TWELVE"]
[null,"MONTHS after date of completion and handover","Item"]
[]
[null,"OPERATING MANUALS, ETC."]
[7,"Allow to provide sets of Operating and"]
[null,"Instruction Manuals including parts lists,"]
[null,"catalogues, etc.","Sets",4]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,null,"MS6/1"]
[null,"(NOTE:  THE RELEVANT DETAIL SPECIFICATION FOR THE MICROPHONE SPEAKER INSTALLATION HAS BEEN INCLUDED IN SECTION 1 : PART 3 : PARA 3.44 : PAGE E3/61)"]

{"sheet":"MS Coll","index":13,"n_rows":56,"n_cols":4,"rows_kept":56,"flags":["formulas_cached_only"]}
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL NEW PSYCHIATRIC WARD"]
[]
[null,"MICROPHONE AND SPEAKER INSTALLATIONS"]
[]
[null,"COLLECTION PAGE"]
[]
[]
[]
[{"$nulls":3},"R"]
[]
[]
[null,"Brought forward from page","MS6/1"]
{"$rows_empty":39}
[null,"Total Carried forward to Summary page  (ESP6)",null,"R"]
[]
[]
[null,"MS6/2"]

{"sheet":"B of Q NC","index":14,"n_rows":100,"n_cols":6,"rows_kept":100,"flags":["formulas_cached_only"]}
[null,"PORT SHEPSTONE REGIONAL HOSPITAL   NEW PSYCHIATRIC WARD"]
[null,"NURSE CALL SYSTEM INSTALLATIONS (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"NURSE CALL SYSTEM."]
[null,"Allow to supply and install a Nurse Call"]
[null,"System generally for the Procedure Room and"]
[null,"Associated facilitiesas per detail specification"]
[]
[null,"Note: Allowance to be made for the "]
[null,"provision of the Pushbuttons / Cancellation"]
[null,"stations and plug in sockets and for "]
[null,"umbilical cords for remote push-Buttons to"]
[null,"be allowed all as part of the Nurse Call "]
[null,"Installations"]
[]
[null,"MAIN NURSES STATION"]
[1,"The Main Annunciator and Control"]
[null,"Station to be installed on the Nurses Station"]
[null,"Desk Counter","No",1]
[]
[2,"Wall Mounted Nurse Call Stations"]
[null,"Units, plug-in-type, with umbilical cords","No",4]
[]
[3,"Nurse Call response illuminated"]
[null,"cancellation stations in wall draw boxes","No",3]
[]
[4,"Emergency Pushbutton Stations in wall ","No",3]
[null,"boxes"]
[]
[5,"Ring Devices with flashing indicating"]
[null,"lights to be installed in wall or ceiling"]
[null,"drawboxes","No",3]
[]
[null,"Nurse Call System Cabling -"]
["`","Supply and install 0,10mm² 10-pair PVC"]
[null,"insulated SANS approved Nurse Call"]
[null,"conductor into conduit and connected"]
[null,"to the equipment specified","m",180]
[]
[]
[]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"NC6/1"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL   NEW PSYCHIATRIC WARD"]
[]
[null,"NURSE CALL SYSTEM INSTALLATIONS (CPAP Work Group No.160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"SERVICE MANUALS"]
[6,"Complete sets of Service Manuals,"]
[null,"Operating Instructions, Part Lists,"]
[null,"and Catalogue Details","No",4]
[]
[null,"TESTING & COMMISSIONING"]
[7,"Allow to test and commission the"]
[null,"installation as per specification"]
[null,"and handing over to the Department","Item"]
[]
[null,"GUARANTEE AND MAINTENANCE"]
[8,"Guarantee and maintenance for the"]
[null,"complete installation including fittings,"]
[null,"fixtures, materials and workmanship"]
[null,"for a period of TWELVE MONTHS"]
[null,"after date of completion and "]
[null,"handover","Item"]
{"$rows_empty":22}
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,"NC6/2"]
[]
[null,"(NOTE:  THE RELEVANT DETAIL SPECIFICATION FOR THE NURSE CALL INSTALLATION HAS BEEN INCLUDED IN SECTION 1 : PART 3 : PARA 3.44 : PAGE E3/61)"]

{"sheet":"NC Coll","index":15,"n_rows":52,"n_cols":4,"rows_kept":52,"flags":["formulas_cached_only"]}
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL NEW PSYCHIATRIC WARD"]
[]
[null,"NURSE CALL INSTALLATION  (CPAP Work Group No.160)"]
[]
[null,"COLLECTION PAGE"]
[]
[]
[]
[{"$nulls":3},"R"]
[]
[]
[null,"Brought forward from page","NC6/1"]
[]
[]
[null,null,"NC6/2"]
{"$rows_empty":33}
[null,"Total Carried forward to Summary page  (ESP)",null,"R"]
[]
[null,"NC6/3"]

{"sheet":"BofQ TV","index":16,"n_rows":107,"n_cols":6,"rows_kept":107,"flags":["formulas_cached_only"]}
[null,"PORT SHEPSTONE REGIONAL HOSPITAL   NEW PSYCHIATRIC WARD"]
[]
[null,"TELEVISION INSTALLATION (CPAP Work Group No. 160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"Supply & Installation of TELEVISION SETS"]
[null,"and Associated Infrastructure"]
[1,"Supply and Install New 1390mm (55inch) LED"]
[null,"HD Television Sets (TV)"]
[null,"The TV Sets shall be of High Quality LG or   "]
[null,"Samsung, or equal and approved Make "]
[null,"including remote control handsets, Sets supplied"]
[null,"with standard Yellow/White/Red - Video/LMono"]
[null,"/Radio, HDMI and USB inputs all duplicated "]
[null,"on the rear and side of of the Set. The TV Sets "]
[", ","Shall be LG, Samsung or equal and approved","No",5]
[]
[2,"Supply and install a 800mm diameter "]
[null,"wall mounted Satellite TV Dish "]
[null,"manufactured from pressed/moulded "]
[null,"aluminium and anodisation coated, complete"]
[null,"with LNB receiver Module, and Galvanised "]
[null,"steel mounting brackets and Galvanised "]
[null,"steel bolting fixtures","No",1]
[]
[3,"Field strength test for the installation of"]
[null,"VHF /UHF Television Aerial System","Item"]
[]
[4,"Television socket outlets for TV Sets","No",2]
[]
[5,"Provisional Single Core Co-axial cable"]
[null,"Installed between Dish and TV Set socket"]
[null,"outlet (conduit measured elsewhere)","m",280]
[]
[6,"Installation of Earthing System for the TV  Sets","Item"]
[]
[7,"Provisional Antennae Earth Conductor "]
[null,"consisting of 16mm² solid Alluminium","m",60]
[]
[8,"3 x 1500mm long Earth Spikes"]
[null,"installed 100mm below ground level","Item"]
[]
[null,"Note: 25mm Galvanised steel conduit and "]
[null,"100 x 100 x 50mm draw boxes, cover plates and "]
[null,"draw wires have been allowed and measured as"]
[null,"part of the General Electrical Installation work"]
[]
[]
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,null,"TV6/1"]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL   NEW PSYCHIATRIC WARD"]
[]
[null,"TELEVISION INSTALLATION (CPAP Work Group No. 160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[1,"GUARANTEE AND MAINTENANCE"]
[null,"Guarantee & maintenance for the"]
[null,"complete installation including, TV SETS, "]
[null,"equipment, fittings, fixtures, materials"]
[null,"and Workmanship for a period of"]
[null,"TWELVE MONTHS after date of"]
[null,"completion and handover","Item"]
[]
[2,"TESTING"]
[null,"Allow for testing and commissioning"]
[null,"the whole of the general Television"]
[null,"Installation as laid down in the spec.,"]
[null,"and for re-testing as may be required"]
[null,"after the making good of all defective"]
[null,"work to the entire satisfaction of the"]
[null,"Department and Engineer","Item"]
{"$rows_empty":27}
[null,"Carried to Collection Page",null,null,"R"]
[]
[null,null,"TV6/2"]
[]
[null,"(NOTE:  THE RELEVANT DETAIL SPECIFICATION FOR THE LIGHTNING PROTECTION INSTALLATION HAS BEEN INCLUDED IN SECTION 1 : PART 3 : PARA 3.44 : PAGE E3/61)"]

{"sheet":"TV Coll","index":17,"n_rows":56,"n_cols":4,"rows_kept":56,"flags":["formulas_cached_only"]}
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL NEW PSYCHIATRIC WARD"]
[]
[null,"TV INSTALLATION  (CPAP Work Group No.160)"]
[]
[null,"COLLECTION PAGE"]
[]
[]
[]
[{"$nulls":3},"R"]
[]
[]
[null,"Brought forward from page","TV6/1"]
[]
[]
[null,null,"TV6/2"]
{"$rows_empty":37}
[null,"Total Carried forward to Summary page  (ESP6)",null,"R"]
[]
[null,"TV6/3"]

{"sheet":"B of Q LP","index":18,"n_rows":106,"n_cols":6,"rows_kept":106,"flags":["formulas_cached_only"]}
[null,"PORT SHEPSTONE REGIONAL HOSPITAL   NEW PSYCHIATRIC WARD"]
[]
[null,"LIGHTNING PROTECTION INSTALLATION (CPAP Work Group No. 160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"LIGHTNING PROTECTION INSTALLATION "]
[null,"(Provisional)"]
[null,"Proprietary Articles"]
[null,"All equipment or materials used in the"]
[null,"Contract shall be that which is specified in"]
[null,"the General Specification or Bills of Quantities"]
[null,"or other approved."]
[null,"Note:  All quantities within this Bill"]
[null,"are Provisional"]
[]
[1,"SOIL TESTING"]
[null,"Allow for the testing and execution of a soil"]
[null,"restivity test survey of the complete scheme and"]
[null,"for submitting a copy of the reports complete"]
[null,"with recommendations tothe Electrical Engineer","Item"]
[]
[2,"TESTING (LIGHTNING PROTECTION)"]
[null,"Allow for the testing of the complete scheme"]
[null,"as described in the Detail Specification,"]
[null,"inclusive of any other costs and issuing of"]
[null,"the SANS Test Certificate","Item"]
[]
[3,"DOWN CONDUCTORS"]
[null,"Supply and Install 70mm² insulated stranded"]
[null,"copper earth conductors in galvanised "]
[null,"conduit in walls, brickwork, etc., as down"]
[null,"conductors to earth rods, etc., including lugs,"]
[null,"ferrules, bolts, etc.","m",400]
[null,"NOTE: Each of the 22 Down conductor is to be"]
[null,"Installed via a Lightning Protection Test Box, "]
[null,"built flush into Brickwork/Concrete Wall at "]
[null,"1000mm above ground level. The Test Boxes and"]
[null,"Conduits by the appointed Electrical Contractor"]
[]
[4,"AIR TERMINALS"]
[null,"Allow for Air Terminals for Non Metallic Sections of "]
[null,"roof coverageconsisting of the follwing:"]
[null,"Supply and install 9,5mm diameter aluminium"]
[null,"alloy conductors on standard stand-off"]
[null,"alluminium alloy guides at 1200mm centres.","m",40]
[]
[]
[null,"Carried to Collection Page",null,null,"R","."]
[]
[null,null,"LP6/1"]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL   NEW PSYCHIATRIC WARD"]
[]
[null,"LIGHTNING PROTECTION INSTALLATION (CPAP Work Group No. 160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"CONNECTING POINTS TO DOWN "]
[null,"CONDUCTORS"]
[1,"Supply and Install connecting points to Down"]
[null,"Conductors consisting of solid 9,5mm dia."]
[null,"aluminium section ferruled to the Air Terminal"]
[null,"on one end and lugged on the other end"]
[null,"(End to be bolted to brass terminal of Down)"]
[null,"Conductor).","No",22]
[]
[null,"SLEEVES, JOINTS AND CRIMPING"]
[null,"Supply and Install the following items:"]
[]
[2,"Crimp sleeves for jointing of roof structure"]
[null,"with down conductors","No",22]
[3,"Ferrules and lugs for bonding of any metal"]
[null,"work to roof structure","No",22]
[4,"Fininals inclusive of connections and jointing"]
[null,"to roof structure","No",22]
[5,"Test point connection for each down Conductor","No",22]
[6,"50mm² Copper Earth Conductor for laying"]
[null,"in trenches as horizontal earth conductor","m",74]
[]
[null,"EARTH RODS"]
[7,"Supply and Install 1,5m Copper Clad Steel "]
[null,"Earth Rods driven into ground including"]
[null,"joining to copper bonding conductor"]
[null,"(Allowed for elsewhere)","No",22]
[]
[null,"GALVANISED CONDUIT"]
[8,"Supply and Install 25mm galvanised conduit"]
[null,"installed flush in walls, including all necessary"]
[null,"off-sets, for down conductors, as specified","m",212]
[]
[9,"Supply and Install 25mm galvanised conduit"]
[null,"coupling and stopper combination at the top"]
[null,"and bottom for down conductors. "]
[null,"(Conductor entry drilled in stopper as Specified)","m",22]
[]
[]
[]
[]
[]
[]
[null,"Carried to Collection Page",null,null,"R","."]
[]
[null,null,"LP6/2"]
[]
[null,"(NOTE:  THE RELEVANT DETAIL SPECIFICATION FOR THE LIGHTNING PROTECTION INSTALLATION HAS BEEN INCLUDED IN SECTION 1 : PART 3 : PARA 3.44 : PAGE E3/61)"]

{"sheet":"LP Coll","index":19,"n_rows":54,"n_cols":3,"rows_kept":54,"flags":["formulas_cached_only"]}
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL NEW PSYCHIATRIC WARD"]
[]
[null,"LIGHTNING PROTECTION INSTALLATION (CPAP Work Group No. 160)"]
[]
[null,"COLLECTION PAGE"]
[]
[]
[]
[]
[null,"Total brought forward from pages","LP6/1"]
[]
[]
[null,null,"LP6/2"]
{"$rows_empty":37}
[null,"Total Carried forward to Summary page  (ESP)"]
[]
[null,null,"LP6/3"]

{"sheet":"BofQ UPS","index":20,"n_rows":51,"n_cols":6,"rows_kept":51,"flags":["formulas_cached_only"]}
[null,"PORT SHEPSTONE REGIONAL HOSPITAL   NEW PSYCHIATRIC WARD"]
[]
[null,"UPS INSTALLATION"]
[null,"INSTALLATIONS (CPAP Work Group No. 160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"UPS INSTALLATIONS"]
[1,"Supply and install the  20kVA Uninterruptible"]
[null,"Power Supply (UPS)  Units with 32 x 45Ahs"]
[null,"battery sets in a suitable cabinet with Three "]
[null,"phase input supply and Three Phase Output"]
[null,"supply, complete with digital display Display "]
[null,"Control Panels and Remote monitoring Unit."]
[null,"The unit UPS shall be complete with batteries"]
[null,"and shall operate as described in the"]
[null,"Detail Electrical Specification. The unit to be "]
[null,"installed in the UPS ROOM on First Floor level.","No",1]
[]
[null,"THE REMOTE DIGITAL DISPLAY"]
[2,"Supply and install a Digital Panel above the "]
[null,"Entrance door in a suitable enclosure","No",1]
[]
[null,"MANUALS / CATALOGUES, etc"]
[2,"Allow to supply four sets of Service"]
[null,"and Maintenance Manuals including"]
[null,"Technical Diagrams operating instructions"]
[null,"and Parts catalogues","No"]
[]
[null,"TESTING & COMMISSIONING OF"]
[null,"UPS INSTALLATION "]
[3,"Allow to test and commission the Installation as "]
[null,"per specification and handing over to the"]
[null," Department's Representative.","Item"]
[]
[null,"GUARANTEE AND MAINTENANCE"]
[4,"Guarantee and maintenance for the"]
[null,"complete installation including fittings,"]
[null,"fixtures, materials and workmanship for"]
[null,"a period of TWELVE MONTHS after date"]
[null,"of completion and handover.","Item"]
[]
[]
[]
[]
[]
[]
[null,"Carried to Collection Page",null,null,"R","."]
[]
[null,null,"UPS6/1"]
[null,"(NOTE:  THE RELEVANT DETAIL SPECIFICATION FOR THE UPS INSTALLATION HAS BEEN INCLUDED IN SECTION 1 : PART 3 : PARA 3.44 : PAGE E3/61)"]

{"sheet":"UPS Coll","index":21,"n_rows":56,"n_cols":4,"rows_kept":56,"flags":["formulas_cached_only"]}
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL NEW PSYCHIATRIC WARD"]
[]
[null,"UPS INSTALLATION (CPAP Work Group 160)"]
[]
[null,"COLLECTION PAGE"]
[]
[{"$nulls":3},"R"]
[]
[]
[null,"Brought forward from page","UPS6/1"]
{"$rows_empty":41}
[null,"Total Carried forward to Summary page  (ESP6)",null,"R"]
[]
[null,"UPS6/2"]

{"sheet":"BofQ DCS","index":22,"n_rows":162,"n_cols":6,"rows_kept":162,"flags":["formulas_cached_only"]}
[null,"PORT SHEPSTONE REGIONAL HOSPITAL   NEW PSYCHIATRIC WARD"]
[]
[null,"DATA/COMPUTER SYSTEMS INSTALLATION (CPAP Work Group No. 160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"NEW COMPUTER/DATA INSTALLATIONS"]
[null,"Allow to Supply and Install the Computer/Data"]
[null,"Equipment and Cabling as per the Data/Telephone "]
[null,"Drawings: SL  231 - TD1, TD2 and TD3 consisting"]
[null,"of the Parking Level, Ground Floor and First Floor "]
[null,"Levels respectively."]
[null,"Noted that the Telephone Layout is shown on the"]
[null,"same Drawings, due to Computer and Telephones "]
[null,"in most cases next to each other. The Telephone "]
[null,"outlets/Installations to be allowed sepeately as per "]
[null,"the dedicated Telephone Bills Of Quantities"]
[]
[null,"SITA Accreditation"]
[1,"Important to note that the Entire Computer/Data"]
[null,"Installations must be completed by a SITA "]
[null,"ie. State Information Technology Agency approved"]
[null,"Contractor. The contractor is to submit "]
[null,"Accreditation Details pior to commencement on "]
[null,"Site. Allowance in this regard.","Item"]
[]
[2,"The Main/Existing Computer Frame "]
[null,"Allow to Incorporate/Connect to the Existing Main"]
[null,"Computer Frame ie. MCF, situated in the Server "]
[null,"Room Located on the Lower Ground Level of the "]
[null,"Existing West Block. ","Item"]
[]
[3,"Reticulation Cabling"]
[null,"Allow to Supply and Install the Reticulation Cabling "]
[null,"between the MCF and the New Main Computer"]
[null,"Switch/Hub to be installed in the Server Room on"]
[null,"the First Floor of the New Psychiatric Building."]
[null,"The cables to consist of an armoured Fibre Optic "]
[null,"Cable, selected to accommodate the passage of  "]
[null,"Data between the Existing and New Facility"]
[null,"The Cables is to be routed via. Cable pipes/"]
[null,"Manholes, Cable Ladders and Conduits, as "]
[null,"indicated on the Site Plan drawing SL 231 - ESP1"]
[null,"Ensure that an additional cable is installed"]
[null," for future","m",460]
[]
[]
[]
[null,"Carried to Collection Page",null,null,"R","."]
[]
[null,null,"DCS6/1"]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL   NEW PSYCHIATRIC WARD"]
[null,"DATA/COMPUTER SYSTEMS INSTALLATION (CPAP Work Group No. 160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[1,"Building Switch/Hub Interconnection Cabling"]
[null,"Supply and Install Fibre Optic cable between the "]
[null,"Switch/Hub units indicated on Parking level, "]
[null,"Ground and First Floors: And the Main Core switch"]
[null,"for the New Psychiatric Ward facility installed by "]
[null,"IT Specialist into the Server room on 1st Floor","m",220]
[]
[2,"SFP CONVERTORS "]
[null,"Allow to Supply and Install SFP CONVERTORS for "]
[null,"Fibre Optic Cable terminations on IT Core Switches"]
[null,"and Patch Panels","No",20]
[]
[3,"THE MAIN CORE SWITCH"]
[null,"Supply and Install the Main Core Switch in the Main"]
[null,"Server Room on First Floor.The Switch is to be"]
[null,"installed in a Suitable metal IT cabinet fully ventilated"]
[null,"Fitted with Lockable Door. The switch to be served "]
[null,"with aprropriate Patch Panels and cords."]
[null,"The Core Switch to be Aruba 3610M 10SF CHM"]
[null,"c/o First Technology or equal and approved","No",1]
[]
[4,"New Edge Swithes/Hubs"]
[null,"Supply and Install New Edge Switches/Hubs and"]
[null,"appropriate Patch Panels in the postions Indicated "]
[null,"for the Security Desk and Associated Offices,"]
[null,"on the walls and Floors, and strictly as required"]
[null,"for all floor offices as indicated on the Computer/"]
[null,"Data drawings. Noted that the Edge Switches "]
[null,"are to be connected to the Main Core Switch via "]
[null,"Fibre Optic Cables as specified"]
[null,"The Edge Switches to be Aruba 2530-24G-POE+"]
[null,"VUWANI c/o First Technology or Equal and Approved","No ",8]
[]
[null,"LAN CABLING"]
[5,"Type Cat. 5E Enhanced Data Cable installed"]
[null,"in conduits / power skirting / trunking systems etc."]
[null,"for the connection of the Computer Stations","m",4050]
[]
[null,"NEW DESK TOP COMPUTERS"]
[6,"Supply and Install Desk Top Computers with "]
[null,"Screens and Mouses (on cords) to be Installed in"]
[null,"selected Departments including basic software "]
[null,"requirements. REFER SPECIFICATIONS","No",98]
[]
[]
[null,"Carried to Collection Page",null,null,"R","."]
[]
[null,null,"DCS6/2"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL   NEW PSYCHIATRIC WARD"]
[null,"DATA/COMPUTER SYSTEMS INSTALLATION (CPAP Work Group No. 160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[1,"PRINTERS"]
[null,"Allow to Supply and Install Laser Jet Printers, "]
[null,"including all connections, Loaded onto the IT "]
[null,"Computer Network as Specified","No",24]
[]
[2,"SOFTWARE "]
[null,"Allow to provide and Install Software for ancillary"]
[null,"Hardware in accordance with DOH requirements"]
[null,"and as required by Port Shepstone Hospital, "]
[null,"Generaly a printer for a cluster of computers.","Item"]
[]
[3,"COMPUTER OUTLETS"]
[null,"Single housings with type MPS modules with RJ45"]
[null,"socket outlets for connecting to computer "]
[null,"plug leads. Note that coverplates for Computer"]
[null,"Outlets in walls (28) and/or Powerskirting Runs"]
[null,"(70) have been allowed for and to be installed as"]
[null,"part of the General Electrical Installations","No",98]
[]
[4,"COMPUTER/PRINTER CONNECTIONS"]
[null,"3000mm long Fly leads for connecting to"]
[null,"computers with R145 connections both ends","No",98]
[]
[5,"CABLE TRAYS and BASKETS (Gridspans)"]
[null,"200mm Wide Galvanised Steel Cable Support "]
[null,"Baskets supplied and Installed specifically by "]
[null,"IT Specialist in False Ceiling Voids on Levels"]
[null,"or/as required. All components including hanging"]
[null," provisions, Bends, splicing etc.to be included","m",360]
[]
[6,"TESTING, COMMISSIONING OF ALL: incl.etc."]
[null,"COMPUTERS, DATA, CABLING INSTALLATIONS."]
[null,"Allow to test and commission the installation"]
[null,"as per specification and handing over to"]
[null,"Department's Representative","Item"]
[]
[7,"GUARANTEE AND MAINTENANCE"]
[null,"Guarantee and maintenance for the complete"]
[null,"installation, including fittings, fixtures,"]
[null,"materials and workmanship for a period of"]
[null,"TWELVE MONTHS after date of completion"]
[null,"and handover.","Item"]
[]
[null,"Carried to Collection Page",null,null,"R","."]
[]
[null,null,"DCS6/3"]
[]
[]
[]
[null,"(NOTE:  THE RELEVANT DETAIL SPECIFICATION FOR THE DATA CABLING SYSTEM INSTALLATION HAS BEEN INCLUDED IN SECTION 1 : PART 3 : PARA 3.44 : PAGE E3/61)"]

{"sheet":"DC Coll","index":23,"n_rows":53,"n_cols":4,"rows_kept":53,"flags":["formulas_cached_only"]}
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL NEW PSYCHIATRIC WARD"]
[]
[null,"DATA / COMPUTER INSTALLATIONS  (CPAP Work Group No.160)"]
[]
[null,"COLLECTION PAGE"]
[]
[]
[]
[{"$nulls":3},"R"]
[]
[]
[null,"Brought forward from page","DC6/1"]
[]
[]
[null,null,"DC6/2"]
[]
[]
[null,null,"DC6/3"]
{"$rows_empty":31}
[null,"Total Carried forward to Summary page  (ESP)",null,"R"]
[]
[null,"DC6/4"]

{"sheet":"BofQ S","index":24,"n_rows":103,"n_cols":6,"rows_kept":103,"flags":["formulas_cached_only"]}
[null,"PORT SHEPSTONE REGIONAL HOSPITAL   NEW PSYCHIATRIC WARD"]
[]
[null,"SECURITY INSTALLATION (CPAP Work Group No. 160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[null,"SECURITY INSTALLATION."]
[null,"Supply, delivery to site, installation, testing and"]
[null,"commissioning the Security Installations "]
[null,"for Doors in Passages as Indicated on the Layout "]
[null,"Drawings"]
[]
[1,"Main Security Control Panels","No",2]
[]
[2,"Transformer, Battery/ Battery Charger","No",2]
[]
[3,"Digital Key Pad Control Units","No",2]
[]
[4,"Security Type Latches for Doors","No",2]
[]
[5,"Magnetic Door Release Mechanisms","No",4]
[]
[6,"1,0mm² 4-pair Security Cable","m",64]
[]
[7,"OPERATING PROCEDURES"]
[null,"On site instructions given to responsible "]
[null,"personnel for the operation of the"]
[null,"Security Installation","Item"]
[]
[8,"SERVICE MANUALS"]
[null,"Complete sets of Service Manuals, Opera-"]
[null,"ting Instructions, Parts Lists and Cat.details","No",4]
[]
[9,"SUNDRY ITEMS"]
[null,"All sundry items required for the complete"]
[null,"supply and installation of the Security"]
[null,"Installations as specified.","Item"]
{"$rows_empty":11}
[null,"Carried to Collection Page",null,null,"R","."]
[]
[null,null,"S6/1"]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL   NEW PSYCHIATRIC WARD"]
[]
[null,"SECURITY INSTALLATION (CPAP Work Group No. 160)"]
[]
["ITEM","DESCRIPTION","No","QTY","RATE","AMOUNT"]
[]
[1,"TESTING AND COMMISSIONING"]
[null,"Allow to test and commission the install-"]
[null,"ation as per specification and handing"]
[null,"over to the Department.","Item"]
[]
[2,"GUARANTEE AND MAINTENANCE"]
[null,"Guarantee & maintenance for the complete"]
[null,"installation, including fittings, fixtures,"]
[null,"materials and workmanship for a period of"]
[null,"TWELVE MONTHS after date of completion"]
[null,"and handover.","Item"]
{"$rows_empty":29}
[null,"Carried to Collection Page",null,null,"R","."]
[]
[null,null,"S6/2"]
[]
[null,"(NOTE:  THE RELEVANT DETAIL SPECIFICATION FOR THE SECURITY INSTALLATION HAS BEEN INCLUDED IN SECTION 1 : PART 3 : PARA 3.44 : PAGE E3/61)"]

{"sheet":"SI Coll","index":25,"n_rows":50,"n_cols":4,"rows_kept":50,"flags":["formulas_cached_only"]}
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL NEW PSYCHIATRIC WARD"]
[]
[null,"SECURITY INSTALLATION (CPAP Work Group No.160)"]
[]
[null,"COLLECTION PAGE"]
[]
[]
[]
[{"$nulls":3},"R"]
[]
[]
[null,"Brought forward from page","S6/1"]
[]
[]
[null,null,"S6/2"]
{"$rows_empty":31}
[null,"Total Carried forward to Summary page  (ESP6)",null,"R"]
[]
[null,"S6/3"]

{"sheet":"FDE Bill1","index":26,"n_rows":352,"n_cols":6,"rows_kept":352,"flags":["formulas_cached_only"]}
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL     "]
[null,"NEW PSYCHIATRIC WARD"]
[]
[null,"FIRE DETECTION INSTALLATION"]
[]
["ITEM","  DESCRIPTION","UNIT","QTY","RATE","AMOUNT"]
[]
[null,"PREAMBLES"]
[null,"The following all to be visited and certified "]
[null,"in order to finally hand over to the Hospital"]
[null,"all as part of the NEW PSYCHIATRIC WARD"]
[null,"CONTRACT"]
[]
[1,"DEMONSTRATION OF WORK COMPLETED"]
[null,"Allow to demonstrate to a the Hospital Personnel and "]
[null,"Engineer the complete Installation"]
[null,"The costs to be allowed for shall include travelling and"]
[null,"time allocated for the inspection","Item"]
[]
[2,"GUARANTEE AND MAINTENANCE"]
[null,"Guarantee and maintenance for the complete installation "]
[null,"of the Fire Detection Installation including fittings"]
[null,"and materials, and workmanship for a period of "]
[null,"TWELVE MONTHS after date of completion and "]
[null,"handover all as part of the NEW PSYCHIATRIC WARD ","Item"]
[]
[3,"RETESTING & RECOMMISSIONING"]
[null,"Allow for retesting and recommissioning as may be "]
[null,"required specification, for retesting as may be required "]
[null,"after the making good of all defective work to the entire "]
[null,"satisfaction of the Department and Consulting Engineers.","Item"]
[]
[4,"AS BUILT DRAWINGS"]
[null,"Provision for the drawings showing all site cable routes,"]
[null,"conduit routes, drawboxes and positions of outlets, etc.","Item"]
[]
[5,"CERTIFICATE OF COMPLETION"]
[null,"Provision for the Final Certificates of Completion to be"]
[null,"issued on completion of the project for the general "]
[null,"Electrical Installation work.","Item"]
[]
[6,"MAINTENANCE MANUALS, ETC."]
[null,"Full sets of maintenance manuals, operating instructions,"]
[null,"schematic diagrams, parts lists and catalogue details","   No",4]
[]
[7,"TRAINING"]
[null,"Training of Operators and Technical Personnel in order "]
[null,"to operate the Fire Detection System, Fire Evacuation "]
[null,"System and P.A. System during Fire Alert and Fire"]
[null,"Fighting conditions \"and\" to understand the technical"]
[null,"requirements in order to carry out basic maintenance "]
[null,"and affect minor repairs on equipment.  It will be"]
[null,"expected to train at least two operators and two "]
[null,"technical personnel over a two-day period to ensure "]
[null,"that the hospital staff are fully conversant Including "]
[null,"signed and dated certificates as required","Item"]
{"$rows_empty":9}
[null,"Carried forward to Collection Page FDE6/8",null,null,"R"]
[]
[null,null,"FDE6/1"]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL     "]
[null,"NEW PSYCHIATRIC WARD"]
[]
[null,"FIRE DETECTION INSTALLATION"]
["ITEM","  DESCRIPTION","UNIT","QTY","RATE","AMOUNT"]
[null,"Generally the FIRE DETECTION SYSTEM TO BE "]
[null,"INSTALLED  is to be in addition, connected to the "]
[null,"existing Main Fire Panel in the Hospital 24Hour "]
[null,"Room. The additions are to be completely "]
[null,"compatible with the existing FIRE DETECTION"]
[null,"INSTALLATION "]
[null,"The specification for the additions to follow the"]
[null,"existing previously as follows:"]
[null,"For the complete supply of the equipment to site and "]
[null,"installation including testing, commissioning and "]
[null,"handing over in perfect working order of a complete"]
[null,"addressable, automatic fire detection and a very early "]
[null,"smoke detection system, complete with all equipment"]
[null," consisting of Main Fire Control Panel, Fire Brigade "]
[null,"Panel, Detectors, Manual Activated Resettable Fire"]
[null,"Alarm units, Sounders, Printers, Wiring, Cabling, etc."]
[null,"including all as provided for below"]
[]
[null,"24 Hour RECEPTION SECURITY STATION ROOM"]
[1,"The Main Fire Control Panel"]
[null,"To be noted that this was previously installed"]
[null,"The addressable Analogue type installation including "]
[null,"CPU and all the auxiliary provisions and equipment"]
[null,"extendable to 4 loops, upgradable to 8 loops, in order to"]
[null,"accommodate up to 24 zones, complete with Network"]
[null,"Cards, extrusion and communicating parts. Including "]
[null,"the full range of cable connecting leads provided.  "]
[null,"(At this stage 10 zones approx. being utilized)","NOTE"]
[]
[2,"Graphic Zone Annunciator Panel"]
[null,"To be noted that this was previously installed"]
[null,"Operating in conjunction with the Main Fire Detection"]
[null,"Control Panel including required interconnecting cable"]
[null,"link arrangements.","NOTE"]
[]
[3,"Fire Brigade Panel"]
[null,"To be noted that this was previously installed"]
[null,"into the Security Entrance Building off Colley Str."]
[null,"Complete with LCD display to enable communication"]
[null,"between the installed Fire Detection System and Fire"]
[null,"Brigade communication signal device equipment "]
[null,"including cable connections including Radio Transmitter "]
[null,"& Receiver and link to the Fire Department.","NOTE"]
[]
[4,"Power Supply Module - 5 kVA UPS"]
[null,"To be noted that this was previously installed"]
[null,"For dedicated Mains at required voltage and rated "]
[null,"current (230 Volt to 24 VDC) for the Fire Detection "]
[null,"System and cabling, including Power Pack with "]
[null,"Batteries and Battery charger.","NOTE"]
[]
[5,"FIELD PANELS AND DEVICES FOR THE FIRE"]
[null,"DETECTION SYSTEM"]
[null,"To be noted that this was previously installed"]
[null,"Analogue addressable detectors and additional"]
[null,"Devices as specified.","NOTE"]
[]
[6,"Additional Remote Graphic Zone Annunciator"]
[null,"To be noted that this was previously installed"]
[null,"For installation into the Security Guard House","NOTE"]
[]
[]
[null,"Carried forward to Collection Page FDE/8",null,null,"R"]
[]
[null,null,"FDE6/2"]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL     "]
[null,"NEW PSYCHIATRIC WARD"]
[]
[null,"FIRE DETECTION INSTALLATION"]
[]
["ITEM","  DESCRIPTION"," UNIT   ","QTY","RATE"," AMOUNT"]
[null,"NOTE : The following is all New and is to"]
[null,"be SUPPLIED and INSTALLED all as "]
[null,"an integral part of This NEW PSYCHIATRIC "]
[null,"WARD CONTRACT"]
[]
[1,"New Main  Fire Control Panel"]
[null,"To be Installed against the Wall in the Security "]
[null,"Office situated on the First Floor of the building"]
[null,"New Addressable Analogue type Panel and associated"]
[null,"installation including CPU and all the auxiliary provisions "]
[null,"and equipment extendable to 4 loops, in order to"]
[null,"accommodate the envisaged 6 zones, the Panel"]
[null,"complete with Network Cards, extrusion and "]
[null,"communicating parts, including the full range"]
[null,"of cable connecting leads provided. The Panel is to "]
[null,"accommodate all the Fire Detection Devices, the "]
[null,"Fire Addressable Points, the Fire Signal to the Fire "]
[null,"Brigade Panel (Situated in the Security Entrance "]
[null,"Building off Colley Street) Important to note that the "]
[null,"Control/Shut Down of Air Handling Units Installed in the "]
[null,"First Floor Plant room are to be Addressable from the "]
[null,"corresponding Devices specifically indicated for the "]
[null,"each separate Zone, and including the Lift Emergency "]
[null,"Signal ","Item"]
[]
[2,"Graphic Zone Annunciator Panel"]
[null,"New Annunciator Panel installed as an Integral part and "]
[null,"Operating in conjunction with the Main Fire Detection"]
[null,"Control Panel including required interconnecting cable"]
[null,"link arrangements.","Item"]
[]
[3,"Microphone /Amplifier Zone Units"]
[null,"Supply and Install at each Main Station on each of the "]
[null,"3 Levels in the positions indicated on the Fire Layout"]
[null,"Drawings  SL 231 - FE1, FE2 and FE3 Control Stations "]
[null,"consisting of Flush mounted Enclosures containing a "]
[null,"Microphone Amplifier combination Unit consisting of a"]
[null,"Main Fire Telephone and Microphone to Communicate"]
[null,"related Fire Control Measures","No",6]
[]
[4,"NEW Illuminated Block Diagrams"]
[null,"Block Diagrams to be inserted in 600x600x74mm"]
[null,"30W LED Panels Enlite Cat No EN-FPR06060  "]
[null,"Surface Aluminium Enclosure mounted in a Surface  "]
[null,"mounted Box Kit Enlite Cat No.EN-SM103B or Similar and "]
[null,"Equal Enclosure type, complete with a DOUBLE "]
[null,"POLYCARBONATE  front Diffusers to enable the"]
[null,"insertion of the applicable Zone/Floor Layout Drawing"]
[null,"(Refer Layout Dwgs - 6 zones)","No",6]
[]
[5,"Ionisation Detectors"]
[null,"Analogue addressable Ionisation Detectors"]
[null,"indicating LED's complete with base and mounting"]
[null,"provisions as required.   "," No",9]
[]
[6,"Optical Detectors"]
[null,"Analogue addressable Optical Detectors including"]
[null,"indicating LED's complete with base and mounting"]
[null,"provisions as required. ","   No",230]
[]
[]
[null,"Carried forward to Collection Page FDE6/8",null,null,"R"]
[]
[null,null,"FDE6/3"]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL     "]
[null,"NEW PSYCHIATRIC WARD"]
[]
[null,"FIRE DETECTION INSTALLATION"]
[]
["ITEM","  DESCRIPTION"," UNIT    ","QTY","RATE"," AMOUNT"]
[]
[1,"Heat Detectors"]
[null,"Analogue addressable heat detectors including"]
[null,"Indicating LED's complete with base & mounting "]
[null,"provisions as required","No",33]
[]
[2,"Optical Detectors installed on Ceilings and "]
[null,"and Concrete Slabs","  No",52]
[]
[3,"Remote indicating LED's for Detectors"]
[null,"Installed in concealed spaces incl. suspended "]
[null,"ceilings etc.","No",52]
[]
[2,"Ionisation Detectors (in Roof Spaces and "]
[null,"Machine Rooms","  No",20]
[]
[3,"Remote indicating LED's for Detectors"]
[null,"Installed in concealed spaces incl. suspended "]
[null,"ceilings etc.","No",15]
[]
[4,"Manual Fire Alarm Units"]
[null,"Manual activated resettable wall mounted Fire"," No",50]
[null,"Alarm Units"]
[]
[5,"Electronic Audible Sounders"]
[null,"Installed in positions shown complete with all "]
[null,"provisions for mounting onto outlet boxes at high"]
[null,"level including interface units.","  No",9]
[]
[6,"Magnetic Door Control Devices"]
[null,"Installed in positions shown complete with all "]
[null,"provisions for mounting onto outlet boxes in"]
[null,"positions to Control Doors","  No",6]
[]
[7,"Speakers"]
[null,"Loudspeakers install on ceilings in suitable enclosures","No",16]
[null,"as indicated on the layout Drawings"]
[]
[8,"Visible Alarms"]
[null,"Complete with flashing \"Red\" strobe lights /speaker"]
[null,"combination units installed in positions throughout "]
[null,"the buildings, shown complete with all provisions"]
[null,"for mounting onto outlet boxes at high level.","  No",5]
[" "]
[9,"Power Supply Units"]
[null,"Including 230V AC / 24V DC Transformers/"]
[null,"Rectifiers with backup for zone power supplies"," No",3]
[]
[10,"Loop Isolators"]
[null,"Installed for each zone in position as shown"]
[null,"adjacent to Fire Draw boxes as indicated for "]
[null,"connection of each loop including LED indicating "]
[null,"device. Connecting to Air Handling Panels, Lift Panel,"]
[null,"equipment in Distribution Boards and Fire Control Panels"]
[null,"as required.","No ",34]
[]
[]
[]
[]
[]
[null,"Carried forward to Collection Page FDE6/8",null,null,"R"]
[]
[null,null,"FDE6/4"]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL     "]
[null,"NEW PSYCHIATRIC WARD"]
[]
[null,"FIRE DETECTION INSTALLATION"]
[]
["ITEM","  DESCRIPTION"," UNIT    ","QTY","RATE"," AMOUNT"]
[]
[null,"FIRE DETECTION, CABLE AND CONDUIT,"]
[null,"WIRE WAYS, ETC., INSTALLATION WORK"]
[null,"Installation work associated with the Fire"]
[null,"Detection System."]
[null,"Note: The Supply & Installation of the Control"]
[null,"Equipment in the Main Control Room and Guard"]
[null,"House part of the items previously referred."]
[]
[null,"FIRE RATED CABLES / CONDUCTORS"]
[]
[1,"2,5mm² PH120 fire detection/ fire resistant cable for"]
[null,"device loops installed in trunking or conduit.","m",2880]
[]
[2,"2,5mm² Four Core PH120 Fire rated armoured Control"]
[null,"Cable installed via conduits, on cable trays, cable pipes, "]
[null,"Service Tunnel and Existing Ceilings to be Connected to "]
[null,"The Existing Main Panel in the 24Hr Room off Bazley "]
[null,"Street and Emergency Standby Set Panel","m",360]
[]
[3,"Fire Rated Junction and Conduit Draw Boxes"]
[null,"RED Fire Rated Drawboxes and pullboxes including"]
[null,"locknuts, bushes, glands, coverplates, fixing "]
[null,"materials when required.","No",6]
[]
[4,"Fire Cable Inspection Enclosure (FCIE)"]
[null,"RED 350 x 250 x 120mm Junction box with hinged ","No",6]
[null,"door - lockable   "]
[]
[5,"RED Fire Cable Inspection Enclosure (FCIE)"]
[null,"100 x 100 x 50mm Flush box","  No",8]
[]
[6,"RED Fire Cable Inspection Enclosure (FCIE)"]
[null,"100 x 50 x 50mm Flush box with Coverplate for each of "]
[null,"LOOP ISOLATORS for Air Handling Units ","No",16]
[]
[]
[null,"Note:"]
[null,"Allow to identify each of the below and receive "]
[null,"same from the Electrical Contractor"]
[]
[7,"Conduit Runs"]
[null,"Installed in concrete, cast into brickwork, cut into"]
[null,"brickwork, installed in roof spaces; including "]
[null,"terminations on to draw boxes, couplings, tees,"]
[null,"saddles etc. (Note: Included in Bills of Quantities "]
[null,"under the \"General Electrical Installation)","Item"]
[]
[8,"Conduit Boxes"]
[null,"Round 75mm dia. galvanised steel conduit boxes "]
[null,"been included with Bills of Quantities under the ","Item"]
[null,"General Electrical Installation "]
[]
[9,"P2000 Unistrut Runs"]
[null,"P2000 Unistrut Runs for the Fire Detection & ","Item"]
[null,"Evacuation Installed as part of the General "]
[null,"Electrical Installations"]
[]
[]
[]
[]
[null,"Carried forward to Collection Page FDE6/8",null,null,"R"]
[]
[null,null,"FDE6/5"]

{"sheet":"FDE Bill2","index":27,"n_rows":139,"n_cols":6,"rows_kept":139,"flags":["formulas_cached_only"]}
[""]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL     "]
[null,"NEW PSYCHIATRIC WARD"]
[]
[null,"EVACUATION INSTALLATION"]
[]
["ITEM","  DESCRIPTION"," UNIT    ","QTY","RATE"," AMOUNT"]
[]
[null,"PREAMBLES"]
[null,"The Evacuation Installation consisting of "]
[null," \"RED\" FIRE TELEPHONE INSTALLATIONS"]
[null,"and EVACUATION SYSTEM INSTALLATION"]
[]
[null,"NOTED THAT THE EVACUATION INSTALLATION ADDITIONS "]
[null,"TO BE INTERGRATED INTO THE EXISTING INSTALLED AT THE"]
[null,"HOSPITAL and that all the ADDITIONAL EQUIPMENT IS TO BE "]
[null,"COMPLETELY COMPATIBLE WITH EXISTING"]
[]
[null," \"RED\" FIRE TELEPHONE INSTALLATION"]
[]
[1,"GUARANTEE AND MAINTENANCE"]
[null,"Guarantee and maintenance for the complete installation of"]
[null,"the Evacuation Installation including fittings, materials"]
[null,"and workmanship for a period of TWELVE MONTHS after"]
[null,"date of completion and handover","Item"]
[]
[2,"RETESTING & RECOMMISSIONING"]
[null,"Allow for retesting and recommissioning  and"]
[null,"making good of all defective work to the entire satisfaction"]
[null,"of the Department and Consulting Engineers.","Item"]
[]
[3,"AS BUILT DRAWINGS"]
[null,"Provision for the drawings showing all site cable routes,"]
[null,"conduit routes, drawboxes and positions of outlets, etc.","Item"]
[]
[4,"CERTIFICATE OF COMPLETION"]
[null,"Provision for the Certificate of Completion to be issued"]
[null,"on completion of the project for the general Electrical"]
[null,"Installation work.","Item"]
[]
[5,"MAINTENANCE MANUALS, ETC."]
[null,"Full sets of maintenance manuals, operating instructions,"]
[null,"schematic diagrams, parts lists and catalogue details.","   No",4]
[]
[null,"TRAINING"]
[null,"Note: The training of the Fire Telephone Installation is to be","Note"]
[null,"included as an integral part of the Fire Detection System."]
{"$rows_empty":20}
[null,"Carried to Collection Page (FDE6/8)",null,null,"R"]
[]
[null,"FDE6/6"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL     "]
[null,"NEW PSYCHIATRIC WARD"]
[]
[null,"EVACUATION INSTALLATION"]
[]
["ITEM","  DESCRIPTION"," UNIT    ","QTY","RATE","AMOUNT"]
[]
[null,"The FIRE and EVACUATION Installations"]
[1,"Supply and Installation for the complete Installation on site"]
[null,"including testing, commissioning and handing over in perfect"]
[null,"working order of complete Evacuation System,"]
[null,"consisting of a Main \"Fire\" Telephone System and"]
[null,"an Evacuation System to the Main Fire Telephone installed "]
[null,"in the Main Security Control office and wall mounted fire telephones "]
[null,"for each zone and the Evacuation System. All connected to  "]
[null,"Main Control Panel and including the Zone Selector Panel,  "]
[null,"Including Micro-phones to the Main Control office and"]
[null,"Evacuation Loudspeakers indicated on the layout Drawings"]
[null,"and finally hand over finally as part of the "]
[null,"New PSYCHIATRIC WARD CONTRACT","Item"]
[]
[null,"FIELD PANELS AND DEVICES FOR THE"]
[null,"EVACUATION INSTALLATION"]
[]
[null,"SUB FIRE STATION ENCLOSURES"]
[null,"(Refer to positions indicated on Dwgs"]
[]
[2,"Red\" Zone Fire Telephone"]
[null,"Handset complete as specified.","No",10]
[]
[3,"Microphone Handset with Amplifier"]
[null,"To drive local zone speakers as specified.","No",10]
[]
[4,"Sub Fire Station Zone"]
[null,"Fire Rated Enclosures for \"Fire Telephone Handset\" and"]
[null,"Evacuation Microphone Handset/Amplifier as specified.","No",10]
[]
[null,"EVACUATION LOUDSPEAKERS"]
[null,"Internal"]
[5,"Allow to Supply and Install Fire Evacuation Loudspeakers in ","No",22]
[null,"positions indicated on the Layout Drawings, Fire Rated to SANS Code"]
[null,"External"]
[6,"Fire Rated to SANS Code, including local and booster amplifiers "]
[null,"consisting of Surface Horn type."," No",6]
[]
[7,"CONDUIT"]
[null,"Conduits placed in position for fixing on brickwork or concrete"]
[null,"including jointing, draw boxes, coupling, tees and/or"]
[null,"saddles. Allowed under Electrical Installation. Allow to identify and ","Item"]
[null,"receive same to successfully complete the works."]
[]
[null,"CABLE"]
[8,"2,5mm² PH120 Fire Rated Cabling (4- pair) for individual  loops"]
[null,"to Fire Telephones, between microphones, loudspeakers "]
[null,"and control panel, installed in conduit/ trunking runs, etc. ","m",980]
[]
[9,"2,5mm² 3-core fire rated armoured cable installed on"]
[null,"cable trays, in trunking runs, conduit runs , cable pipes,etc"]
[null,"for connecting of the Emergency RED FIRE TELEPHONES to the"]
[null,"EXISTING MAIN PANEL in the 24Hr Room of Bazley Street"]
[null,"and including all Panels and outlets indicated on drawings"]
[null,"that require Fire Signals as indicated on the First Floor Machine Room  ","m",660]
[]
[]
[null,"Carried to Collection Page (FDE6/8)",null,null,"R"]
[]
[null,"FDE6/7"]

{"sheet":"Collect","index":28,"n_rows":68,"n_cols":10,"rows_kept":68,"flags":["formulas_cached_only"]}
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL     "]
[null,"NEW PSYCHIATRIC WARD"]
[]
[]
[null,"FIRE DETECTION AND EVACUATION INSTALLATION"]
[null,"(CPAP Work Group No. 160)"]
[]
[]
[]
[]
[{"$nulls":5},"COLLECTION PAGE"]
[]
[]
[]
[]
[]
[{"$nulls":7},"AMOUNT",null,"AMOUNT"]
[null,"FIRE DETECTION",{"$nulls":5},"R"]
[]
["                                                                                                                                                                            ","Total brought forward from pages",{"$nulls":3},"FDE6/1"]
[]
[{"$nulls":5},"FDE6/2"]
[]
[{"$nulls":5},"FDE6/3"]
[]
[{"$nulls":5},"FDE6/4"]
[]
[{"$nulls":5},"FDE6/5"]
[]
[]
[{"$nulls":5},"SUB TOTAL",null,null,"R"]
[]
[]
[]
[]
[]
[null,"EVACUATION INSTALLATION"]
[]
[null,"Total brought forward from pages",{"$nulls":3},"FDE6/6"]
[]
[{"$nulls":5},"FDE6/7"]
{"$rows_empty":8}
[{"$nulls":5},"SUB TOTAL",null,null,"R"]
{"$rows_empty":10}
[null,"TOTAL BILLS NOS.11.1 & 11.2 CARRIED TO SUMMARY PAGE  (ESP)",{"$nulls":6},"R"]
[]
[]
[]
[]
[]
[{"$nulls":5},"FDE6/8"]

{"sheet":"FINAL SUMMARY","index":29,"n_rows":53,"n_cols":4,"rows_kept":53,"flags":["formulas_cached_only"]}
[]
[]
[null,"ELECTRICAL INSTALLATION SECTION"]
[]
[]
[]
[null,"Total Amount brought forward from pages"]
[null,null,"PAGE","AMOUNT"]
[{"$nulls":3},"R"]
[null,"General Electrical Installation"]
[]
[]
[null,"Provisional Sum","PS6/2","40 000.00"]
[]
[null,"General Electrical Installation Work","E6/63"]
[]
[null,"Telephones Installation","TI/3"]
[]
[null,"Public Address Installation","PA6/3"]
[]
[null,"CCTV Installation","CCTV6/5"]
[]
[null,"Microphone and Speaker Installation","MS6/2"]
[]
[null,"Nurse Call Installation","NC6/3"]
[]
[null,"Television Installation","TV6/3"]
[]
[null,"Lightning Protection Installation","LP6/3"]
[]
[null,"UPS Installation","UPS/2"]
[]
[null,"Data/Computer and Cabling System Installation","DCS6/4"]
[]
[null,"Security Installation","S6/3"]
[]
[null,"Fire Detection & Evacuation Installation","FDE6/8"]
[]
[null,"Fire Pump Installation","E6/66"]
{"$rows_empty":8}
[null,"TOTAL FOR THE ELECTRICAL INSTALLATION","R"]
[null,"CARRIED TO Page FS  (EXCL.VAT)"]
[]
[]
[]
[null,"ESP6"]

{"sheet":"COLLECTION PAGES","index":30,"n_rows":710,"n_cols":4,"rows_kept":710,"flags":["formulas_cached_only"]}
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL NEW PSYCHIATRIC WARD"]
[]
[null,"ELECTRICAL INSTALLATIONS  (CPAP Work Group No. 160)"]
[]
[null,"PROVISIONAL SUM"]
[]
[null,"COLLECTION PAGE"]
[]
[""]
[]
[{"$nulls":3},"AMOUNT"]
[]
[]
[null,"Total brought forward from pages","PS6/1",{"v":40000,"d":"R 40,000.00"}]
{"$rows_empty":29}
[null,"Total Carried forward to Summary page  (ESP)",null,{"v":40000,"d":"R 40,000.00"}]
[]
[null,null,"PS6/1"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL NEW PSYCHIATRIC WARD"]
[]
[null,"GENERAL ELECTRICAL INSTALLATION WORK (CPAP Work Group No.160)"]
[]
[null,"COLLECTION PAGE"]
[{"$nulls":3},"AMOUNT"]
[]
[]
[null,"Total brought forward from pages","E6/1"]
[null,null,"E6/2"]
[null,null,"E6/3"]
[null,null,"E6/4"]
[null,null,"E6/5"]
[null,null,"E6/6"]
[null,null,"E6/7"]
[null,null,"E6/8"]
[null,null,"E6/9"]
[null,null,"E6/10"]
[null,null,"E6/11"]
[null,null,"E6/12"]
[null,null,"E6/13"]
[null,null,"E6/14"]
[null,null,"E6/15"]
[null,null,"E6/16"]
[null,null,"E6/17"]
[null,null,"E6/18"]
[null,null,"E6/19"]
[null,null,"E6/20"]
[null,null,"E6/21"]
[null,null,"E6/22"]
[null,null,"E6/23"]
[null,null,"E6/24"]
[null,null,"E6/25"]
[null,null,"E6/26"]
[null,null,"E6/27"]
[null,null,"E6/28"]
[null,null,"E6/29"]
[null,null,"E6/30"]
{"$rows_empty":10}
[null,"CARRIED FORWARD TO FOLLOWING PAGE ","R"]
[]
[]
[null,null,"GE 1"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL NEW PSYCHIATRIC WARD"]
[]
[null,"ELECTRICAL INSTALLATIONS  (CPAP Work Group No. 160)"]
[]
[null,"COLLECTION PAGE (cont.)"]
[{"$nulls":3},"AMOUNT"]
[]
[null,"BROUGHT FORWARD FROM PAGE GE 1","R"]
[]
[]
[null,"Totals brought forward from pages","E6/31"]
[null,null,"E63/2"]
[null,null,"E6/33"]
[null,null,"E6/34"]
[null,null,"E6/35"]
[null,null,"E6/36"]
[null,null,"E6/37"]
[null,null,"E6/38"]
[null,null,"E6/39"]
[null,null,"E6/40"]
[null,null,"E6/41"]
[null,null,"E6/42"]
[null,null,"E6/43"]
[null,null,"E6/44"]
[null,null,"E6/45"]
[null,null,"E6/46"]
[null,null,"E6/47"]
[null,null,"E6/48"]
[null,null,"E6/49"]
[null,null,"E6/50"]
[null,null,"E6/51"]
[null,null,"E6/52"]
[null,null,"E6/53"]
[null,null,"E6/54"]
[null,null,"E6/55"]
[null,null,"E6/56"]
[null,null,"E6/57"]
[null,null,"E6/58"]
[null,null,"E6/59"]
[null,null,"E6/60"]
[null,null,"E6/61"]
[]
[]
[]
[]
[null,"Total Carried forward to Summary page  (ESP6)",null,"R"]
[]
[]
[]
[null,null,"GE 2"]
[]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL NEW PSYCHIATRIC WARD"]
[]
[null,"TELEPHONE INSTALLATIONS  (CPAP Work Group No. 160)"]
[]
[null,"COLLECTION PAGE"]
[]
[""]
[]
[]
[]
[]
[null,"Total brought forward from pages","T6/1"]
[]
[]
[null,null,"T6/2"]
{"$rows_empty":36}
[null,"Total Carried forward to Summary page  (ESP6)"]
[]
[null,null,"T6/3"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL NEW PSYCHIATRIC WARD"]
[]
[null,"PUBLIC ADDRESS INSTALLATIONS (CPAP Work Group No. 160)"]
[]
[null,"COLLECTION PAGE"]
[]
[]
[]
[null,"Total brought forward from pages","PA6/1"]
[]
[]
[null,null,"PA6/2"]
{"$rows_empty":38}
[null,"Total Carried forward to Summary page  (ESP6)"]
[null,null,0]
[]
[null,null,"PA6/3"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL NEW PSYCHIATRIC WARD"]
[]
[null,"LIGHTNING PROTECTION INSTALLATION (CPAP Work Group No. 160)"]
[]
[null,"COLLECTION PAGE"]
[]
[]
[]
[]
[null,"Total brought forward from pages","LP6/1"]
[]
[]
[null,null,"LP6/2"]
{"$rows_empty":37}
[null,"Total Carried forward to Summary page  (ESP)"]
[]
[null,null,"LP6/3"]
[]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL NEW PSYCHIATRIC WARD"]
[]
[null,"UPS INSTALLATION (CPAP Work Group 160)"]
[]
[null,"COLLECTION PAGE"]
[]
[{"$nulls":3},"R"]
[]
[]
[null,"Brought forward from page","UPS6/1"]
{"$rows_empty":41}
[null,"Total Carried forward to Summary page  (ESP6)",null,"R"]
[]
[null,"UPS6/2"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL NEW PSYCHIATRIC WARD"]
[]
[null,"MICROPHONE AND SPEAKER INSTALLATIONS"]
[]
[null,"COLLECTION PAGE"]
[]
[]
[]
[{"$nulls":3},"R"]
[]
[]
[null,"Brought forward from page","MS6/1"]
{"$rows_empty":40}
[null,"Total Carried forward to Summary page  (ESP6)",null,"R"]
[]
[]
[null,"MS6/2"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL NEW PSYCHIATRIC WARD"]
[]
[null,"SECURITY INSTALLATION (CPAP Work Group No.160)"]
[]
[null,"COLLECTION PAGE"]
[]
[]
[]
[{"$nulls":3},"R"]
[]
[]
[null,"Brought forward from page","S6/1"]
[]
[]
[null,null,"S6/2"]
{"$rows_empty":31}
[null,"Total Carried forward to Summary page  (ESP6)",null,"R"]
[]
[null,"S6/3"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL NEW PSYCHIATRIC WARD"]
[]
[null,"CCTV INSTALLATIONS (CPAP Work Group No.160)"]
[]
[null,"COLLECTION PAGE"]
[]
[]
[]
[{"$nulls":3},"R"]
[]
[]
[null,"Brought forward from page","CCTV6/1"]
[]
[]
[null,null,"CCTV6/2"]
[]
[]
[null,null,"CCTV6/3"]
[]
[]
[null,null,"CCTV6/4"]
{"$rows_empty":32}
[null,"Total Carried forward to Summary page  (ESP6)",null,"R"]
[]
[null,"CCTV6/5"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL NEW PSYCHIATRIC WARD"]
[]
[null,"TV INSTALLATION  (CPAP Work Group No.160)"]
[]
[null,"COLLECTION PAGE"]
[]
[]
[]
[{"$nulls":3},"R"]
[]
[]
[null,"Brought forward from page","TV6/1"]
[]
[]
[null,null,"TV6/2"]
{"$rows_empty":37}
[null,"Total Carried forward to Summary page  (ESP6)",null,"R"]
[]
[null,"TV6/3"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL NEW PSYCHIATRIC WARD"]
[]
[null,"NURSE CALL INSTALLATION  (CPAP Work Group No.160)"]
[]
[null,"COLLECTION PAGE"]
[]
[]
[]
[{"$nulls":3},"R"]
[]
[]
[null,"Brought forward from page","NC6/1"]
[]
[]
[null,null,"NC6/2"]
{"$rows_empty":33}
[null,"Total Carried forward to Summary page  (ESP)",null,"R"]
[]
[null,"NC6/3"]
[]
[]
[null,"PORT SHEPSTONE REGIONAL HOSPITAL NEW PSYCHIATRIC WARD"]
[]
[null,"DATA / COMPUTER INSTALLATIONS  (CPAP Work Group No.160)"]
[]
[null,"COLLECTION PAGE"]
[]
[]
[]
[{"$nulls":3},"R"]
[]
[]
[null,"Brought forward from page","DC6/1"]
[]
[]
[null,null,"DC6/2"]
[]
[]
[null,null,"DC6/3"]
{"$rows_empty":31}
[null,"Total Carried forward to Summary page  (ESP)",null,"R"]
[]
[null,"DC6/4"]