TENDER NO: RW10396363/22

THE CONSTRUCTION OF REINFORCED AND PRECAST CONCRETE VALVE

CHAMBERS FOR THE UPGRADE OF THE HEADERS

AT LETHABO INTAKE STATION

# CIVIL TECHNICAL SPECIFICATION

- TECHNICAL SPECIFICATIONS

Rand Water Civil works Technical Specifications that shall apply to this contract are listed in this section.

It is worth noting that the Civil Technical Specifications listed in this section, applies to all concrete changes, unless stated otherwise in a particular subsection.

  - EXCAVATIONS AND EARTHWORKS

### Working in Roads

Before excavating the trench along or across any road the Contractor shall notify the property owners and the Engineer that the work is to be commenced and ascertain and comply with the conditions that have been imposed for working in or across the road.

The Contractor shall arrange the work to ensure a minimum of interruption to traffic and shall be liable for any injury to persons or animals and for any damage to property or things due to negligence on the part of the Contractor or his employees.

### Approval of Operations

Prior to the commencement of each section or type of excavation the Contractor shall submit to the Engineer for approval a detailed programme of operations, methods and plant to be used for executing that section or type of excavation, including details of dewatering, pumping, shoring, drilling patterns, etc.  The Engineer's approval will not be unreasonably withheld provided the method and equipment proposed can be expected to produce an acceptable end result and such approval shall not relieve the Contractor of his/her responsibilities for safety, programme or any other requirements of the contract.

The Contractor may use any method he chooses to excavate any class of material, but his/her chosen method of excavation shall not determine the classification of the excavation.  The Engineer will decide and approve the classification of the material to be excavated.

### Classification of Material

Material to be excavated shall be classified as follows:

Class B material shall be hard material and boulders greater than 1 m3 that, in the opinion of the Engineer, requires the use of explosives for its excavation.  Material that can be ripped by a Caterpillar D8'H' machine (or similar machine with a minimum mass of 35 000 kg and flywheel power in excess of 220 kW) fitted with a single tine rear mounted ripper suitable for heavy ripping or a back-acting excavator of flywheel power exceeding 0,20 kW for each millimetre of tined-bucket width will not be classified in this category.

Class A material shall be all material that is not classified by the Engineer as Class B material.

### Limits of Excavation

The bottom and sides of excavations in contact with concrete surfaces shall be finished sufficiently true to give the minimum thickness of concrete specified for the various structures.  These excavation surfaces shall be free from loose, soft or friable material.  No material shall remain within such lines.

### Excavations to Be Approved

In no case shall excavations be filled in or covered in any way until the excavated surfaces have been inspected and approved by the Engineer.

The Contractor shall advise the Engineer whenever the excavations are ready for inspection or whenever it is necessary to cover up the work.  In default of such notice the work so covered shall, on order of the Engineer, be uncovered by the Contractor and reinstated without extra charge.

### Excavation

Topsoil is defined for the purposes of this contract as the upper layer of soft material with a depth not exceeding 150 mm below the natural ground surface in which veld or cultivated grass is growing. Before proceeding with the bulk excavation the Contractor shall strip the topsoil over the area to be excavated plus a further width of 5m outside the payment lines. The use of rippers will not be permitted in Class A material.

Any excavation in material below or outside excavation profiles, (overbreak), for surfaces against which mass or reinforced concrete is to be placed shall be filled with suitable in-situ material to the general excavation profile.

### Trimming

Site or porous concrete shall be placed on a trimmed section in Class A material or backfill within 3 (three) days of achieving the final trim. Trimming to the excavation profiles shall be sufficiently true to give the minimum thickness of concrete specified for the various elements of the structures.  No material shall remain above or within the excavation profile.

Should the Contractor trim Class A material below or outside excavation profiles, (over excavation), in respect of surfaces against which geographic, piping, site, porous, mass or reinforced concrete is to be placed he shall fill in the volume so excavated with suitable material to a height 80 mm above the excavation profile compacted in horizontal layers not exceeding 150 mm finished thickness to 95% (ninety-five per cent) of the Modified AASHTO density at optimum moisture content and subsequently trim to the correct profile.

Alternatively the Contractor may, with the Engineer's permission, fill over-trimmed volumes by increasing the thickness of the porous concrete layer by up to 30 mm. Trench excavation shall be carried out in all materials between the subsoil surface or the natural ground surface and trench excavation profiles as determined from the drawings.

The drainage pipe trenches shall, except in restricted areas, be excavated by machine in combination with the use of explosives and mechanical breakers where necessary from top to bottom to the trench excavation profiles or as instructed by the Engineer except as otherwise determined by the Contractor.

The profiles of the side walls of trench excavations shall be the safe slope profiles determined by the Contractor.

The excavation surfaces on the floor of the trench which are to receive the pipe bed or pipe support cradle shall, after completion, be free from loose, soft or friable material and no material shall remain above or within the trench excavation profiles.

If the trench is dug to a depth in excess of that required, in Class A material (over excavation) or Class B material (overbreak), the Contractor shall backfill suitable material, in layers of not more than 200 mm finished thickness, and compact these layers to 93% (ninety-three per cent) Modified AASHTO density at optimum moisture content.

The drainage pipeline to be laid across any road designated as a "minor road" shall be installed in a trench of normal width and depth for the full width of the road in accordance with the details shown on the drawings.

Excavation of unsuitable foundation materials is defined, for the purposes of this contract, as the removal of in-situ materials at or below excavation profiles which, in the opinion of the Engineer, are unsuitable as foundation materials in terms of design requirements.

Unsuitable foundation materials will include Class A materials which have the potential for collapse or are unacceptably compressible or Class B materials which form local pinnacles or plateaux at or near the prescribed profiles whose presence will result in substantial differential settlements of the structure founded in part on Class A and in part on Class B materials.

Excavation of unsuitable foundation material shall be carried out below excavation profiles over the areas and to the depths instructed by the Engineer but not exceeding 1 m depth. The profiles of the sides of excavations carried out to remove unsuitable foundation materials shall be the safe slope profiles determined by the Contractor.

### Generally

The Contractor shall set out the excavations accurately in accordance with the drawings and data supplied by the Engineer.

The Contractor shall provide, erect, set to line and level and maintain approved substantial working profiles on the perimeter of excavations and along the length of the trench at changes of grade and direction.  Each working profile shall be fitted with a horizontal cross-bar set at a predetermined height above the designed excavation profiles to which excavations are to be carried out and have setting marks which will define the local setting out lines and the centre line of the trench.  Where required by the Engineer the Contractor shall provide a working profile with the cross-bar extending across the full width of the trench. A working profile shall remain in position during all stages of the excavations until the concrete is placed or the pipe is laid past the chainage of the working profile.

The Contractor shall provide sets of boning rods, templates and piano wire, for the sole use of the Engineer, for checking the profiles of the excavations.  The Contractor shall also provide, set and level all the pegs required to transfer lines and levels to the excavation floor in order to control the preparation of the prescribed profiles.

Excavation will be required to expose existing pipelines to allow the installation of the drainage line.  In exposing existing pipelines the Contractor shall excavate by machine, or by hand if necessary, around and under the pipelines taking care to avoid damage to the bitumen or cement mortar coated pipes.  Any damage caused to pipe coatings during excavations will be made good by Rand Water and any costs so incurred will be deducted from moneys due to the Contractor.

The Contractor shall provide and use equipment and machinery of adequate capacity and suitable type and quality for the efficient and expeditious execution of the work.

### Over-break and Over-excavation

It is to be expected that during excavations material will be removed from below the prescribed profiles.  In the cases where the excavation floor is formed of materials classified as Class B the additional depth will for purposes of this contract be termed over-break and can be expected to vary according to the nature of the rock, the jointing planes, the extent of weathering of the rock, the methods and procedures used in the blasting of the rock and the expertise of the personnel undertaking the blasting.  In the case where the excavation floor is formed in materials classified as Class A, the additional depth will for purposes of this contract be termed over excavation.

### Safety of Excavations

Excavations shall be undertaken in a safe manner in compliance with the regulations promulgated under the Occupational Health and Safety Act (Act 85 of 1993) or any amendment thereof.  Safety precautions to be observed by the Contractor shall include the sloping, stepping or benching or shoring, timbering or otherwise supporting the sides of the excavations or any other provision as stipulated in Regulation 11 of the aforesaid act, with which the Contractor declares himself to be conversant.

The shoring method adopted shall be compatible with the excavating, backfilling and construction method and shall not restrict the installation and construction. Shores shall be designed to withstand the earth pressures exerted upon them from the side of the excavation which shall include the superimposed loading of construction.

The Engineer may call upon the Contractor to timber the sides of the excavation at any point, without cost to Rand Water, which he may consider in any way dangerous.  Such timbering shall be left in place until the completion of the work at the point affected. Timbering shall consist of open planking, walings and substantial struts and shall be carried out in a workmanlike manner and to the satisfaction of the Engineer. The Contractor shall allow for the removal of timbering immediately prior to backfilling or on the instructions of the Engineer.

MAINTAINING THE SIDES OF THE EXCAVATIONS IN A SAFE CONDITION SHALL AT ALL TIMES BE THE SOLE RESPONSIBILITY OF THE CONTRACTOR. NO UNDER-CUTTING OF THE SIDES WILL BE ALLOWED

### Protection of Work

The Contractor shall provide, at his/her own expense, all measures necessary for the protection of the excavations during the progress of the work, and shall be solely responsible for securing, lighting and watching all places dangerous to traffic, persons, animals or property, and shall be liable for all claims arising therefrom.

The excavations shall be maintained until the structures are completed and backfilled.  Should the sides fall in or any debris or water accumulate in the excavations due to any cause the excavation shall be cleaned out and any damage arising therefrom made good by the Contractor at his/her own cost as directed by the Engineer.

### Depositing Spoil from Excavations

Spoil is defined for the purpose of this contract as material excavated from the works and is to be dealt with in accordance with the following:

Topsoil shall be deposited from the excavations and stockpiled separately in temporary stockpiles.  In order to conserve the bacteriological life in the topsoil the storage heaps, strips or layers shall not exceed 1,5m in total depth.

To the maximum extent possible all suitable materials excavated shall be used in the construction of the works. Such materials shall be selected from the unsuitable materials and stockpiled separately in temporary stockpiles on sites to be negotiated by the Contractor and approved by the Engineer.

Surplus spoil, rubble and debris from the excavations shall be loaded up and transported from the sites to a dumping site or sites, to be negotiated by the Contractor and approved by the Engineer, dumped, levelled and spread, all to the satisfaction of the Engineer. The frequency of the removal of rubble off site shall be, at minimum, as specified in the Environmental Management Plan.

No dumping site shall be used without the prior written approval of the Engineer and the owner of the property on which it is proposed to dump spoil.

The assessment of the quantity of suitable material to be stockpiled for filling shall be the responsibility of the Contractor entirely and any deficit shall be made good by the Contractor without cost to Rand Water.  The balance of the suitable material for filling which is assessed as surplus to the requirements of the work may be removed from the sites as excavations proceed.

No material shall be stockpiled in violation of any Statute or ordinance or to obstruct any watercourse or drainage channel.

In the case of trench excavations, the spoil bank shall be trimmed well back from the edge of the excavation so as to leave the minimum of 1,0 m clear between the edge of the spoil bank and the edge of the trench, provided that sufficient space is available on the opposite side of the trench for pipe laying purposes.  Where this is not the case, the spoil bank shall be a minimum of 7 m clear of the excavation.  The Contractor shall keep these strips clear of spoil at all times.

The top surface of all permanent spoil dumps shall be left smooth and even and side-slopes, where required, are to be stable for the material concerned.  Adequate drainage to the top surface and side-slopes shall be provided to prevent future erosion.

### Material for Filling

All material used in the filling beneath structures, behind walls, for formation of terraces and embankments and backfilling of pipes shall be suitable material as defined in the following clause.

Suitable material for filling beneath structures, behind walls, formation of terraces and embankments etc. and for stage II backfill in drain pipe trenches shall comprise loose, fine soil or powdered soft shales which on excavation, handling and compaction break down into a soil like texture and shall have the characteristics of a sandy silt or clayey sand material with a plasticity index not exceeding 15. The fill shall contain no ouklip or materials deleterious to concrete and shall be free of pebbles, stones and fragments of shattered rock with maximum dimensions exceeding 50 mm. The material used shall have a uniform moisture content and be free from roots and deleterious proportions of organic matter.  The material shall not be too wet for practical drying to the required moisture content. Alternatively, where instructed by the Engineer, loose fine soil with a plasticity index exceeding 15 shall be used as suitable material for filling beneath structures and behind walls in association with cement or lime stabilization.

Suitable material for drain pipe bed and for stage I backfilling in drain pipe trenches shall comprise loose, fine soil or powdered soft shales which on excavation, handling and compaction break down into a soil like texture and shall have the characteristics of a sandy silt or clayey sand material with a plasticity index not exceeding 15.  The fill shall contain no ouklip or materials deleterious to bitumen wrapped steel pipes and shall be free of pebbles, stones and fragments of shattered rock with maximum dimensions exceeding 10 mm. The material used shall have uniform moisture content and be free from roots and deleterious proportions of organic matter. The material shall not be too wet for practical drying to the required moisture content.

Suitable material for use in road sub-base and base layers in drainage pipeline trench at road crossings shall comprise selected graded crushed stone Class G1 as specified in terms of TRH14 - Guidelines for Road Construction Materials.

### Source of Materials

Unless authorized otherwise by the Engineer, suitable material shall be selected only from materials excavated under the contract.

If insufficient suitable material for filling is available for selection from the excavations the Contractor shall with the approval of the Engineer, supplement the available suitable material for filling by importing suitable material approved by the Engineer.  The Contractor shall negotiate for, obtain, load and transport to site the supplementary requirements for filling.

### Compaction of In-Situ Material

Where required, the in-situ material at the excavation profile or at the surface exposed after the removal of unsuitable foundation material shall be ripped to a depth of 150 mm and treated with 4% lime and 4% cement, and then compacted to 90% (ninety per cent) of the Modified AASHTO density below the exposed surface.

Compaction shall be carried out between optimum moisture content and optimum moisture content plus 2% (two per cent).  Density testing of the compacted in-situ material shall be carried out in accordance with these specifications.

Any wetting of the soil shall be done overnight before compaction to ensure even soaking of the soil.

### Filling

Filling Below Structures

The material used for filling below structures shall be suitable material in accordance with the approved construction drawings, project specifications and the geotechnical report recommendations.

After the excavation profile or the surface exposed after removal of unsuitable foundation material has been accepted in terms of Clause E8 and where required, in terms of Clause E16, the filling below structures may commence. All filling below structures shall be placed in 150 mm finished thickness layers compacted to 95% (ninety-five per cent) of the Modified AASHTO maximum dry density at moisture contents in the range between optimum moisture content and optimum moisture content plus 2% (two per cent). The filling shall be installed such that the final layer shall be at a level at least 80 mm above and subsequently trimmed back to the required profile.

Filling Behind Walls and Structures

The material used for filling behind walls and structures shall be suitable material in accordance with Clause E14. When the concrete in structures below natural ground surfaces has attained adequate strength the space between the concrete structures and the excavation face shall be filled in with suitable material.

The filling shall be compacted to a minimum of 90% (ninety per cent) of the Modified AASHTO density at optimum moisture content, as directed by the Engineer, in layers not exceeding 200 mm in thickness after compaction.  Compaction shall be carried out with mechanical rummers and vibrating rollers in a series of continuous operations over the full width of the layer concerned. Fill shall not be returned against the walls until permission has been obtained from the Engineer. The filling shall be taken up to natural ground surface or, where applicable, to the subsoil surface.

Filling In Trenches

The material used for filling below drain pipe bed shall be suitable material in accordance with Clause E14. The filling below pipe bed or pipe support cradle shall be placed in 200 mm finished thickness layers compacted to 90% (ninety per cent) of the Modified AASHTO maximum dry density at moisture contents in the range between optimum moisture content and optimum moisture content plus 2% (two per cent). The filling shall be installed such that the final layer shall be at a level at least 80 mm above and subsequently trimmed back to the trench excavation profile. The pipe bed and pipe support cradle shall be installed on the floor of the trench excavation profile in accordance with the details shown on the drawings.

As the valve chambers and other structures are completed the Contractor shall fill in the trench without delay either to the full extent or partially as and when directed by the Engineer in accordance with the details shown on the drawings. The earth filling under, around and over the pipe up to 300 mm above the pipe shall be of suitable Stage I material defined in Clause E14 material compacted by mechanical rummers in 150 mm finished thickness layers to 90% (ninety per cent) of Modified AASHTO density.

The remainder of the backfilling, to natural ground surface or the subsoil surface shall be suitable Stage II material as defined in Clause E14 placed in the trench in layers not greater than 300 mm finished thickness and compacted by mechanical rummers and vibrating rollers to 90% (ninety per cent) of Modified AASHTO density.

Filling in Trenches at Road Crossings

The material used for filling below drain pipe bed, under, around and over the pipe up to the subbase level specified on the drawings shall be of suitable Stage I material defined in Clause E14 material compacted by mechanical rammers in 150 mm finished thickness layers to 95% (ninety-five per cent) of Modified AASHTO density at optimum moisture content.

Filling Topsoil

After the backfilling of the excavations has been completed to the subsoil surface the topsoil shall be returned to the upper 300 mm layer from which it was removed to restore the natural ground surface.  The topsoil shall be evenly spread and lightly compacted to leave the upper ground surface in a neat and tidy condition as near as may be to the original condition encountered before excavation commenced or to such details for embankments as are indicated on the drawings.

Generally

Any surface on which a layer of filling is to be placed shall be clean, firm and suitable for the bonding of a successive layer of filling. If, in the opinion of the Engineer, the surface to receive any layer of filling is too smooth or dry to bond properly with the next layer, it shall be moistened and scarified to the satisfaction of the Engineer before the next layer is placed.

All suitable material for filling shall be brought within the required uniform moisture content range by methods approved by the Engineer.  The required moisture content range shall be determined by the Contractor. The filling of compacted material shall be carried out in horizontal layers of even thickness for the full area being refilled, or such portion of that area as the Engineer may approve, such that, after compaction, all intermediate completed layers are constructed to within a 30 mm tolerance of the thickness specified.

In order to ensure that the refilling is carried out in accordance with Clause E17 the Contractor shall establish levels, working profiles, lines, etc. for the use of the Engineer in checking the accuracy of the work and shall not proceed with the construction of successive layers until the Engineer has accepted the accuracy of the work and the degree of compaction achieved in the layer under construction.

Moisture/density tests on all compacted material below structures and behind walls shall be conducted by the Contractor.  Further density tests may be ordered by the Engineer.  Such tests shall be done in situ using the sand replacement method or by other approved methods.  All test results shall be submitted to the Engineer for approval. The crusher run fill shall be placed in the trench and compacted as required at the optimum moisture content.  The Contractor shall take all necessary measures to prevent drying out of the material prior to the completion of compaction.

Crusher Run Fill

Crusher run fill shall comprise a stable mixture of fragmented rock and fine binder material complying with the following grading requirements:

| Sieve size mm | Percentage passing |  |  |
| --- | --- | --- | --- |
| 26,5 | 100 |  |  |
| 19 | 85 | - | 95 |
| 13,2 | 71 | - | 84 |
| 4,75 | 42 | - | 60 |
| 2,0 | 27 | - | 45 |
| 0,425 | 13 | - | 27 |
| 0,075 | 5 | - | 12 |

The following indices and limits shall not be exceeded:

Maximum flake index: 35;

Atterberg limits: 25;

Plasticity index: 6 and

linear shrinkage: 3.

The crusher run fill shall be thoroughly mixed to provide a homogeneously graded material and the quantity of water to provide the optimum moisture content for compaction to the required density shall then be added and the material again thoroughly mixed.

### Testing of Placed Material and Material to Be Placed

- The Contractor is to identify a South African National Standards accredited laboratory for the intended use of testing soil material to be used in the works. The list of proposed accredited laboratories is to be presented to the Engineer for review and approval. The criteria of what tests are to be conducted are to be determined by the Engineer and communicated to the contractor.

### Hauling of materials

- All haul distances for the duration of construction shall be taken as Freehaul and the Contractor shall include all costs associated with this specification into their earthworks rates.

### Existing Structures

- All existing structures adjacent to where excavations are to be made, which may be affected by Construction operations (SANS 2001 and SANS 10400 shall apply), shall be adequately supported against collapse by the Contractor. Any repairs or replacements for the damage to or collapse of existing boundary walls (and the damage or collapse of other structures resulting from the damage or collapse of the boundary walls) shall be to borne by the Contractor.

### Shoring

- Due to space constraints the Contractor is expected to implement shoring to be able to achieve vertical excavations. The shoring design and construction will be undertaken by the geotechnical engineering under the employ of the Contractor, the go ahead for the construction will be sought from the Engineer

## CONCRETE, FORMWORK AND REINFORCEMENT

### Cement

The cement used for all portions of the structures (except where otherwise stated) shall be one of the following:

- A mixture in equal proportions by mass of Portland cement complying with SABS ENV 197 1   1992 and milled granulated blastfurnace slag ground to a fineness not less than 3 500 cm2/g and having a glass count not less than 95% (ninety five per cent) by mass.

- Portland cement complying with SABS ENV 197 1   1992.

- A mixture of approved proportions by mass of Portland cement complying with SABS ENV 197 1   1992 and pulverised fly ash from an approved source complying with ASTM C618.

If required by the Engineer, the Contractor shall provide certificates of tests showing that the cement on the site conforms with these Specifications and requirements.  All cement used on the work shall at all times be subject to the approval of the Engineer and any cement rejected shall be immediately removed from the site.

Aluminous cement shall not be used.

No cement from broken sacks shall be used on the works.  All cement spilled on the floors of the storage sheds shall be swept up weekly and removed from the works together with all broken sacks of cement.

### Fine Aggregate

Fine aggregate shall be clean, angular, sharp drift, pit or river sand entirely free from vegetable or any other foreign matter and shall be in accordance with SABS 1083 (latest edition).  It shall be screened and washed if directed by the Engineer.  No dump or crusher sand shall be used.

Samples of fine aggregate proposed to be used are to be submitted to and approved by the Engineer.

Fine aggregate shall be stored on a concrete surface and washed sand shall be allowed to drain for at least 24 (twenty four) hours before use.  The Engineer may require the Contractor to test the sand daily (or more frequently if necessary) for moisture content, impurities and grading before use.  Water demand shall not exceed 195 l/m3

### Coarse Aggregate

Coarse aggregate for concrete shall be hard, non-friable quartzite or other suitable rock, in accordance with SABS 1083 (latest edition) crushed and screened to the specified sizes, of good shape, clean and free from dust.

The maximum size of aggregate shall be 25 mm in floor and walls and 19 mm in roof slab.

Coarse aggregate containing more than 19% (nineteen per cent) shale will not be accepted.

Samples of coarse aggregate proposed to be used shall be submitted to and approved by the Engineer.  Any broken stone delivered to the site which contains 5% more flaky and/or 10% more elongated particles than the approved sample will be condemned and shall be removed from the site.  Voids ratio shall not exceed 47% (forty seven per cent).

### Water

The quantity of water used for concrete shall be carefully adjusted so that between the time that the concrete it is placed and worked into its final position and when it hardens.  The water shall be carefully measured so as to ensure the same quantity being used in each batch of concrete.  Sloppy or over wet concrete will be rejected and the quantity of water shall at all times be subject to regulation by the Engineer.

### Gauging and Proportioning

The material to be used for concrete shall be accurately gauged in correctly designed watertight gauging boxes so proportioned that the cement is measured by whole sacks; portions of sacks will not be allowed.

Gauging boxes shall be submitted to the Engineer for approval.

### Concrete Strength Requirements

The concrete mix for each portion of the work shall be specially designed by the Contractor to comply with the following requirements and shall be subject to the prior approval in writing of the Engineer:

- 15 MPa Concrete (Unreinforced)

The minimum works cube compressive strength shall be 15 MPa at 28 (twenty eight) days.

- 35 MPa Concrete (Reinforced)

The minimum works cube compressive strength shall be 35 MPa at 28 (twenty eight) days and the slump limits shall not be less than 30 mm nor more than 80 mm. . Xypex Admix C-500NF must be added to all 35 MPa structural concrete at a dosage of 4 kg/m3. Technical assistance, which is provided free of charge by the manufacturer, shall be utilised by the Contractor.

Concrete test cubes shall be taken for each pour of concrete.  The Contractor shall be responsible for the mixing, curing and testing of all cubes and shall submit test results from an approved laboratory. The number of tests to be conducted, as well as the test interval shall be as detailed under section 2.2.8 of this specification.

### Testing of Concrete

During the progress of construction, tests shall be made under the direction of the Engineer to determine whether the concrete being produced complies with the standards of quality, durability and strength specified. The Contractor shall be responsible for testing of concrete on site or an approved laboratory, as per instruction by the Engineer, and shall submit test results to the Engineer.

- Frequency

Unless otherwise directed by the Engineer, for each class of concrete, one sample shall be taken from each day's casting and one sample from at least every 50 m3 of each grade of concrete placed for the purpose of compressive strength testing. Only one sample shall be drawn from any one batch of concrete and no sample shall be taken of any grade until at least 3 batches of such grade have been mixed and discharged for that particular pour.

- Test Cubes and Cylinders

The Contractor shall prepare 6 test cubes, 150 mm nominal size, from each sample for compressive strength testing. Three of each set of six test cubes shall be tested at 7 days after making and the remaining three cubes at 28 days after making. The average of the results for three cubes will be taken as the test result.

The Contractor shall prepare 3 cylinders, 150 mm diameter by 300 mm long from each 500m3 of grade 30 concrete placed, in accordance with SABS Test Methods 861, 862 and 863, for the purpose of permeability tests. The cylinders shall be cured and stored in accordance with the requirements of the NBRI (National Building Research Institute).

- Compressive Strength Tests

If the tests disclose a consistent relationship between the 7-day and 28-day strengths of the concrete, the 7-day strength may be used as a basis for the assessment of the 28-day strength.  Both 7-day and 28-day strength tests shall be carried out regularly throughout the contract to provide a record of any seasonal variation in the relation between the 7-day and 28-day strengths.

Until such a relationship has been established on site the 28-day strength shall be taken to be not more than 1,67 times the 7-day test result in the case of ordinary Portland cement (and twice in the case of a mixture of ordinary Portland cement and milled granulated blast furnace slag or pulverized fuel ash).

If a 28-day strength assessed from a 7-day test result fails to meet the acceptance criteria for the concrete, the Contractor may at his/her discretion, demolish and re-construct at his/her own expense the volume of concrete affected; or, alternatively he/she may elect to extend the time for removal of formwork and/or curing.  The acceptance criteria for the concrete will be as specified and based on the 28-day test results.

- Acceptance criteria for concrete

If the average of the results of the tests on three test cubes from any sample of a specific class of concrete is more than 3 MPa below the specified 28-day works cube strength, then the concrete represented by such result/s will be deemed not to satisfy the requirements of the Specification.

The average of any 3 consecutive test results of a specific class of concrete shall exceed the specified 28-day works cube strength by at least 2 MPa.  If the average lies between the specified 28-day works cube strength and the specified strength plus 2 MPa, then the concrete represented by such results will be deemed not to satisfy the requirements of the Specification

The degree of control on the batching of concrete shall be such that the standard deviation of the most recent 30 of 30 or more test results (i.e. the average of 3 cubes each) does not exceed 5 MPa.

The average strength of the most recent 30 of 30 or more test results shall not be less than the specified strength plus 1,64 standard deviations.  If this average fails to meet this requirement, or if it becomes clear from plots of the moving average of 6 test results that this situation is approaching, the mix design shall be adjusted at the cost of the Contractor to ensure compliance with this criterion.

No more than 5 per cent of all test results shall exceed the specified strength plus 16,5 MPa. If these requirements are exceeded when considering the most recent 30 of 30 or more test results, the mix design shall be adjusted at the cost of the Contractor to ensure compliance. Alternatively, the Engineer may require that the area of reinforcement at any particular location in the structure be increased at the cost of the Contractor to control potential increased shrinkage cracking.

If cracking in excess of that permitted by BS 8007:1987 or any revision thereof occurs in any part of the structure where the concrete was found not to comply with standard deviation requirements and reinforcement had not been increased to minimise cracking, then the Contractor shall repair such cracks at his own expense to the satisfaction of the Engineer.

If the evaluation of test results indicates that the concrete represented by such  results does not satisfy the requirements of  the Specification, the Engineer in his sole discretion may adopt one or more of the following procedures in the sequence given to determine whether replacement or strengthening of the structure is necessary :-

- Non-destructive testing, subject to similar concrete of proven acceptable quality being available in comparable members in the same construction as a reference.  (Impact hammers and ultrasonic testing are two examples of such techniques which may be used provided that such apparatus has been previously calibrated.)

- The testing of drilled cores in accordance with current SANS standard methods.

Where cube test results shows the concrete strength to be unacceptable, or if a tested portion of the structure fails  to pass the tests, the Contractor shall, on  the instructions and directions of  the Engineer, either replace or strengthen by approved means :-

- each section that contains concrete that failed;

- any other section, the functional purpose of which is affected by the concrete that failed.

If on the basis of cube test results the concrete does not meet the requirements of the Specification, but non-destructive testing or testing of drilled cores shows that the concrete strength is acceptable : then if the Engineer shall be satisfied that the structural adequacy and durability of that part of the structure in which the concrete has been used is not seriously impaired, the concrete shall be deemed to be acceptable, but the mix design and other factors influencing the quality shall be reviewed in order to ensure that further concrete cast will meet the requirements of the Specification.

- Permeability Tests

The permeability coefficient of the test cylinders, as tested by the NBRI of the CSIR, shall not be greater than 5 × 10-7 mm/second. If the permeability coefficient exceeds this value, the Contractor shall show that the permeability of the concrete placed in the work complies with the Specification, failing which, the work will be rejected.

- Other Tests

The Contractor shall be responsible for conducting the following tests, at the instruction of the Engineer, and submit the results to the Engineer:

- apparent density

- UCS (Unconfined Compressive Strength)

- Phenolphthalein indicator (or Carbonation depth) test

- Cover test

- Durability tests: water sorptivity, oxygen permeability and chlorine conductivity

### Admixtures

Xypex Admix C-500NF miust be added to all 35MPa structural concrete at a dosage of 4 kg/m3. Technical assistance, which is provided free of charge by the manufacturer, shall be utilised by the Contractor.

### Mixing

Where no ready-mix concrete is used, mixing shall be done in a mechanical concrete mixer of approved design. Mixing of concrete shall comply with the requirements of SABS 1200 GB (clause 5.3.3).

### Placing Concrete

No concrete shall be mixed or ready-mix delivered until the foundations, ground water handling arrangements, reinforcement, joint treatment, clean up, formwork and concrete mixing procedure, handling and placing equipment have been approved by the Engineer.

Concrete shall be placed in position immediately after it is mixed and before any initial set has taken place.  Leavings shall not be used in any way but shall be discarded and immediately removed from the site.

Concrete shall be placed so as to prevent the separation of constituents and shall be thoroughly rammed and compacted while being placed.

Concrete shall surround the reinforcing bars completely.  The reinforcing bars shall not be displaced when depositing or ramming concrete.  While concrete is setting it shall not be disturbed or shaken and shall be kept saturated for 7 (seven) days after placing.

### Concrete during Cold Weather

During cold weather no material having a temperature below 5°C shall be used for making concrete.

No concrete shall be placed when the ground or air temperature is below 2°C or if the ground or air temperature is likely to fall below 2°C within 6 (six) hours after placing the concrete.

### Protection

Concrete shall be kept damp and protected against the action of sun, wind and frost by means of wet sacks, wet sand or other approved method, for at least 7 (seven) days after being placed in position.

### Finishing

Concrete shall be clean, hard, non-porous and entirely free from honeycombing. The Contractor shall cut away, remove and replace, without compensation, any concrete that is honeycombed or porous, or that the Engineer may consider in any way of inferior quality. All top surfaces of floors, slabs or beams shall be puddled until the fines rise to the surface.

### Construction Joints

All the construction joints are to be pre-molded with sealant and doweled. The isolation joints are to be pre-molded around the column stub, in a circular and diamond shaped manner, as per the engineering drawings.

Suitable openings shall be left in the shuttering temporarily to facilitate the removal of sawdust, shavings, nails, debris etc.

A grout made of 2:1 cement mortar shall be run along the joint as the new concrete is being placed.

The Tenderer shall include for the cost of shuttering, hacking and preparing all surfaces for construction joints in the schedule rates for concrete.

### Formwork

Correctly designed shuttering, centering, and casing, rigidly supported and braced, shall be erected.  Particular care shall be taken that no movement of the formwork takes place while the concrete is being placed in position or after it has been placed in position.

Forms shall be of good material of uniform thickness and width, strongly made and held in place by external bracing so that no distortion can occur.  The use of damaged forms is prohibited.

All clear-spanning beams and lintels shall have a camber of 6 mm to every 3 m of length.

Joints between forms shall be sufficiently tight to prevent leakage of fines and cement.  Forms shall be thoroughly cleaned down before they are re-used.

Formwork designs are to be undertaken by the Contractor and thereafter submitted to the Engineer for review and approval prior to the erection of formwork – the designs are to comply with all relevant SANS specifications. All formwork shall be approved by the Engineer before any concrete is placed.

Any runways required for the placing of concrete shall be so constructed as to be entirely independent and free from the concrete forms.

### Stripping Of Formwork

Formwork shall be removed carefully so as not to damage the concrete and the minimum periods during which formwork shall remain in position after concreting are:

| Sides of slabs Sides of Walls, Beams and Unloaded | - - | 24 (twenty-four) hours 4 (four) days |
| --- | --- | --- |
| Slab soffits | - | 10 (ten) days |
| Cantilever slab soffits | - | 15 (fifteen) days |
| Beam soffits: props left under | - | 7 (seven) days |
| Removal of beam props | - | 14 (fourteen) days |

The Engineer may order forms to be left in position for periods of at least 50% (fifty per cent) longer than those given above at no extra charge to Rand Water IF, IN HIS/HER DISCRETION, HE/SHE CONSIDERS THE WEATHER TO BE VERY COLD.

Stripping of formwork shall comply with the requirements of SABS 1200 G.

### Steel Reinforcement in Concrete

The bars for reinforcement shall be of high tensile and mild steel and shall conform in every respect to the latest appropriate standard specification; welded fabric shall be manufactured from high tensile steel wire.

All bars shall be clean and free from scale or grease and shall not be oiled or galvanised. The amount of rust shall be limited to 0.9% of the volume of a rust free bar, in addition all rebar shall be free of loose rust.

The size, length and bending of the reinforcement shall be strictly in accordance with the bending schedule and detail drawings supplied to the Contractor.  All bending shall be done cold.

### Placing Steel Reinforcement

The reinforcing bars shall be placed accurately in the exact positions shown on the detail drawings. The bars shall be wired together with 1,6 mm diameter black wire at every second point of intersection and shall be fixed so as to prevent any displacement during concreting.

All placing of reinforcement shall be done well in advance of the concrete and no concrete shall be placed until the reinforcement in position has been inspected and passed by the Engineer. The concrete cover shall be measured from the face of the concrete to the outside of main reinforcement nearest the face of the concrete and is exclusive of any plaster or finishing material.

The use of plastic spacer blocks will not be permitted.

### Inspection of Work

All erection of formwork, placing of reinforcement, chipping of concrete, etc. shall be completed by 15:00 on the afternoon proceeding the day on which it is proposed to cast concrete, to enable the Engineer to inspect the works during normal working hours.

The Engineer may increase this notice period up to 24 (twenty four) hours before concreting of work commences, where large sections of work are involved.

### Concrete Works

- All concrete to be finished to the specifications contained in this specification document, contract documents or drawings.

- All concrete mixes by the Contractor should comply with the minimum requirements set out in SANS 2001-CC1:2012.

- All concrete (preparation, deliver and or erection) is required to comply with the requirements of SANS 2001-CC1:2012

- All concrete to be 35 MPa cube strength at 28 days, unless specified otherwise on the construction drawings.

### Precast Concrete Valve Chambers (including roof slab)

The precast concrete roof shall be designed by a competent engineer – professionally registered Engineer (Pr. Eng.) or Engineering Technologist (Pr. Tech. Eng.) in the employ of the manufacturer of the precast roof – the liability of the design and construction will however rest with the Contractor. The Contractor is to issue, to the Engineer, a design file of the roof elements for the Engineer’s approval – prior to manufacture.

- The roof is to be designed to the requirements of SANS 10400 and should also meet the minimum requirements for Rand Water chambers

- The Contractor is made aware of the lead time of 21 calendar days required by the Engineer to review and provide feedback on the design to the Contractor. No manufacture may proceed without approval of the design by the Engineer.

## STRUCTURAL STEELWORK AND SUNDRY ITEMS

### General Requirements

The steelwork shall be supplied completed with plates, bolts, trimmers, etc., necessary for the completion of the contract.

### Sub-Contractors

The Contractor shall satisfy the Engineer that any proposed Sub-Contractors for e.g. fabrication, erection etc., have the necessary facilities to carry out the work to the standards and at the rate of progress required.

### Materials and Standards

All structural steel materials shall be new Grade S355JR, unless shown otherwise on the drawings. and shall be in accordance with SANS 1431. The Contractor shall, if necessary, satisfy the Engineer from his/her records that all materials meet the above requirements.

All structural steelwork to be hot dip galvanized to SABS 763 after fabrication. All bolts and fasteners shall be corrosion protection.

All bolts and nuts shall be of the class specified by in the construction drawings and shall be in accordance with the relevant SANS or ISO standards. Electrodes for welding shall comply with requirements of SANS 2001-CSI and SANS 10162: Part 1.

Stair treads and landings shall be Rectagrid open-grid flooring.

### Drawings

The Contractor shall prepare and submit a full set of fabrication drawings (workshop drawings) including the design of connections to the Engineer for approval prior to commissioning the manufacture of any structural steel elements.

The Contractor shall allow in his/her programme a period of two weeks for the approval of any drawing.

The final drawings shall be blackline unfolded, untearable, 0.075 mm thick transparency film, polyester base, matt finish on both sides, bearing Rand Water standard drawing title block. The size of the final drawings to be supplied shall comply with the ISO A series of drawing paper.

### Workmanship

Steelwork shall be of welded or bolted construction and shall comply with the requirements of SANS 10162. All steelwork welded or bolted together shall be in full contact over the whole of the meeting surfaces.

All welding shall be shielded metal arc welding (SMAW) complying with the requirements of SANS 2001-CSI and SANS 10162: Part 1. Highly skilled welders are required to execute all welding, under the most careful and expert supervision.

The prepared fusion faces of the weld shall be free from all irregularities, slag, oil, paint or any substance which may affect the quality of the weld. Components to be welded shall be securely held in their correct relative positions during welding and the welding sequence adopted shall be such that distortion is reduced to a minimum.

All connection shall develop the full strength of the members connected. Unless otherwise stated, the Contractor shall provide for suitable field connections that will, in his/her opinion, afford the greatest overall economy consistent with design requirements.

### Fabrication Tolerances

Completed members shall be free from twists, bends and open joints. Sharp kinks or bends shall be cause for rejection of material.

Straightness of compression members shall not deviate by more than 1/1000 of the axial length between points which are to be laterally supported.

A variation in length of not greater than 1 mm is permissible in the over a 1000 mm length of members with both ends finished for contact bearing. Members without ends finished for contact bearing, which are to be framed to other steel parts of the structure, may have a variation from the detailed length not greater than 2 mm for members 10 m or less in length and not greater than 3 mm for members over 10 m in length.

Open grid flooring shall be panels, either riveted or welded at each intersection and of approved type. The pattern of the grid is to be uniform and the flooring is to be secured to the supporting steelwork either by welding or with suitable clips and/or bolts, as directed. Securing clips must be of such design that they will still work under vibration of the structure. The bars forming the grid shall be straight, free from defects and set-square and/or parallel to each other.

The Engineer shall be advised as soon as the fabrication of steelwork is in hand so that he may inspect and examine the materials and workmanship during fabrication. The Engineer or his duly authorized representative shall have access to the Contractor’s premises for all reasonable times for the purpose of inspection.

### Protection of Steelwork

All steelwork shall be inspected at the maker’s works by Rand Water’s Inspector before shot-blasting, galvanizing or painting.

After inspection all fabricated steelwork shall be cleaned by steel shot-blasting to produce a matt surface of even texture, free from rust and scale and without sharp peaks of metal which may protrude through subsequent paint coatings. Preparation of steelwork shall be generally in accordance with SABS 064. Care shall be taken to remove all abrasive residues prior to priming.

All steelwork for internal stairs and ladders and handrailing shall be hot-dip galvanized to SANS 121 after fabrication. All bolts and fastenings shall be corrosion resistant.

Grating sump covers shall be hot-dipped galvanized after fabrication.

## Drawings and Information to be provided after acceptance of the Tender

All detail drawings, general arrangement drawings and details of the proposed shoring and dewatering of excavations, installation of chamber waterproofing ,etc. shall be subject to approval by the Engineer and shall be submitted for such approval as soon as possible after the contract has been placed.

Rand Water will not be responsible for any delays, loss or inconvenience to the Contractor through failure to comply with this requirement.

The Contractor shall prepare and submit to the Engineer for approval, all the necessary working and detail drawings and schedules of steel reinforcement to meet his approved progress schedule. The Contractor shall allow at least two weeks for approval by the Engineer of any drawings or schedule, and shall not be entitled to claim extra payment in respect of extra cost arising from delay in the approval of drawings or schedules.

Any delays due to subsequent modification of these drawings or schedules shall not be a cause for extending the time for completion of the contract; adequate notice of any modification shall be given by the Contractor to enable all necessary drawings and information to be produced and approved so that the work can proceed without delays.

The Contractor shall be responsible for any errors that may rise from any defects in the drawings supplied by him and for any loss, damage or expense sustained by Rand Water in making good such errors.

Final drawings shall be on unfolded, untearable transparent film, with a polyester base, having a matt finish on both sides and a thickness of 0.075 mm. These Drawings shall bear Rand Water’s contract number (i.e. RW01288/16). In addition where drawings have been completed using CAD programme, compact disc copies of each drawing shall be provided either on AUTOCAD or DXF format.

Drawings shall not be larger than size A0 in accordance with SANS 10111-2011. In all cases the drawing is to be in accordance with this standard.

## GENERAL REQUIREMENTS

### The Contractor may be required to support existing cables and other services on site during construction – to accommodate such services during excavation activities. The costs associated with such work (as well as the design and erection of necessary temporary works) shall be deemed to be included in the rates for excavation works.

### The Contractor is required to comply with the requirements of the Occupational Health and Safety Act (latest amendment) and its accompanying Construction Regulations (latest amendment) – and is also required to prepare and submit all documents pertaining with the requirement of the said Act and regulations.

The Contractor’s attention is drawn to the following risks which may arise on site:

#### The presence of medium voltage cables within the anticipated working area of valve chambers.

#### Vertical excavations and excavations surface support required for the valve chambers.

#### Working at heights and deep excavations.

#### Potentially heaving soils and the use of cranes next to open excavations.

### The Contractor is required to accompany their priced documents with a proposed, high level, construction method statement, in line with Occupational Health and Safety, as well as, Construction Regulation standards. The method statement should include a programme highlighting the activities anticipated for the proposed works.

### The Contractor is required to issue to the Engineer, prior to the use of intended construction materials, test certificates issued by an accredited, independent testing authority (Accredited by the South African Bureau of Standards or other equivalent accreditation body) to confirm that the respective materials comply with the specified requirement, or a certificate by the patent holder or designer, certifying that the manufactured item complies in all respects with relevant product specifications.

### A Degree of Accuracy II shall be applicable to all structural works under this project.

### The Contractor’s Attention is drawn to the fact that this is a multi-disciplinary project and as such Construction work will require adequate integration.

### The Contractor shall make allowance in his tendered rates for hiring and keeping in his employ, for the duration of the construction activity, a Professional Registered Engineer (Pr. Eng.) to assist him with the design of any temporary works. The design of the works is to be issued to the engineer in design file for approval – the design of the works shall be deemed to be included in the tendered rates for formwork.

### The new Valve chambers are designed to be water tight and must be water tightness tested to the RW specification detailed below:

### For testing of liquid retention, the chamber should be cleaned and initially filled to the normal maximum level with the specified liquid (water) at a uniform rate of not greater than 2m (two meters) in 24 hours.

### When first filled, the liquid level should be maintained by the addition of further liquid for a stabilizing period while absorption and autogenous healing take place. The stabilizing period must be 21 days for the for the valve chamber design crack width of 0.2mm. After the stabilizing period the level of the liquid surface should be recorded at 24 hour intervals for a test period of 7 days. During the 7-day test period the total permissible drop in level, after allowing for evaporation and rainfall, should not exceed 1/500th of the average water depth of the full tank or 10mm.

### Notwithstanding the satisfactory completion of the test, any evidence of seepage of the liquid to the outside faces of the valve chamber walls should be assessed against the requirements of the specification. Any necessary remedial treatment of the concrete, cracks, or joints should, where practical, be carried out from the liquid face.

### Should the structure not satisfy the 7-day test, then after the completion of the remedial work it should be refilled and left for a further stabilizing period; a further test of 7days’ duration should then be undertaken in accordance with this clause

### The review time of 21 days (for reviews to be undertaken) shall apply to all individual submissions. Therefore where a contractor is aware of items requiring multidiscipline integration then the Contractor should aim to submit all documents at once – otherwise separate submissions shall be treated as individual submissions.

### The review time of 21 days shall not be deemed to include comments on the submissions made. Receipt of comments shall trigger a new review cycle.

- The above applies to all design submissions issued to the engineer.

- GENERAL  SPECIFICATIONS

  - GENERAL REQUIREMENTS

The Contractor shall, at his/her own cost, maintain the whole of the site in a clean and orderly condition, to the satisfaction of the Engineer. On completion of the work, the Contractor shall tidy up the site to the satisfaction of the Engineer; all temporary buildings shall be dismantled and removed; all surplus material, debris etc. shall be carted away and the whole site shall be left in a neat and tidy condition.

  - DESCRIPTION OF THE SITE

    - Site Location

The site for the reinforced and precast concrete valve chambers are in Rand Water’s Lethabo INTAKE STATION, Vereeniging, Gauteng Province.

    - Site Boundaries

The Contractor shall confine his/her construction activities to within the contractual boundaries of the site. The Contractor shall not extend his/her activities outside the contractual boundaries unless the Engineer has specifically authorized the extension in writing.

  - PROTECTION OF THE WORK

The Contractor shall in particular keep the site free of water to allow for dry working conditions, provisions for dealing with water are discussed further in the technical specifications.

  - OCUPATIONAL HEALTH AND SAFETY

It is the Contractor’s responsibility at all times to ensure that all works, including excavations are undertaken in a safe manner in compliance with the regulations promulgated under the Occupational Health and Safety Act (Act 85 of 1993) or any amendment thereof.  Safety precautions to be observed by the Contractor shall include the sloping, stepping or benching or shoring, timbering or otherwise supporting the sides of the excavations or any other provision as stipulated in Regulation 11 of the aforesaid act, with which the Contractor declares himself to be conversant.

The shoring method adopted shall be compatible with the excavating, backfilling and construction method and shall not restrict the installation and construction. Shores shall be designed (including but not limited to geological studies, service detection) to withstand the earth pressures exerted upon them from the side of the excavation which shall include the superimposed loading of construction. All shoring designs must be reviewed and accepted by Rand Water engineers before implementation.

The Engineer may call upon the Contractor to timber the sides of the excavation at any point, without cost to Rand Water, which he may consider in any way dangerous.  Such timbering shall be left in place until the completion of the work at the point affected.

Timbering shall consist of open planking, wallings and substantial struts and shall be carried out in a workmanlike manner and to the satisfaction of the Engineer.

The Contractor shall allow for the removal of timbering immediately prior to backfilling or on the instructions of the Engineer.

MAINTAINING THE SIDES OF THE EXCAVATIONS IN A SAFE CONDITION SHALL AT ALL TIMES BE THE SOLE RESPONSIBILITY OF THE CONTRACTOR. NO UNDER-CUTTING OF THE SIDES WILL BE ALLOWED

  - FEATURES REQUIRING SPECIAL ATTENTION

    - Existing Services and Structures

Care must be taken that the existing pipework, valves, electric cables etc. are not damaged or destroyed during any activity necessary for the execution of the works. Any damage to existing services will be to the contractors account.

    - Quality Plan

The Contractor will be required to submit a detailed integrated manufacturing and quality plan to the Engineer or Engineer’s representative.

The Contractor shall request the Engineer via e-mail and through a formal letter, at least 48 hours in advance, to come out to site to inspect works at set control points - which may be stated in the contract specification documents or accompanying drawings (e.g. inspection of excavations for foundation, inspection of rebar etc.)

The Contractor shall keep a quality control file on site with the quality control plan, all quality control forms and test results and shall present this file to the Engineer at each site inspection. Furthermore, the contractor shall send all relevant site and lab test results (e.g. compaction test results, concrete cube test results etc.) via e-mail to the Engineer as soon as they become available.

    - Construction Methodology for Chambers 2A; 2B and 11

The Contractor will be required to complete the full excavation for chambers 2A, 2B and 11. Pipe and valve supports must be used to support the existing live pumpsets (for phase 2 and 3). It is the contractors prerogative to design and provide sufficient supports strong enough to withstand the loads of the infrastructure during the construction periods.

The entire base and starter bars for chamber 2A, 2B and 11 will be cast in Phase 1. Thereafter, chamber 2A (walls and roof slab) will be cast in Phase 1 together with construction joints and  wall starter/lapping bars for chamber 2B.

Chamber 22 (walls and roof slab) will be cast in Phase 2 together with construction joints and  wall starter/lapping bars for chamber 1.

- Chamber 11 (walls and roof slab) will be cast in Phase 3.

DRAWINGS

The following Drawings shall form and be read as part of the Contract:

| Drawing No. | Description | Discipline | Revision |
| --- | --- | --- | --- |
| R0_9160/200 | General Arrangement of floor plan layout for chambers 2A, 2B and 11 | Civil | 0 |
| R0_9160/201 | General Arrangement of valve chamber 2A: 1.8m Mag flow + 1.4m Non-Return + 1.8m Butterfly + 0.4m Surge Anticipation Valves | Civil | 0 |
| R0_9160/202 | General Arrangement of valve chamber 2A: 1.8m Mag flow + 1.4m Non-Return + 1.8m Butterfly + 0.4m Surge Anticipation Valves | Civil | 0 |
| R0_9160/203 | General Arrangement of valve chamber 3 for 2000mm diameter butterfly valve | Civil | 0 |
| R0_9160/204 | General Arrangement of valve chamber 4 for 2000mm diameter butterfly valve | Civil | 0 |
| R0_9160/205 | General Arrangement of valve chamber 5 for 1800mm diameter butterfly valve | Civil | 0 |
| R0_9160/206 | General Arrangement of valve chamber 6 for 800mm diameter butterfly valve | Civil | 0 |
| R0_9160/207 | General Arrangement of valve chamber 7 for 800mm diameter butterfly valve | Civil | 0 |
| R0_9160/208 | General Arrangement of valve chamber 8: 1.8m Mag flow + 1.4m Non-Return + 1.8m Butterfly + 0.4m Surge Anticipation Valves | Civil | 0 |
| R0_9160/209 | General Arrangement of valve chamber 8: 1.8m Mag flow + 1.4m Non-Return + 1.8m Butterfly + 0.4m Surge Anticipation Valves | Civil | 0 |
| R0_9160/210 | General Arrangement of valve chamber 9: 2.5m Mag flow | Civil | 0 |
| R0_9160/211 | General Arrangement of valve chamber 2B: 1.8m Mag flow + 1.4m Non-Return + 1.8m Butterfly + 0.4m Surge Anticipation Valves | Civil | 0 |
| R0_9160/212 | General Arrangement of valve chamber 2B: 1.8m Mag flow + 1.4m Non-Return + 1.8m Butterfly + 0.4m Surge Anticipation Valves | Civil | 0 |
| R0_9160/213 | General Arrangement of valve chamber 11 for 1800mm diameter mag flow | Civil | 0 |
| R0_9160/214 | General Arrangement of valve chambers 12 and 14: 1.8m Mag flow + 1.4m Non-Return + 1.8m Butterfly + 0.4m Surge Anticipation Valves | Civil | 0 |
| R0_9160/215 | General Arrangement of valve chamber 12: 1.8m Mag flow + 1.4m Non-Return + 1.8m Butterfly + 0.4m Surge Anticipation Valves | Civil | 0 |
| R0_9160/216 | General Arrangement of valve chamber 13 for 2000mm diameter butterfly valve | Civil | 0 |
| Drawing No. | Description | Discipline | Revision |
| R0_9160/217 | General Arrangement of valve chamber 15 for 1800mm diameter mag flow | Civil | 0 |
| R0_9160/400 | General Arrangement of steel platforms | Civil | 0 |
| R0_9160/401 | General Arrangement of steel platforms and details | Civil | 0 |
| Standard drawings |  |  |  |
| A8879 | Details of cast in frame for valve chamber sumps | Civil | 0 |
| A9858 | Details of grab rails at access manhole | Civil | 0 |
| 11860 | Steelfibre concrete manhole cover and support frame | Civil | 0 |
| A12210 | Typical valve support details | Civil | 0 |
| A7406 | Standard galvanized cat ladder details wall mounted | Civil | 0 |
| RA 27329 | Detail of External Mass Concrete Steps | Civil | 0 |
| RA26809/5 | Details of valve actuator extension | Mech. | 0 |
| RA9160/101 | Details of sump pump | Mech. | 0 |