## Arrangement of Waterways

### 1. Delivery Tunnel

The Design of the 38 km long Delivery Tunnel  was based on a "valveless" control system, i.e. upstream control by way of the Muela Intake up to drown out, thereafter tunnel control (“conductance”).  The tunnel will remain full of water at all times.  To achieve this without downstream closure capability the vertical alignment everywhere upstream of the Ash Outfall Crump Weir control is below the level of that control.

#### 2. Basic Project Parameters

The following basic project parameters are relevant:

- Muela Tail pond:

- Operating levels (Phase I)	1773,5 masl

- Full supply (spillway level)	1775,0 masl

- PMF level			1777,5 masl

- Tunnel Output:

- Nominal yield	(Phase IA)	18,0 m3/s

- Nominal yield	(Phase I)	29,6 m3/s

- Nominal yield	(Phase II)	42,0 m3/s

- Design flow	(Phase I)	32,6 m3/s (theoretically fully aged tunnel)

- Maximum capacity		38,0 m³/s (calculated on basis of last set of ageing data)

- Little Caledon Bypass:

- Tunnel take-off level		1734,0 masl

- Outlet Level			1715,0 masl

- Nominal yield	(Phase I)	20,0 m3/s

- Ash Outfall:

- Outfall Crump Weir level	1734,0 masl

- Maximum capacity		48,0 m³/s (confirmed during 1998 flow testing)

The layout of the Delivery Tunnel and a long section showing the design HGL are included in Appendix A.

#### 3. Delivery Tunnel North Access

Access to the tunnel is gained as follows:

Table 1:  Tunnel Access Points and Modes.

| Access Point Description | Tunnel Chainage (m) | Interval (m) | Tunnel Invert Level (masl) | Adit Length (m) | Remarks |
| --- | --- | --- | --- | --- | --- |
| Caledon North Adit | 16 418 | 736 | 1 666,563 | 232 m to BH(2) | Vehicular access |
| Little Caledon Tunnel Bypass | 25 105 | 8 687 | 1 715,610 | 1,5 m MH(2) Bypass Shaft Off-take 154m US | On foot access |
| Little Caledon South Adit | 25 308 | 203 | 1 714,771 | 7 m to BH(2) | Vehicular access |
| Little Caledon North Adit | 25 909 | 601 | 1 716,373 | 7 m to BH(2) | Vehicular access |
| Ash Outfall | 37 013 | 11 104 | 1 731,250 | Portal | Vehicular access |

Notes:

1.	GS = Gate Shaft.

2.	BH = Tunnel Bulkhead in Access Adit.

3.	MH = Access Manhole in pipework in Valve Chamber.

#### 4. Delivery Tunnel North Ventilation

The tunnel is ventilated as follows:

Table 2:  Tunnel Ventilation Points.

| Ventilation Point Description | Tunnel Chainage (m) | Interval (m) | Tunnel Invert Level (masl) | Opening Size (m) | Remarks |
| --- | --- | --- | --- | --- | --- |
| VS No. 5 | 15 081 | 5 732 | 1 728,272 | 0,23 m | 124 m Deep HDPE pipe |
| Caledon South Adit | 15 682 | 601 | 1 668,315 | 3,4 m | Vehicular access |
| Caledon North Adit | 16 418 | 736 | 1 666,563 | 3,4 m | Vehicular access |
| VS No. 6A | 17 042 | 624 | 1 726,055 | 0,23 m | 73 m Deep HDPE pipe |
| Little Caledon Tunnel Bypass | 25 105 | 8 063 | 1 715,610 | 3 m | 31 m Deep RC shaft |
| Little Caledon South Adit | 25 308 | 203 | 1 714,771 | 3,4 m | Vehicular access |
| Air Valve South | 25 329 | 21 | 1 714,648 | 0,15 m | 8 m S/S pipe and air valve |
| Little Caledon North Adit | 25 909 | 580 | 1 716,373 | 3,4 m | Vehicular access |
| Air Valve North | 25 916 | 7 | 1 716,556 | 0,15 m | 8 m S/S pipe and air valve |
| Ash Outfall | 37 013 | 11 097 | 1 731,250 | 4,6m | Vehicular access |

Notes:

1.	GS = Gate Shaft.

2.	BH = Tunnel Bulkhead in Access Adit.

3.	MH = Access Manhole in pipework in Valve Chamber.

#### 5. Delivery Tunnel North Linings

Two different types of tunnel lining designs were employed along Delivery Tunnel.

Table 3:  Tunnel Diameter and Lining Types.

| Lining Type | Diameter (m) | Length (m) | Start(1) Chainage (m) | Remarks |
| --- | --- | --- | --- | --- |
| Concrete | 4,5 | 589 |  | Caledon VS5 Drive |
| Steel | 3,0 | 20 | 15 682 | Caledon South Adit Bulkhead |
| Concrete | 4,5 | 111 |  | Caledon River Crossing South |
| Steel | 3,4 | 495 |  | Caledon River Crossing Steel Liner |
| Concrete | 4,5 | 223 |  | Caledon River Crossing North |
| Steel | 3,0 | 20 | 16 418 | Caledon North Adit Bulkhead |
| Concrete | 5,662 | 570 |  | Caledon VS6A Drive |
| Segment Lining | 4,6 | 7 040 |  | Caledon Drive |
| Steel | 3,4 | 215 |  | Low Cover Section |
| Segment Lining | 4,6 | 788 |  | Caledon Tunnel Drive |
| Concrete | 5,662 | 203 |  | Little Caledon South Drive |
| Concrete | 2,4 | 55 |  | Little Caledon Tunnel Bypass Off-take |
| Steel | 1,6 | 128 |  | Little Caledon Tunnel Bypass Off-take |
| Steel | 3,0 | 10 | 25 308 | Little Caledon South Adit Bulkhead |
| Concrete | 4,5 | 652 |  | Little Caledon Siphon |
| Steel | 3,0 | 10 | 25 909 | Little Caledon North Adit Bulkhead |
| Concrete | 5,662 | 91 |  | Little Caledon North Drive |
| Segment Lining | 4,6 | 10 981 |  | Ash Tunnel Drive |
| Concrete | 4,6 | 10 | 37 013 | Ash Outfall |

Notes:

1.	Measured from closest point of access.

#### 6. Delivery Tunnel North Geometric Sections

The Delivery Tunnel may be divided into four Geometric Sections, within each of which there is a dewatering facility:

- Caledon, consisting only of the Caledon river crossing bounded by Ventilation Shaft No 5 and Ventilation Shaft No 6A, and

- Little Caledon, consisting of the Caledon and Ash Tunnels and the Little Caledon river crossing bounded by Ventilation Shaft No 6A and the Ash Outfall.

Table 4:  Water Volumes per Tunnel Section (Delivery Tunnel)

| Description of Geometric Section | Volume drained by Gravity (m3) | Volume drained by Pumping (m3) | Total Volume (m3) |
| --- | --- | --- | --- |
| Caledon | 28,701.0 | 9,734.2 | 33,435.7 |
| Little Caledon | 328,839.0 | 3,086.8 | 333,925.6 |
| TOTAL | 357,540.0 | 12,921.0 | 366,361.3 |

Also refer to the Delivery Tunnel long section included in Appendix A.

#### 7. Dewatering Shafts

The Tunnel is dewatered by means of two dewatering shafts located, one each, in the four river crossings traversed by the Tunnel.  Details of the shafts are as follows.

Table 5:  Dewatering Shaft Details.

| Description of Section | Diameter (mm) | Control Valve (CV) | Outlet Level (masl) |
| --- | --- | --- | --- |
| Caledon | 250 & 600 | Fixed Cone Sleeve Valve | 1,670.000 |
| Little Caledon | 700 & 900 | Butterfly Valve | 1,710.300 |

These were designed and built as dry shafts with internal pipe and control work.  Discharge coefficients for the dewatering shafts are shown in Table 10 below.

Table 6:  Dewatering Shaft Discharge Coefficients (Cv)

| Dewatering | % Open |  |  |  |
| --- | --- | --- | --- | --- |
| Shaft | 100 | 75 | 50 | 25 |
| Caledon | 0,137 | 0,103 | 0,069 | 0,034 |
| Little Caledon | 1,083 | 0,889 | 0,563 | 0,302 |

with,

#### 8. Little Caledon Tunnel Bypass

The Tunnel Bypass arrangement is designed such that

(i)	The tunnel will remain full of water at all times,

(ii)	At full valve opening the hydraulic resistance of the bypass works is approximately the same as that of the downstream tunnel to the Ash Outfall.  With the bypass fully open the Delivery Tunnel flow will therefore be shared approximately equally between the Ash and Little Caledon rivers,

(iii)	The off-take from the Delivery Tunnel has an invert sill level of 1734,0 masl placing it at the same level as the Outfall level control and therefore making it impossible for air to be drawn into the tunnel,

(iii)	The 900 mm  FCSV and 1600 mm  Butterfly valves closure rates are limited to minimise pressure transients in the tunnel,

(iv)     The off-take is via a shaft to atmosphere with an overflow level marginally above the full flow hydraulic grade line in the tunnel thus providing, by overflow, positive assurance that tunnel design pressures cannot be exceeded by mal-operation of valves or Intake Gates.

The effect of bypass operation will be to increase the flow in the DT because of a reduction in the overall hydraulic resistance of the tunnel.  For example, the design flow rate through Delivery Tunnel will increase from 32,6 m3/s to 39,5 m3/s with the Bypass open.

#### 9. Ash River Outfall

The Ash Outfall Works principally comprises an open rectangular channel with an upstream transition to the tunnel and equipped with a Crump Weir.  The Crump Weir serves a dual purpose of a hydraulic control for the operation of the tunnel and as a flow measurement device.  In the latter respect it serves as a back up to the flow measurement facility at the Ngoajane River Crossing in Lesotho.

The Crump Weir level is at 1734,0 masl and is 9 m wide.

RELEVANT DRAWINGS

Delivery Tunnel lay out

Delivery Tunnel long section

Ash Outfall

Ash river layout

Tunnel By Pass off-take

Caledon Dewatering Shaft

Little Caledon Dewatering Shaft