| To whom it may concern | Date | 7 JUly 2026 |
| --- | --- | --- |
|  | Enquiries | Supplier Clarification Questions |
|  | E-mail address |  |

Dear Sir/Madam

| Request for Enquiry Number |  |
| --- | --- |
| Description / Project Title | TO ENGINEER, PROCURE AND CONSTRUCT A WATER ELECTROLYSIS HYDROGEN GENERATION PLANT, WHICH MUST BE INTEGRATED WITH THE EXISTING RENEWABLE POWER PLANT FOR “GREEN H2 PRODUCTION” AT ERIC ROSHERVILLE FOR A PERIOD OF THREE (3) YEARS. |
| Tender Questions Closing Date | 10 July 2025 |

| Item | Reference: | Questions | Answers | Clarity Published Dates |
| --- | --- | --- | --- | --- |
|  | Green Hydrogen Facility OHS Requirements Presentation - High risk, H&S Evaluation Criteria - Ref: 6 (Pg 2) | 37(2) Eskom Agreement / Occupational Health and Safety Act: Section 37(2) Agreement – Form The Tenderer kindly requests the official tender submission documents to facilitate the timely preparation and submission of a fully compliant, high-quality bid in accordance with Eskom's requirements. | 37(2) Eskom Agreement / Occupational Health and Safety Act: Section 37(2) Agreement – Form has been uploaded on the tender bulletin. | 17 July 2026 |
|  | Annexure A 3.3.2, Pg 18 | The hydrogen plant must be within a cabinet, in a container with all associated H2 production equipment. The H2 plant is considered to be a temporary / mobile plant that can be relocated to a different site in future. This container must include a heating, ventilation and air conditioning (HVAC) system as required to control the temperature and humidity within the container during operations and to ensure there is no accumulation of gas at any point within the container. The specification requires the hydrogen plant container to be provided with an HVAC system to control temperature and humidity, and to prevent hydrogen accumulation within the container. Please clarify whether active humidity control and air conditioning are mandatory requirements, or whether mechanical ventilation only will be acceptable where it satisfies the OEM requirements, maintains the required equipment operating temperature range, and prevents hydrogen accumulation. This approach appears to be consistent with the Kusile installation observed during the site visit, where the hydrogen room was naturally ventilated rather than provided with full temperature and humidity-controlled air conditioning. Should active temperature and/or humidity control be required, please specify the required internal temperature and relative humidity ranges to be maintained within the container. Active humidity control would result in a larger and more complex HVAC system, with increased power demand, maintenance requirements and cost. | The specific details of the design for heating, ventilation and air conditioning system are to be determined by the supplier. The design of the system must satisfy the OEM’s requirements in terms of controlling the temperature and humidity within the container during operations. Ventilation is essential to ensure there is no accumulation of gas at any point within the container and must be included in the design. Active humidity control and air conditioning are not mandatory. Please note that the Kusile plant is housed within a permanent structure while the scope in Annexure A requires the hydrogen plant to be housed in a container (which has less free space). |  |
|  | 2.7 Annexure A Page 18. “H2 at min 27 bar, min purity 99.9% vol, dew point -50C or better at 101.4kPa | The project requirements in Annexure A specify “H2 at min 27 bar pressure, 99.9% purity, and -50C dewpoint at 101.4kPa”. If we provide Hydrogen at 30barG and 99.90% purity, the dewpoint would be~-21C at 101.4kPa. If we need to achieve a -50C dewpoint at 101.9kPa, the purity would be 99.996%. To accomplish this we would need a purgeless dryer which adds complexity and reduces reliability. In order to improve reliability, we recommend raising the dewpoint requirement in the specification to: H2 at min 27 bar, min purity 99.9% vol, dew point – 20C or better at 101.4kPa. Is this acceptable? | A system which provides H2 at min 27 bar, min purity 99.9% vol, dew point – 20C or better at 101.4kPa will not be automatically disqualified. It will be evaluated in terms of the whole offer to see if the system meets the requirements of the project. All deviations must be declared in the Deviation Schedule and the provided spreadsheet 240-RT&D-782 Technical Schedule for Renewable Hydrogen Facility |  |