{"text_format":"3","workbook":"xls","n_sheets":4,"sheets":["A&B Schedules","Deviation Schedule","Test Schedule","Documentation"],"not_rendered":{"external_links":2,"defined_names":3},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"A&B Schedules","index":0,"n_rows":61,"n_cols":8,"rows_kept":61,"merged":[[0,1,0,7],[1,1,1,7],[2,1,2,7],[3,1,3,7],[5,4,5,6],[6,4,6,6],[8,1,8,7],[9,1,9,7],[12,2,12,3],[13,2,13,3],[14,3,14,4],[20,3,20,4],[28,3,28,4],[33,3,33,4],[35,3,35,4],[37,3,37,4],[39,2,39,4],[40,2,40,4],[41,3,41,4],[44,3,44,4],[46,3,46,4],[49,1,50,7],[51,0,51,6],[53,0,53,7],[55,0,55,1],[60,2,60,3]],"flags":["formulas_cached_only"]}
[null,"Technical Schedules A and B for"]
[null," D-DT 6044- BAR, CU RD 10.0mm ANNEALED"]
[null,"NB. UNIQUE SCHEDULES ARE TO BE COMPLETED PER SAP NUMBER LISTED BELOW "]
[null,"NB. SUPPLIERS TO CONFIRM ADHERENCE TO THE LATEST PUBLISHED REVISION OF ALL APPLICABLE ESKOM DOCUMENTS AND DRAWINGS"]
[]
[{"$nulls":3},"Sap Number","Description",null,null,"Eskom Standard"]
[{"$nulls":3},"0400769","BAR, CU RD 10.0mm ANNEALED D6044",null,null,"D-DT 6044"]
[]
[null,"Schedule A:  Purchasers specific requirements"]
[null,"Schedule B:  Guarantees and technical particulars of equipment offered"]
[]
[null,1,null,2,null,3,4,5]
[null,"Item ","Description",null,null,"UM","Schedule A","Schedule B"]
[null,1,"Product Information"]
[null,1.1,"·","Purchasing details"]
[null,"1.1.1",null,"Eskom SAP No",400769,null,"xxxxxxxxxx"]
[null,"1.1.2",null,"Manufacturer","Manufacturer name",null,"xxxxxxxxxx"]
[null,"1.1.3",null,"Manufacturer's Product Code","Specify Code",null,"xxxxxxxxxx"]
[null,"1.1.4",null,"Manufacturer's Drawing number & Revision number","Specify No and Rev",null,"xxxxxxxxxx"]
[{"$nulls":3},"What is the weight of the supplied product","Specify Weight","kg/m","0.702kg/m"]
[null,1.2,"·","Material physical properties"]
[null,"1.2.1",null,"Normal vlaues for standard annealed copper at a temperature of 20 0C","IEC 60028"]
[{"$nulls":3},"Volume resistivity",null,"Ω.m2/m","0,017 241 "]
[{"$nulls":3},"Density",null,"g/cm3","8,89 "]
[{"$nulls":3},"Co-efficient of linear expansion ",null,"per °C","17 × 10 -6 "]
[{"$nulls":3},"Co-efficient of variation of the resistence with temperature, measure between two potential points rigidly fixed to the wire, the metal being allowed to expand freely",null,"per °C","0,003 93 "]
[{"$nulls":3},"Mass resistivity of standard annealed copper",null,"Ω.g per m","0,153 8 "]
[{"$nulls":3},"Diameter","D-DT 6044","mm",10]
[null,1.3,"·","Chemical composition"]
[{"$nulls":3},"Copper (silver being counted as copper)","SANS 804:2008","%","Min 99,90"]
[{"$nulls":3},"Bismuth","SANS 804:2008","%","Max 0,0010"]
[{"$nulls":3},"Lead ","SANS 804:2008","%","Max 0,005"]
[{"$nulls":3},"Total of all impurities (excluding oxygen and silver)","SANS 804:2008","%","Max 0,03"]
[null,1.4,"·","Compliance with SANS 182-1"]
[{"$nulls":3},"All constructional requirements are in accordance with SANS 182-1","SANS 182-1; sub-clause 4.",null,"Yes "]
[null,1.5,"·","Packing requirements with SANS 182-1"]
[{"$nulls":3},"1) Unless otherwise specified by the purchaser, the conductor shall be packed on a robust wooden drum or wooden reel that has a barrel of diameter at least 30d, where d is the nominal overall diameter of the conductor.\n2) The moisture content of the wood used for fabrication of the drums or reels shall not\nexceed 15 %.\n3) When wooden drums or reels resistant to biological attack are required by the purchaser,\nthe wood shall have been impregnated (by pressure or in a hot/cold open tank) in\naccordance with SANS 10005, with a class C preservative or with chromated copper\narsenate.","SANS 182-1; sub-clause 5.1",null,"Yes "]
[null,1.5,"·","Marking requirements with SANS 182-1"]
[{"$nulls":3},"Each coil, reel, or drum shall bear the following\ninformation legibly and indelibly marked on a firmly attached label or printed on a cheek of the reel or drum:\na) the manufacturer's trade name or trade mark or both;\nb) reference area of conductor or size of wire, as applicable, and type of product;\nc) nominal length in metres;\nd) gross mass in kg (net mass if in coils or on reels); and\ne) year of manufacture.                               ","SANS 182-1; sub-clause  5.2",null,"Yes"]
[null,2,"Documentation (to be submitted with tender)"]
[null,null,"Note:  All documentation to also be provided in electronic format."]
[null,2.1,"·","General"]
[null,"2.1.1",null,"Approved Manufacturer Drawings showing markings and dimensions.Product brochure with  Illustration clearly showing general arrangements, critical dimensions etc. will be accepted should the manufacturers drawing not be made available. ","1 Set submitted",null,"Yes"]
[{"$nulls":3},"Sampling documentation","1 Set submitted",null,"Yes"]
[null,2.2,"·","Test Reports ",null,null,"Required"]
[null,"2.2.1",null,"Has the relevant signed mandatory test schedule been submitted.","Signed Test Schedule Submitted ",null,"Yes"]
[null,2.3,"·","Product sample",null,null,"Required"]
[{"$nulls":3},"A sample may be requested for material and dimension verification.","1 Sample submitted",null,"Yes"]
[]
[null,"Deviations to any of the stated requirements are to be captured on the Deviation Schedule."]
[]
["NB: By signing below the supplier is legally binding themselves to the compliance with the Standard Requirements completed on this Schedule"]
[]
["SUPPLIER SIGNATURES"]
[]
[null,null,"         "]
[{"$nulls":3},"Name (Print)",null,null,"Company name"]
[]
[]
[]
[null,null,"Sign",{"$nulls":3},"Date"]

{"sheet":"Deviation Schedule","index":1,"n_rows":46,"n_cols":6,"rows_kept":46,"merged":[[0,0,0,6],[1,0,1,6],[1,7,1,13],[1,14,1,20],[1,21,1,27],[1,28,1,34],[1,35,1,41],[1,42,1,48],[1,49,1,55],[1,56,1,62],[1,63,1,69],[1,70,1,76],[1,77,1,83],[1,84,1,90],[1,91,1,97],[1,98,1,104],[1,105,1,111],[1,112,1,118],[1,119,1,125],[1,126,1,132],[1,133,1,139],[1,140,1,146],[1,147,1,153],[1,154,1,160],[1,161,1,167],[1,168,1,174],[1,175,1,181],[1,182,1,188],[1,189,1,195],[1,196,1,202],[1,203,1,209],[1,210,1,216],[1,217,1,223],[1,224,1,230],[1,231,1,237],[1,238,1,244],[1,245,1,251],[1,252,1,255],[2,0,2,6],[2,7,2,13],[2,14,2,20],[2,21,2,27],[2,28,2,34],[2,35,2,41],[2,42,2,48],[2,49,2,55],[2,56,2,62],[2,63,2,69],[2,70,2,76],[2,77,2,83],[2,84,2,90],[2,91,2,97],[2,98,2,104],[2,105,2,111],[2,112,2,118],[2,119,2,125],[2,126,2,132],[2,133,2,139],[2,140,2,146],[2,147,2,153],[2,154,2,160],[2,161,2,167],[2,168,2,174],[2,175,2,181],[2,182,2,188],[2,189,2,195],[2,196,2,202],[2,203,2,209],[2,210,2,216],[2,217,2,223],[2,224,2,230],[2,231,2,237],[2,238,2,244],[2,245,2,251],[2,252,2,255],[3,0,3,6],[4,2,4,6],[5,2,5,6],[6,2,6,6],[7,2,7,6],[8,2,8,6],[9,2,9,6],[10,2,10,6],[11,2,11,6],[12,2,12,6],[13,2,13,6],[14,2,14,6],[15,2,15,6],[16,2,16,6],[17,2,17,6],[18,2,18,6],[19,2,19,6],[20,2,20,6],[21,2,21,6],[22,2,22,6],[23,2,23,6],[24,2,24,6],[25,2,25,6],[26,2,26,6],[27,2,27,6],[28,2,28,6],[29,2,29,6],[30,2,30,6],[31,2,31,6],[32,2,32,6],[33,2,33,6],[34,2,34,6],[36,0,36,6],[38,0,38,6],[40,0,40,1],[41,2,41,3],[45,2,45,3]],"flags":["formulas_cached_only"]}
["Deviation schedule"]
[" D-DT 6044- BAR, CU RD 10.0mm ANNEALED"]
["SAP No:.                            (To Be Specified)"]
["Any deviations offered to this specification shall be listed below with reasons for deviation.  In addition, evidence shall be provided that the proposed deviation will at least be more cost-effective that that specified by Eskom.The deviation must be completed even if there are no deviations. Post evaluation,  the letter of garantee to confim that the product is not compromised even though it was not tested according to the latest  Standard."]
["Item","Clause","Description of Deviation"]
{"$rows_empty":31}
["NB: By signing below the supplier is legally binding themselves to the compliance with the Standard Requirements completed on this Schedule"]
[]
["SUPPLIER SIGNATURES"]
[]
[null,null,"         "]
[null,null,"Name (Print)",null,null,"Company name"]
[]
[]
[]
[null,null,"Sign",null,null,"Date"]

{"sheet":"Test Schedule","index":2,"n_rows":20,"n_cols":6,"rows_kept":20,"merged":[[0,0,0,7],[1,0,1,7],[2,1,2,5],[3,0,3,7],[9,1,9,2],[10,0,10,6],[11,1,11,8],[12,1,12,8],[15,1,15,2],[19,1,19,2]],"flags":["formulas_cached_only"]}
["Test Report Schedule"]
[" D-DT 6044- BAR, CU RD 10.0mm ANNEALED"]
[null,"The test reports are required for the selected SAP number listed on this sheet."]
["SAP No:.                                     (To be specified)"]
[]
[null,1,2,3,4,5]
[null,"Item ","Description","Standard","Clause No.","Report No."]
[null,null,"Dimension and Material Verification","SANS 804 and D-DT 6044"]
[]
[]
["NB: By signing below the supplier is legally binding themselves to the compliance with the Standard Requirements completed on this Schedule"]
[]
[null,"SUPPLIER SIGNATURES"]
[]
[]
[null,"Name (Print)",{"$nulls":3},"Company name"]
[]
[]
[]
[null,"Sign",{"$nulls":3},"Date"]

{"sheet":"Documentation","index":3,"n_rows":7,"n_cols":2,"rows_kept":7,"merged":[[0,0,0,3]],"flags":["formulas_cached_only"]}
["This page is for SI personnel use only - This page to be disabled during enquiry stage"]
[]
[null,"Buyers Guide"]
[null,"http://tescod1.eskom.co.za:84/Prt09BG/6000/6044.pdf"]
[]
[null,"Eskom Specification"]
[null,"https://hyperwave.eskom.co.za/240-75883110"]