|  | FBC Free State OU and Northern Cape OU INVESTIGATION REPORT | Template Identifier | 240-43921804 | Rev | 6 |
| --- | --- | --- | --- | --- | --- |
|  |  | Document Identifier | 240-136349448 | Rev | 2 |
|  |  | Review Date | 10 April 2018 |  |  |
|  |  | Effective Date | 01 March 2022 |  |  |

| INFORMATION SUPPLIED BY THE CUSTOMER AND POPULATED BY INSURANCE DEPARTMENT |  |  |  |
| --- | --- | --- | --- |
| Incident location (Town) | Jacobsdal | Sector | Bloemfotein |
| Date of incident | 13.09.2021 | Time of Incident | 09:00 |
| Date reported (fault) |  | Reference number |  |
| Date reported (claim) | 28.01.2022 | Reference number | Not registered |
| Pole No. | JACO284 | Works order No. |  |
| Name of claimant | LA Lategan I Joubert | Contact number | 083 751 6170 daughter 083 270 5729 |
| Stand Number/Address | Farm Joubertina Jacobsdal | Claim No. | 434708 |
| Summary of incident |  |  |  |
|  | Lategan Grazing Joubert Grazing |  | R800 000.00 R419 834.13 |
| Insurance remarks |  |  |  |
| Date to PCC |  |  |  |

| INVESTIGATION MAINTENANCE AND OPERATIONS DEPARTMENT |  |  |  |
| --- | --- | --- | --- |
| Complied by | Jaco Weldhagen | Designation | Sector Engineer |
| Authorised by | Korone Moea | Designation | Sector Manager |
| Claimant’s allegations for claim: |  |  |  |
| Date and Time of Incident | 13/09/2021 09:00 | Date and Time supply Restored | NA |
| Time Dispatched | NA | Work Order Number | NA |
| Number of Interruptions | NA | Duration of Interruptions | NA |
| Network or Customers Affected | NA | Planned Outage? (Yes/No) | NA |
| Approximate MVA hours lost | NA | Network or Customers still at risk (Yes/No) | Yes |
| Weather Conditions | Wind/ Dry | Protection Details | At Koffiefontein SS last event trip recorded on Jacobsdal 132 KV fdr - 02/11/2021. |
| Proposed Contingency Plans | Install X arm supports on 132 KV 5 Pole wood structures and remove crow’s nests on 22 KV structures. |  |  |
| Root Cause of the Incident | Short circuit between crow’s nest and white phase conductor. |  |  |
| Summary of the Incident | Fire started at JACO 284. |  |  |
| Summary of Switching and Actions taken after the Incident | NA |  |  |
| Voltage Regulation within NRS048 | NA |  |  |
| Findings | 1.JK71 . Fire May /June 2019. Red phase glass insulator broken. Red and blue phase X arm support off. 2.JK74 Fire June 2021 . Red and Blue phase X arm supports off. Blue phase insulators polluted . Cross earth wire off. 3. JK76 Fire July August 2021. Red phase insulators polluted. Cross earth wire off. 4. JACO284 Fire report indicating fire started at JACO 284 on 13/09/2021.Page 14 of 17. |  |  |
| Line Maintenance / Pole Inspection Reports attached (In case of veld fires) |  |  |  |
| Proposed Recommendations to prevent recurrence | Install X arm supports on 132 KV 5 Pole wood structures and remove crow’s nests on 22 KV structures. |  |  |
| I hereby Acknowledge that the Above Information provided by me is correct and to the Best of my Ability | PJ Weldhagen |  |  |

| Approval of Investigation by Sector Manager | Comments and Action by Sector manager: Name: Date: Signature: …………………………………….. |
| --- | --- |

PHOTOS AND ANY OTHER SUBSTANTIATED DOCUMENTATION

1.

2.

3.

4.

| PROVINCIAL CLAIMS COMMITTEE USE ONLY |  |  |
| --- | --- | --- |
| Notes for consistency: - A note log to be kept of discussions regarding steps to be taken to prevent future incidents. - Eskom only responsible up to meter point, therefore the Customer is responsible for his own installation beyond this meter point. - Claims caused by stormy weather arising in December must be paid due to inconvenience caused to customers. - Ex Gratia payment: a minimum of 50% direct damage will be considered and based on the circumstances an amount higher than 50% will be considered based on consensus reached by the committee. - Veld Fire claims: Direct losses will be paid as per advice from the Agricultural extension officer of the Area. - Airdac in townships should be at a height of 4.7 meter as per EMR 15. - Staff needs to be sensitized as to the wording for root causes for normal deterioration. - Position where the LV neutral is broken will determine whether Eskom is liable. - Guiding principles for negligence: a) Deviation from the procedures, standards and legal requirements b) Reasonable steps not taken where it was required (Excluding major works & failure of major equipment) c) Omission or failure to act. - Damage due to strong winds causing poles to break (veldt set alight) will not be considered as a claim.- |  |  |
| QUESTIONS - Is Eskom liable? - Was fault attended to in a reasonable time? | Yes N/a | REMARKS: The crow’s nest not removed, and it cause the fire No fault was reported, |

| PROVINCIAL CLAIMS COMMITTEE DECISION |  |
| --- | --- |
| PCC Decision 19.04.2022 Approved subject to LA recommendation REASON |  |
| POLICY | REASONS FOR REJECTION |
| There must be damage to Eskom property | No conclusive evidence could be detected on Eskom network linking the damage to an Eskom event. |
| Must be one sudden, unforeseen, specific or identifiable event | - Incident could not have caused the damage - Eskom not responsible for the cause of the fire |
| Proximate cause should not be due to parties external to Eskom | - Proximate cause due to persons external to Eskom |
| Power fluctuations/power failures are specifically excluded unless Eskom contributed to the fault. | - Phases incorrectly connected - Neutral burnt - Refer clause 6. 3 - Lack of maintenance - Fault repaired within a reasonable time. - Voltage Regulation was within the NRS048 |
| Act of God | - Eskom could not have foreseen - Customer could not have taken reasonable standard |
| Must be direct damage | - Consequential loss - Incorrectly disconnected - Cable damaged due to excavation activities in the area by non-Eskom contractor and highly unlikely that damaged cable could have caused damage to Customers equipment. - Fault on customer side |

6.3	Customers are cautioned that they should ascertain from ESKOM the nature of the protection 			provided on the supply and should provide adequate means for the protection of their own 			equipment.  Inter alia,

6.3.1	It is not practicable for ESKOM to install protective equipment on its system which will ensure in all 		cases that motors and/or other equipment on the CUSTOMER's side will be protected in the event 		of low voltage or over voltage or single-phasing. It is therefore necessary for the CUSTOMER to 		take adequate measures to protect his motors and/or equipment against damage that may arise 		under low voltage or over voltage conditions or from single-phasing;

6.3.2	Where a voluntary or involuntary outage of supply may cause damage to the CUSTOMER's plant or 		business, he should take measures to protect himself against such possible damage. (i.e. standby 		generator & personal Insurance (Especially a sensitive business) Should the CUSTOMER have, or 		decide to install, his own standby generating plant for use during such outages, the equipment for 		connecting such plant to his electrical installation shall be subject to ESKOM's approval.  Such 			standby plant shall be operated only during such outages and furthermore the use and operation 		thereof by the CUSTOMER shall be subject to such terms and conditions as ESKOM may lay down 		to ensure the safety and protection of its personnel and equipment.

20.	CONTINUITY, REDUCTION OR VARIATION OF SUPPLY

20.1	ESKOM shall take all reasonable precautions to procure and maintain suitable plant for the 			generation and distribution of electricity calculated to secure to its consumers a constant supply of 		electricity and shall procure efficient technical staff to control such plant, but ESKOM does not 			guarantee that the same will always be maintained, and ESKOM shall not be liable for damages, 		expenses or costs caused to the CUSTOMER from any interruption in the supply, variation of 			voltage, variation of frequency, any failure to supply a balanced three-phase current or failure to 			supply electricity unless the said interruption or failure is due to the negligence of ESKOM in failing 		to carry out its obligations aforesaid.  In the event that ESKOM should be liable for damage caused 		to the CUSTOMER as a result of any such reduction in load or any interruption in the supply, or any 		variation of voltage or frequency or any failure to supply electricity, such liability shall be limited to 		direct damage only.

20.2	For purposes of the efficient operation and extension of ESKOM's distribution system, or if ESKOM 		should experience any shortage of generating capacity, ESKOM shall have the right to interrupt the 		supply to the CUSTOMER