{"text_format":"3","workbook":"xlsx","n_sheets":3,"sheets":["Co-Ax Cable Desk AB","Telephone Cable Desk AB","\"Z\" Cable Desk AB"],"read":"whole","date_system":"1900"}

{"sheet":"Co-Ax Cable Desk AB","index":0,"n_rows":72,"n_cols":6,"rows_kept":72,"merged":[[0,0,0,5],[6,1,6,2],[9,1,9,2],[16,1,16,2],[26,1,26,2],[33,1,33,2],[38,1,38,2],[43,1,43,2],[56,1,56,2],[65,1,65,2]]}
["240-64813538: HIGH FREQUENCY COAXIAL CABLE FOR POWER LINE CARRIER APPLICATIONS  Annex A: Schedules A and B for Desktop Evaluation"]
["ITEM","DESRIPTION","SCHEDULE A","SCHEDULE B","REMARKS","WEIGHT"]
[1,"Manufacturer Name","Specify",null,null,0.62]
[null,"Location of factory/ manufacturer’s premises","Physical Address",null,null,0.62]
[2,"National, International or Military Specification with which the cable complies","Specify",null,null,0.62]
[3,"Cable equivalent to RG12 A/U with Overall PVC Sheath","YES",null,null,0.62]
[4,"Electrical specification"]
[null,"a) Continuous voltage rating  ","Specify",null,null,0.56]
[null,"b)       Capacitance","67pF / meter (5% Tolerance) ",null,null,0.56]
[null,"c)       Attenuation"]
[null,"1)       At 500kHz","0.004dB / meter",null,null,0.56]
[null,"2)       At 2MHz","0.11dB / meter",null,null,0.56]
[null,"d)       Frequency range","40 - 500kHz",null,null,0.56]
[null,"e)       Corona extinction voltage               Vrms(min)","Specify",null,null,0.56]
[null,"f)         Characteristic impedance ","75W",null,null,0.56]
[null,"g)       Spark tests voltage                         Vrms(min)","Specify",null,null,0.56]
[5,"Inner conductor (core) details"]
[null,"a)        Number",1,null,null,0.56]
[null,"b)        Conductor area                                 mm2","0.9",null,null,0.56]
[null,"c)        Conductor material","Sn annealed Cu",null,null,0.56]
[null,"d)        Number of Cu strands",7,null,null,0.56]
[null,"e)        Strand diameter","0.4mm",null,null,0.56]
[null,"f)          DC resistance at 20°C                       ohms/km","< 20",null,null,0.56]
[null,"g)        50Hz resistance at 20°C                   ohms/km","Specify",null,null,0.56]
[null,"h)        Inductive reactance at 50Hz             ohms/km","Specify",null,null,0.56]
[null,"i)          Maximum continuous conductor temperature °C","Specify",null,null,0.56]
[6,"Dielectric Material"]
[null,"a)       Material composition","Polyethylene",null,null,0.56]
[null,"b)       Dielectric constant","2.3",null,null,0.56]
[null,"c)       Specify gravity","Specify",null,null,0.56]
[null,"d)       Velocity of propagation","Specify",null,null,0.56]
[null,"e)       Temperature limits","Specify",null,null,0.56]
[null,"f)         Overall diameter","7.2mm",null,null,0.56]
[7,"Insulation material"]
[null,"a)       core insulation compound used","Specify",null,null,0.56]
[null,"b)       screen insulation compound used","Specify",null,null,0.56]
[null,"c)       cable sheath compound used","Specify",null,null,0.56]
[null,"d)       fire propagation properties of finished cable","Specify",null,null,0.56]
[null,"e)       smoke/acid gas emission for"]
[null,"1)       core insulation","Specify",null,null,0.56]
[null,"2)       bedding and screen insulation","Specify",null,null,0.56]
[null,"3)       finished cable","Specify",null,null,0.56]
[null,"f)         Power frequency withstand test voltage for  one minute (centre conductor to outer conductor)","4kVrms",null,null,0.56]
[8,"Outer Braid Conductor / Screen and Armouring"]
[null,"a)        screen material","Plain annealed copper wires ",null,null,0.56]
[null,"b)        screen filling factor","Specify",null,null,0.56]
[null,"c)        screen thickness","0.2mm wires",null,null,0.56]
[null,"d)        water barrier","Specify",null,null,0.56]
[null,"e)        braided screen","YES",null,null,0.56]
[null,"f)          individual screen thickness                mm  ","Specify",null,null,0.56]
[null,"g)        individual screen resistance               ohms/km","Specify",null,null,0.56]
[null,"h)        individual screen coverage                100%","YES",null,null,0.56]
[null,"i)          overall screen resistance                   ohms/km","Specify",null,null,0.56]
[null,"j)          armouring wire material                     ","Galvanised steel",null,null,0.56]
[null,"k)        armouring wire diameter                    mm   ","0.9",null,null,0.56]
[null,"l)          armouring tensile strength                 N/mm","Specify",null,null,0.56]
[9,"Complete cable"]
[null,"a)       Diameter                                     mm","17 mm maximum",null,null,0.56]
[null,"b)       Min. bending radius                    mm",100,null,null,0.56]
[null,"c)       Mass                                           kg/km","Specify",null,null,0.56]
[null,"d)       Drum length"]
[null,"1)       average            m","Specify",null,null,0.56]
[null,"2)       minimum         m  ","Specify",null,null,0.56]
[null,"3)       maximum        m","Specify",null,null,0.56]
[null,"e)       Drum markings (Clause 5.1)","YES",null,null,0.56]
[10,"Test Certificates"]
[null,"State the location within the tender documentation where the Test Certificates for the following tests  can be found:"]
[null,"1)      Conductor elongation at break according to SANS 6282-3. ","Specify",null,null,0.56]
[null,"2)      Insulation physical properties according to SANS 1411-7","Specify",null,null,0.56]
[null,"3)      Insulation spark test according to SANS 62230","Specify",null,null,0.56]
[null,"4)       Sheath physical properties according to SANS 1411-2","Specify",null,null,0.56]
[null,"5)      Finished cable voltage withstand according to SANS 6284-3","Specify",null,null,0.56]

{"sheet":"Telephone Cable Desk AB","index":1,"n_rows":119,"n_cols":6,"rows_kept":119,"merged":[[0,0,0,5],[5,1,6,1],[5,2,6,2],[5,5,6,5],[7,1,9,1],[7,5,9,5],[10,1,12,1],[10,5,12,5],[13,1,15,1],[13,5,15,5],[18,1,20,1],[18,5,20,5],[22,1,24,1],[22,5,24,5],[31,1,40,1],[31,5,40,5],[42,1,44,1],[42,5,44,5],[49,5,51,5],[52,1,56,1],[52,5,56,5],[60,1,61,1],[60,5,61,5],[63,5,65,5],[70,1,73,1],[70,5,73,5],[81,1,82,1],[81,5,82,5],[83,1,86,1],[83,5,86,5],[88,5,90,5],[93,1,96,1],[93,5,96,5],[109,5,118,5]]}
["240-64813568: STANDARD INDOOR AND OUTDOOR TELEPHONE CABLE - Annex A: Schedules A and B for Desktop Evaluation"]
["ITEM","DESCRIPTION","SCHEDULE A","SCHEDULE B","REMARKS","WEIGHT"]
["0.","Manufacturer Name","Specify",null,null,0.7]
[null,"Location of factory/ manufacturer’s premises","Physical Address",null,null,0.8]
["1.","Conductors"]
[null,"Wire","Circular, Annealed, Electrolytic Copper",null,null,0.65]
[]
[null,"Diameter Tolerance","0,5mm - 0,49 / 0,51",null,null,0.65]
[null,null,"0,63mm - 0,62 / 0,64"]
[null,null,"0,91mm - 0,89 / 10,91"]
[null,"Maximum Electrical Resistance","0,5mm - 90,31 Ω/km",null,null,0.65]
[null,null,"0,63mm - 56,94 Ω/km"]
[null,null,"0,9mm - 27,91 Ω/km"]
[null,"Maximum Elongation before Fracture","0,5mm - 15%",null,null,0.65]
[null,null,"0,63mm - 20%"]
[null,null,"0,9mm - 20%"]
["2.","Conductor Insulation"]
[null," Material","Coloured Polyethylene",null,null,0.65]
[null,"Minimum Thickness of Insulation","0,5mm - 0,18mm",null,null,0.65]
[null,null,"0,63mm - 0,22mm"]
[null,null,"0,9mm - 0,25mm"]
[null,"Maximum tolerated shrink back when subjected to 100oC for 24 hours","6mm overall, less than 4mm per end",null,null,0.65]
[null,"Maximum force required to strip insulation from conductor","0,5mm - 17,7 N",null,null,0.65]
[null,null,"0,63mm- 17,7 N"]
[null,null,"0,91mm- 24,6 N"]
[null,"High voltage withstand","2000 V RMS (50Hz) or 3000 V DC",null,null,0.65]
[null,"Insulation resistance (Refer to Page 10 of Specification)","> 37,5 MΩ per km at 20°C",null,null,0.65]
["2.","Conductor Insulation (Cont)"]
[null,"HV spark withstand capability","According to SANS 62230",null,null,0.65]
[null,"Colours of insulation","According to BS6234 incorporated in Insulation",null,null,0.65]
[null,"Application of colour coding","1,5mm spiral or ring with dark colours over light, visible every 25mm",null,null,0.65]
[null,"Colour code of conductors","Pair 1 - Blue/White",null,null,0.65]
[null,null,"Pair 2 - Orange/White"]
[null,null,"Pair 3 - Green/White"]
[null,null,"Pair 4 - Brown/White"]
[null,null,"Pair 5 - Grey/White"]
[null,null,"Pair 6 - Blue/Red"]
[null,null,"Pair 7 - Orange/Red"]
[null,null,"Pair 8 - Green/Red"]
[null,null,"Pair 9 - Brown/Red"]
[null,null,"Pair l0 - Grey/Red"]
["3.","Conductor Twinning"]
[null,"Twist","0,5mm - ≤ 100mm",null,null,0.65]
[null,null,"0,63mm- ≤100mm"]
[null,null,"0,9mm - ≤ 150mm"]
[null,"Crosstalk Attenuation","> 50 dB/km at audio",null,null,0.65]
[null,"Maximum capacitive unbalance","400 pF per 500m",null,null,0.65]
["4.","Stranding of Cables"]
[null,"Ten pairs and below","Single Unit",null,null,0.65]
[null,"Above ten pairs ",{"$nulls":3},0.65]
[null,"* 25 pairs","Sub-units of 5 pairs"]
[null,"* 50 pairs","Sub-units of 10 pairs"]
[null,"Colour code of sub-units","Unit 1 – Blue",null,null,0.65]
[null,null,"Unit 2 – Orange"]
[null,null,"Unit 3 – Green"]
[null,null,"Unit 4 – Brown"]
[null,null,"Unit 5 – Grey"]
["5.","Tape Lapping of Cables"]
[null,"Material","Paper or Melinex",null,null,0.65]
["6.","Aluminium/Polyethylene Laminate"]
[null,"Nominal thickness","0,15mm – Aluminium",null,null,0.65]
[null,null,"0,04mm – PE"]
[null,"Construction","Aluminium on inside",null,null,0.65]
[null,"Overlap",{"$nulls":3},0.65]
[null,"• Cables < 25mm diam","3mm"]
[null,"• Cables > 25mm diam","6mm"]
[null,"Peel Strength (Aluminium from PE)","0,25 N/nm",null,null,0.65]
[null,"100% coverage when cable bent","15 x diam",null,null,0.65]
[null,"Resistance","Indicate Ω/km",null,null,0.65]
["7.","Identification of Cables"]
[null,"Information required on outer","- Number of pairs",null,null,0.65]
[null,null,"- Conductor size"]
[null,null,"- Manufacturer"]
[null,null,"- Year of manufacture"]
[null,"Identification marks repeated ","Every 350mm or less",null,null,0.65]
["8.","Sheath"]
[null,"Material","Polyethylene",null,null,0.65]
[null,"HV spark withstand capability","According to SANS 62230",null,null,0.65]
[null,"Internal pressure test ","100 kPa for 3 hours",null,null,0.65]
[null,"No ripple or damage to sheath and moisture barrier when cable bent","For at least one turn at 15 x diam",null,null,0.65]
[null,"Water vapour permeation rate","< 0,13Dg / 100mm/week",null,null,0.65]
[null,"Colour","Black Armoured",null,null,0.65]
[null,null,"White Unarmoured"]
[null,"Minimum thickness (Armoured cable thickness in brackets)","4pair - 0,6mm (1,0)",null,null,0.65]
[null,null,"10pair - 0,7mm (1,0)"]
[null,null,"25pair - 0,9mm (1,2)"]
[null,null,"50pair - 1,0mm (1,2)"]
[null," Comply with the following additional requirements (Refer to the  following sections of this standard):"]
[null,"3.8.1 Impact test","YES/NO",null,null,0.65]
[null,"3.8.2 Environmental stress – Cracking","YES/NO"]
[null,"3.8.3 Shrink back test","YES/NO"]
["9."," Armouring of Cables"]
[null,"Material","Galvanised Steel Wire",null,null,0.65]
[null,"Nominal diameter of wire","4pair 0,9mm",null,null,0.65]
[null,null,"10pair 0,9mm"]
[null,null,"25pair 0,9mm"]
[null,null,"50pair 1,25mm"]
["10.","Test Certificates."]
[null,"State the location within the tender documentation where the Test Certificates for the following tests  can be found:"]
[null,"10.1  Conductor elongation at break according to SANS 6282-3, Section 2, elongation at break of wire. ","Specify",null,null,0.65]
[null,"10.2  Conductor spark test according to SANS 62230.","Specify",null,null,0.65]
[null,"10.3 Conductor resistance according to section 4.2","Specify",null,null,0.65]
[null,"10.4  Insulation physical properties  according to SANS 1411-7 Polyethylene (PE) or an equivalent standard. Report shall be provided. ","Specify",null,null,0.65]
[null,"10.5 Sheath spark test according to SANS 62230","Specify",null,null,0.65]
[null,"10.6  Sheath physical properties according to SANS 1411-7 Polyethylene (PE) or an equivalent standard. Report shall be provided.","Specify",null,null,0.65]
[null,"10.7  Sheath pressure test according to section 4.13","Specify",null,null,0.65]
[null,"10.8  Moisture barrier continuity according to section 4.11","Specify",null,null,0.65]
[null,"10.9 Finished cable voltage withstand   according to SANS 6284-3","Specify",null,null,0.65]
["11."," Drumming and Sealing of Cables: State whether the product tendered complies with the following specification:"]
[null,"Cable Drum - according to Telkom Spec 00378","YES/NO",null,null,0.65]
[null,"Markings on drum:"]
[null,"Eskom Order No.","YES/NO"]
[null,"Cable Code & Spec","YES/NO"]
[null,"Gross Mass","YES/NO"]
[null," \"Not to be laid flat\"","YES/NO"]
[null,"\"Sling with bar through centre of drum\"","YES/NO"]
[null,"  Manufacturer","YES/NO"]
[null," Indication of rolling direction","YES/NO"]
[null,"Cable Length","YES/NO"]

{"sheet":"\"Z\" Cable Desk AB","index":2,"n_rows":55,"n_cols":6,"rows_kept":55,"merged":[[0,0,0,5]]}
["240-64813692: MINIATURE CONTROL CABLE REQUIRED FOR TELEPROTECTION SIGNALS ( “18Z” CABLES) - Annex A: Schedules A and B for Desktop Evaluation"]
["ITEM","DESCRIPTION","SCHEDULE A","SCHEDULE B","REMARKS","WEIGHT"]
[1,"Manufacturer Name","Specify",null,null,0.76]
[null,"Location of factory/ manufacturer’s premises","Physical Address",null,null,0.76]
[2,"Voltage rating  (V)",440,null,null,0.76]
[3,"Core details:"]
[null,"(a)   number of cores (18)",18,null,null,0.76]
[null,"(b) conductor area mm2","0.5",null,null,0.76]
[null,"(c) conductor material","Sn annealed Cu",null,null,0.76]
[null,"(d) DC resistance at 20°C  ohms/km","40.1 max",null,null,0.76]
[null,"(e) 50 Hz resistance at 20°C  ohms/km","Specify.",null,null,0.76]
[null,"(f) inductive reactance at 50 Hz ohms/km","0.736 max",null,null,0.76]
[null,"(g) capacitance"]
[null,"(i) all cores to sheath μF/km","Specify",null,null,0.76]
[null,"(ii) between cores  μF/km","Specify",null,null,0.76]
[null,"(h) maximum continuous conductor temperature  °C","Specify",null,null,0.76]
[4,"Insulation material"]
[null,"(a) core insulation compound used","Specify PVC type",null,null,0.76]
[null,"(b) screen insulation compound used","Specify PVC type",null,null,0.76]
[null,"(c) cable sheath compound used","Specify PVC type",null,null,0.76]
[null,"(d) fire propagation properties of finished cable.","Specify",null,null,0.76]
[null,"(e) smoke/acid gas emission for"]
[null,"- core insulation ","Specify",null,null,0.76]
[null,"- bedding and screen insulation","Specify",null,null,0.76]
[null,"- finished cable","Specify",null,null,0.76]
[5,"Screen and armouring"]
[null,"(a) screen material","Cu braid",null,null,0.76]
[null,"(b) screen coverage","80% min. ",null,null,0.76]
[null,"(c) screen thickness","Specify",null,null,0.76]
[null,"(d)   overall screen resistance ohms/km","Specify",null,null,0.76]
[null,"(e) armouring wire material","galv. steel",null,null,0.76]
[null,"(f) armouring wire diameter mm","0.9",null,null,0.76]
[null,"(g) armouring tensile strength N/mm2","Specify",null,null,0.76]
[6,"Core identification"]
[null,"(a) colour coded","Yes",null,null,0.76]
[null,"(b) numbered","No",null,null,0.76]
[null,"(c) colour standards","Specify",null,null,0.76]
[null,"(d) colour stability","Specify",null,null,0.76]
[7,"Complete cable"]
[null,"(a) diameter  mm","Specify",null,null,0.76]
[null,"(b) mass     kg/m","Specify",null,null,0.76]
[null,"(c) drum length ",{"$nulls":3},0.76]
[null,"(i) average m","Specify",null,null,0.76]
[null,"(ii) minimum m","Specify",null,null,0.76]
[null,"(iii) maximum m","Specify",null,null,0.76]
[null,"(d) drum markings","Specify",null,null,0.76]
[8,"Test Certificates"]
[null,"State the location within the tender documentation where the Test Certificates for the following tests  can be found:"]
[null,"(i)     Conductor elongation at break according to SANS 6282-3. ","Specify",null,null,0.76]
[null,"(ii) Insulation physical properties according to SANS  1411-4","Specify",null,null,0.76]
[null,"(iii) Insulation spark test according to SANS 62230","Specify",null,null,0.76]
[null,"(iv) Sheath physical properties according to SANS 1411-7","Specify",null,null,0.76]
[null,"(v)  Finished cable voltage withstand according to  SANS 6284-3","Specify",null,null,0.76]
[null,"(vi) The average capacitance between wire cores shall be measured in a completed cable with all other cores, armouring and screen connected to earth.","Specify",null,null,0.76]
[null,"(vii) The average capacitance between each core and earth shall be measured in a completed cable with all other cores, armouring and screen connected to earth.","Specify",null,null,0.76]