SCHEDULE C: INSULATOR REQUIREMENTS

| INSULATOR TYPE | ITEM 26 SAP 600014 - LONGROD 765kV, 400KN 31mmkV |  |  |
| --- | --- | --- | --- |
| Conceptual Design Drawing No. | N/A |  |  |
| PARAMETER | CLIENT REQUIREMENTS | Comply (Y/N) | Comments |
| MODEL Number |  |  |  |
| Shed Material | Silicone-based |  |  |
| Open Profile | Y/N? |  |  |
| Alternating Sheds | Preferred |  |  |
| Corecover Thickness | mm |  |  |
| Life Expectancy | 50 years |  |  |
| Altitude of Application | 1800m |  |  |
| Temperatures : | Minimum -5 0C Maximum 500C Average 30 0C |  |  |
| Specific Creepage | 31 mm/kV |  |  |
| S/P Ratio | 1.0 |  |  |
| BIL (+) – (@altitude) | 2100 kV |  |  |
| SIL (+) – (@altitude) | 1550 kV |  |  |
| Dry-arcing distance (DAD) with corona rings | 6000 mm |  |  |
| Connecting Length | Shortest Possible Considering DAD limit |  |  |
| Corona Rings : | Live/dead/both |  |  |
| Dimensions | Live end |  |  |
|  | Dead end |  |  |
| Ratings (kA/s) | Live end |  |  |
|  | Dead end |  |  |
| SML | 400 kN |  |  |
| End fittings : |  |  |  |
| Type | Ball-Socket |  |  |
| Size | 28 mm |  |  |
| IEC120 | (Y/N) |  |  |
| Deviations: |  |  |  |