BID SPECIFICATION

STATE INFORMATION TECHNOLOGY AGENCY (SOC) LTD

Registration number 1999/001899/30

| RFB REF. NO: | RFB 2817-2023 |
| --- | --- |
| DESCRIPTION | APPOINTMENT OF A SERVICE PROVIDER FOR MAINTENANCE SUPPORT OF UPS BATTERIES AT VARIOUS SITA SITES FOR A PERIOD OF 60 MONTHS |
| PUBLICATION DATE | 17 OCTOBER 2023 |
| BRIEFING SESSION | COMPULSORY VIRTUAL BRIEFING SESSION DATE: 26 OCTOBER 2023 TIME: 10:00 AM VENUE: MICROSOFT TEAMS Meeting ID: 355 475 792 612 Passcode: 4ajxaF |
| CLOSING DATE FOR QUESTIONS AND ANSWERS | 31 OCTOBER 2023 |
| RFB CLOSING DETAILS | DATE: 13 NOVEMBER 2023 TIME: 11:00 AM (SOUTH AFRICAN TIME) PLACE: TENDER OFFICE, PONGOLA IN APOLLO, 459 TSITSA STREET, ERASMUSKLOOF, PRETORIA (HEAD OFFICE) |
| PUBLIC OPENING OF RFB RESPONSES | N/A |
| RFB VALIDITY PERIOD | 200 DAYS FROM THE CLOSING DATE |

PROSPECTIVE BIDDERS MUST REGISTER ON NATIONAL TREASURY’S CENTRAL SUPPLIER DATABASE PRIOR TO SUBMITTING BIDS.

Contents

ANNEX A:	INTRODUCTION	4

1.	PURPOSE AND BACKGROUND	4

1.1.	PURPOSE	4

1.2.	BACKGROUND	4

2.	SCOPE OF BID	4

2.1.	SCOPE OF WORK	4

2.2.	RELEVANT MAJOR EQUIPMENT OF ELECTRICAL PLANT	5

2.3.	DELIVERY ADDRESS	6

3.	REQUIREMENTS	6

3.1.	SERVICE REQUIREMENTS	6

4.	BID EVALUATION STAGES	8

ANNEX A.1:	EVALUATION REQUIREMENTS	9

5.	ADMINISTRATIVE PRE-QUALIFICATION REQUIREMENTS	9

5.1.	ADMINISTRATIVE PRE-QUALIFICATION VERIFICATION	9

5.2.	ADMINISTRATIVE PRE-QUALIFICATION REQUIREMENTS	9

6.	TECHNICAL MANDATORY	10

6.1.	INSTRUCTION AND EVALUATION CRITERIA	10

6.2.	TECHNICAL MANDATORY REQUIREMENTS	11

6.3.	DECLARATION OF COMPLIANCE	12

ANNEX A.2:	SPECIAL CONDITIONS OF CONTRACT (SCC)	13

7.	SPECIAL CONDITIONS OF CONTRACT	13

7.1.	INSTRUCTION	13

7.2.	SPECIAL CONDITIONS OF CONTRACT	13

7.3.	DECLARATION OF COMPLIANCE	24

ANNEX A.3:	COSTING AND PREFERENCE	26

8.	COSTING AND PREFERENCE	26

8.1.	COSTING AND PREFERENCE EVALUATION	26

8.2.	COSTING CONDITIONS	27

8.3.	DECLARATION OF ACCEPTANCE	28

8.4.	PREFERENCE REQUIREMENTS	28

TERMS AND DEFINITIONS	33

9.	ABBREVIATIONS	33

ANNEX B:	BIDDER SUBSTANTIATING EVIDENCE	34

10.	MANDATORY REQUIREMENT EVIDENCE	34

10.1.	SUPPLIER CERTIFICATION / AFFILIATION REQUIREMENTS	34

10.2.	BIDDER EXPERIENCE AND CAPABILITY	34

10.3.	CIDB REGISTRATION REQUIREMENTS	35

10.4.	PREFERENTIAL GOAL REQUIREMENTS	36

ANNEX C:	CIDB REGISTRATION REQUIREMENT	37

ANNEX D:	MAINTENANCE REQUIREMENTS	38

11.	MAINTENANCE REQUIREMENTS	38

11.1.	UPS Batteries Maintenance Requirements.	38

11.2.	Plant Room Maintenance Requirements	39

11.3.	UPS Batteries Inspection Requirements	39

11.4.	Service Pack Requirements.	40

ANNEX E:	CIDB BASIC GUIDE GENERAL CONDITIONS OF CONTRACT FOR CONSTRUCTION WORKS (GCC 2004)	41

INTRODUCTION

# PURPOSE AND BACKGROUND

## PURPOSE

The purpose of this RFB is to invite Suppliers (hereinafter referred to as “bidders”) to submit bids for appointment of a service provider for maintenance support of Maintenance Support of UPS Batteries at the SITA Beta, Numerus, Erasmuskloof and Pietermaritzburg Sites for a period of sixty (60) months.

## BACKGROUND

The electrical plant maintenance is essential for reliability of power supply for continued operation of critical computer environments. The higher reliability is achieved by having a good maintenance support and rapid response to the emergency interruption of services. The level of expertise, services and work required are not available within SITA and need to be outsourced. The scope of service is based on the schedule for planned maintenance and breakdowns to the UPS system equipment.

# SCOPE OF BID

## SCOPE OF WORK

The high-level scope of work for sites allocated to the contractor under this contract comprises, (but is not limited to):

  - On-site Disaster Recovery Support with a maximum 360-minutes incident response time.

  - On-site Preventive/Routine/Scheduled maintenance with fixed rate based for Specified Services.

  - On-site Corrective/Remedial maintenance. The cost for this item is not deemed part of the Scheduled Maintenance rate. The cost for this item will be based on corrective maintenance labour unit rates and cost-plus percentage mark-up on material.

  - On-site Call Outs. The cost for this item is not deemed part of the Scheduled Maintenance rate. The cost for this item will be based on unit rates for call-out fee per incident as specified on corrective maintenance labour unit rates.

  - On-site Emergency Maintenance followed by a Root Cause Analysis. The cost for this item is not deemed part of the Scheduled Maintenance rate. The cost for this item will be based on corrective maintenance labour unit rates and cost-plus percentage mark-up on material.

  - Support and critical repairs (with a maximum 360-minutes incident response time) on VLA UPS Battery Banks

  - Required service level: Availability 24/7/365 during the sixty (60) months contract period, with a maximum 360-minutess incident response time.

  - Upon SITA’s request, the bidder must provide inspection, and quality assurance services on other SITA electrical contractors’ work performed for SITA of systems that have impact to the equipment performance and services on this scope.

  - Upon SITA’s request, provide services relating to the isolation and commissioning infrastructure specified in this scope.

  - Upon SITA’s requests, service and repairs of similar battery system at other sites. The service will be “works order based” for known corrective maintenance requirements, and be “callout based” (followed by a works order) for power incidents where immediate response is required.

  - The services described under this scope will be required for a period of sixty (60) months. The service will be “works order based” for known corrective maintenance requirements, and be “callout based” (followed by a works order) for power incidents where immediate response is required.

## RELEVANT MAJOR EQUIPMENT OF ELECTRICAL PLANT

Although the electrical plant for which support is required covers a wide span of electrical devices and systems, the major plant components under this contract are detailed below. Bidders should also note that SITA from time to time upgrades the electrical infrastructure for various sites, which means that the type of units and quantities of the units indicated below may change during the contract period.

  - BETA DATA CENTRE - UPS Battery Systems:

  - Battery Bank 1 of 205x YCP35 VLA cells

  - Battery Bank 2 of 205x YCP35 VLA cells

  - Battery Bank 3 of 192x YCP35 VLA cells

  - Battery Bank 4 of 192x YCP35 VLA cells

  - NUMERUS DATA CENTRE - UPS Battery Systems:

- Battery Bank 1 of 204x YCP35 VLA cells

- Battery Bank 2 of 204x YCP35 VLA cells

- Battery Bank 3 of 204x YCP35 VLA cells

- Battery Bank 4 of 240x FHP13 VLA cells

- Battery Bank 5 of 240x FHP13 VLA cells

  - ERASMUSKLOOF - UPS Battery Systems:

- Battery Bank 1 - 192x YCP21 cells 268Ah Vented Lead Acid cells per Battery Bank

- Battery Bank 2 - 192x YCP21 cells 268Ah Vented Lead Acid cells per Battery Bank

- Battery Bank 3 - 192x YCP21 cells 268Ah Vented Lead Acid cells per Battery Bank

  - PIETERMARITZBURG DATA CENTRE - UPS Battery Systems:

- Battery Bank 1 of 216x YCP33 VLA cells

- Battery Bank 2 of 2166x YCP33 VLA cells

## DELIVERY ADDRESS

| No | Site Name | Physical Address |
| --- | --- | --- |
|  | Beta Data Centre | 222 Johannes Ramokhoase Street, Pretoria |
|  | Numerus Data Centre | 35 Hamilton Street, Pretoria |
|  | Erasmuskloof Head Office | 459 Tsitsa Street, Pretoria |
|  | SITA Pietermaritzburg Data centre | 334 Jabu Ndlovu St; Pietermaritzburg; 3201 |

REQUIREMENTS

## SERVICE REQUIREMENTS

  - On-site Disaster Recovery Support with a maximum 360-minutes incident response time.

  - On-site Preventive/Routine/Scheduled maintenance. Scheduled Maintenance will be fixed rate based for Specified Services requirement as detailed in Annex D.

On-site Corrective/Remedial maintenance. The cost for this item is not deemed part of the Scheduled Maintenance rate. The cost for this item will be based on corrective maintenance labour unit rates and cost-plus percentage mark-up on material.

  - On-site Call Outs. The cost for this item is not deemed part of the Scheduled Maintenance rate. The cost for this item will be based on unit rates for call-out fee per incident as specified on corrective maintenance labour unit rates.

  - On-site Emergency Maintenance followed by a Root Cause Analysis. The cost for this item is not deemed part of the Scheduled Maintenance rate. The cost for this item will be based on unit rates for call-out fee per incident as specified on corrective maintenance labour unit rates.

  - Support and critical repairs (with a maximum 360-minutes incident response time) on VLA UPS Battery Banks.

  - Planned, periodic maintenance services on VLA UPS Battery Banks.

  - Required service level: Availability 24/7/365 during the sixty (60) months contract period, with a maximum 360-minutes incident response time.

  - Upon SITA’s request, the bidder must provide inspection, and quality assurance services on other SITA electrical contractors’ work performed for SITA of systems that have impact to the equipment performance and services on this scope.

  - Upon SITA’s requests, service and repairs of similar battery system at other sites. The service will be “works order based” for known corrective maintenance requirements, and be “callout based” (followed by a works order) for power incidents where immediate response is required.

  - Upon SITA’s request, provide services relating to the isolation and commissioning l infrastructure specified in this scope.

  - The services described under this scope will be required for a period of sixty (60) months. The service will be “works order based” for known corrective maintenance requirements, and be “callout based” (followed by a works order) for power incidents where immediate response is required.

# BID EVALUATION STAGES

- The bid evaluation process consists of several stages that are applicable according to the nature of the bid as defined in the table below.

- The bidder must qualify for each stage to be eligible to proceed to the next stage of the evaluation.

Table 1: Bid Evaluation stages.

| Stage | Description | Applicable for this bid YES/NO |
| --- | --- | --- |
| Stage 1 | Administrative pre-qualification verification | YES |
| Stage 2 | Technical Mandatory requirement evaluation | YES |
| Stage 3 | Special Conditions of Contract verification | YES |
| Stage 4 | Cost / Preference evaluation | YES |

EVALUATION REQUIREMENTS

# ADMINISTRATIVE PRE-QUALIFICATION REQUIREMENTS

## ADMINISTRATIVE PRE-QUALIFICATION VERIFICATION

- The bidder must comply with ALL of the bid pre-qualification requirements in order for the bid to be accepted for evaluation.

- If the Bidder fails to comply with any of the administrative pre-qualification requirements, or if SITA is unable to verify whether the pre-qualification requirements are met, then SITA reserves the right to: -

  - Reject the bid and not evaluate it, or

  - Accept the bid for evaluation, on condition that the Bidder must submit within 7 (seven) days any supplementary information to achieve full compliance, provided that the supplementary information is administrative and not substantive in nature.

## ADMINISTRATIVE PRE-QUALIFICATION REQUIREMENTS

- Submission of bid response: The bidder must submit a bid response documentation pack –

  - delivered at the correct physical within the stipulated date and time as specified in the “Invitation to Bid” cover page, and;

  - in the correct format as one (1) original document marked as “ORIGINAL”, one (1) copy marked as “COPY” and soft copies of the submission in PDF on memory stick / USB with pricing schedule in excel format.

- Attendance of briefing session: A Compulsory Virtual Briefing session will be held. The bidder has to sign the briefing session attendance register using the same information (bidder company name, bidder representative person name and contact details) as would be submitted in the bidder’s response document.

- Registered Supplier. The bidder is, in terms of National Treasury Instruction Note 4A of 2016/17, registered as a Supplier on National Treasury Central Supplier Database (CSD).

# TECHNICAL MANDATORY

## INSTRUCTION AND EVALUATION CRITERIA

- The bidder must comply with ALL the requirements as per section 6.2 below by providing substantiating evidence in the form of documentation or information, failing which it will be regarded as “NOT COMPLY”.

- The bidder must provide a unique reference number (e.g. binder/folio, chapter, section, page) to locate substantiating evidence in the bid response. During evaluation, SITA reserves the right to treat substantiation evidence that cannot be located in the bid response as “NOT COMPLY”.

- The bidder must complete the declaration of compliance as per section 6.3 below by marking with an “X” either “COMPLY”, or “NOT COMPLY” with ALL of the technical mandatory requirements, failing which it will be regarded as “NOT COMPLY”.

- The bidder must comply with ALL the TECHNICAL MANDATORY REQUIREMENTS in order for the bid to proceed to the next stage of the evaluation.

- No URL references or links will be accepted as evidence.

## TECHNICAL MANDATORY REQUIREMENTS

| TECHNICAL MANDATORY REQUIREMENTS | Substantiating evidence of compliance (used to evaluate bid) | Evidence reference (to be completed by bidder) |
| --- | --- | --- |
| - BIDDER CERTIFICATION / AFFILIATION REQUIREMENTS The Bidder must be registered at the Department of Labour as an Electrical Contractor. | Attach to ANNEX B a copy of documentation (valid certificate, license, or letter) from the Department of Labour as evidence that the bidder is registered as an Electrical Contractor. Note: SITA reserves the right to verify the information provided. | <provide unique reference to locate substantiating evidence in the bid response – see Annex B, section 10.1> |
| - BIDDER EXPERIENCE AND CAPABILITY - The bidder must have executed maintenance of a Vented Lead Acid Battery Cells or similar at Data Centre or Equivalent High Availability Environment (Hospital, Airport, Bank, or similar High Availability Environments) in the last 10 Years. | The Bidder must provide all of the following reference details from at least two (2) customer/site/project to whom maintenance services was executed on Vented Lead Acid Battery Cells or similar for Data Centre or equivalent High Availability Environment (Hospital, Airport, Bank, or similar High Availability Environments) in the last ten (10) years: - Company name; and - Reference Person Name, Tel and/or email; and - Project Scope of Work; and - Project Start and End-date. Note (1): Failure to complete Table 5 fully as indicated above will result in disqualification. Note (2): SITA reserves the right to verify information provided. | <provide unique reference to locate substantiating evidence in the bid response – see Annex B, section 10.2, table 5> |
| - CIDB REGISTRATION REQUIREMENT The bidder must be registered with Construction Industry Development Board (CIDB) with a minimum rating, of 5EB PE or 5EP PE or 6EB or 6EP or higher. | The Bidder must complete and sign ANNEX C to confirm that the Bidder is registered with the Construction Industry Development Board (CIDB) with a minimum rating, of 5EB PE or 5EP PE or 6EB or 6EP or higher. Note: SITA reserves the right to verify the information provided. | <provide unique reference to locate substantiating evidence in the bid response – see Annex B, section 10.3 and Annex C> |

## DECLARATION OF COMPLIANCE

| DECLARATION | Comply | Not Comply |
| --- | --- | --- |
| The bidder declares by indicating with an “X” in either the “COMPLY” or “NOT COMPLY” column that – - The bid complies with each and every TECHNICAL MANDATORY REQUIREMENT as specified in SECTION 6.2 above; AND - Each and every requirement specification is substantiated by evidence as proof of compliance. |  |  |

SPECIAL CONDITIONS OF CONTRACT (SCC)

# SPECIAL CONDITIONS OF CONTRACT

## INSTRUCTION

- The successful supplier will be bound by Government Procurement: General Conditions of Contract (GCC) as well as this Special Conditions of Contract (SCC), which will form part of the signed contract with the successful Supplier. However, SITA reserves the right to include or waive the condition in the signed contract.

- SITA reserves the right to –

  - Negotiate the conditions, or

  - Automatically disqualify a bidder for not accepting these conditions.

  - Award to multiple bidders.

  - Not to award; or

  - To do a partial award.

- In the event that the bidder qualifies the proposal with own conditions, and does not specifically withdraw such own conditions when called upon to do so, SITA will invoke the rights reserved in accordance with sub-section 7.1(2) above.

- The bidder must complete the declaration of acceptance as per section 7.3 below by marking with an “X” either “ACCEPT ALL” or “DO NOT ACCEPT ALL”, failing which the declaration will be regarded as “DO NOT ACCEPT ALL” and the bid will be disqualified.

## SPECIAL CONDITIONS OF CONTRACT

- CONTRACTING CONDITIONS

  - Formal Contract. The Supplier must enter into a formal written Contract (Agreement) with SITA.

  - Right of Award. SITA reserves the right to award the contract for required goods or services to multiple Suppliers.

  - Right to Audit. SITA reserves the right, before entering into a contract, to conduct or commission an external service provider to conduct a financial audit or probity to ascertain whether a qualifying bidder has the financial wherewithal or technical capability to provide the goods and services as required by this tender.

- DELIVERY ADDRESS

The supplier must deliver the required products or services at as indicated in Section 2.3, Delivery Address.

- DELIVERY SCHEDULE

  - The scope of work (Section 2.1) and Section 3 (Requirements) will be over the period of sixty (60) months.

  - The Supplier is responsible to perform the work as outlined in the following Work Breakdown Structure (WBS):

| WBS | Statement of Work | Delivery Timeframe |
| --- | --- | --- |
|  | On-site Disaster Recovery Support with a maximum 360-minutes incident response time. | Over the duration of sixty (60) months |
|  | On-site Preventive/Routine/Scheduled maintenance. |  |
|  | On-site Corrective/Remedial maintenance. |  |
|  | On-site Call Outs. |  |
|  | On-site Emergency Maintenance followed by a Root Cause Analysis. |  |
|  | Support and critical repairs (with a maximum 360-minutes incident response time) on UPS Systems of which the major components. |  |
|  | Planned, periodic maintenance services on the following major components: - Support and repairs on Modular UPS Units - Support and repairs on VLA Battery Banks |  |
|  | Required service level: Availability 24/7/365 during the sixty (60) months contract period, with a maximum 360-minutess incident response time. |  |
|  | Upon SITA’s request, the bidder must provide inspection, and quality assurance services on other SITA electrical contractors’ work performed for SITA of systems that have impact to the equipment performance and services on this scope. |  |
|  | Upon SITA’s request, provide services relating to the isolation and commissioning infrastructure specified in this scope. |  |
|  | The services described under this scope will be required for a period of sixty (60) months. The service will be “works order based” for known corrective maintenance requirements, and be “callout based” (followed by a works order) for power incidents where immediate response is required. |  |

- SERVICES AND PERFORMANCE METRICS

  - During Maintenance support period the Supplier is responsible to provide the following services as specified in the Service Breakdown Structure (SBS):

| SBS | Service Element | Service Level |
| --- | --- | --- |
|  | Emergency Contact during warranty and maintenance periods | 24h x 7days x 52weeks |
|  | Incident Response during warranty and maintenance periods | Maximum 360-minutes |

- SERVICE LEVEL REQUIREMENTS, WARRANTIES, AND PENALTIES

All Service Level time lines indicated below are relevant any time of day, any time of year, during the contract period.

The following SLA time windows are applicable to this contract:

  - The Change Control windows will be planned by both parties (SITA and the contractor) and practical timeslots (which must not exceed the specified maximum number of timeslots or the specified maximum duration of each timeslot) and dates be agreed to. The scope of work to be executed and completed for each of the Change Control windows will be agreed to by both SITA and the contractor.

  - SITA will notify the contractor telephonically that a problem is experienced at (in scope) site, and that he needs to attend to site immediately. The contractor shall provide the number of his emergency contact details, or representative that needs to be contacted for this purpose. The contractor shall have a qualified technician on site within 360360 minutes from the first telephonic call/call attempt (unless SITA agrees to an alternative response time with the contractor during the call). Plant / Infrastructure repairs shall start within 60minutes from the first telephonic call/call attempt (unless SITA agrees to an alternative response time with the contractor during the call or on-site inspection). The 360 minutes requirement will be heavily dependent on the severity of the incident. If the incident is less severe, SITA will settle for slightly longer response times. SITA will be the judge of the incident severity. Should the Support Contractor’s response time to site exceed the specified 360 minutes (or alternative duration as agreed to by SITA) an equivalent penalty fee will be applied, per incident.

  - Penalties shall be applied at SITA’s discretion, following the breach of a Service Level Agreement. The contractor shall have the opportunity to provide a report, within seven (7) calendar days following the incident or SITA’s notice of penalty, indicating why the contractor deem the penalty not to be applied. SITA shall take this into consideration, but SITA’s decision shall be final and shall deduct penalty values from the monthly invoices for the relevant site(s).

- SUPPLIER PERFORMANCE REPORTING

  - The Supplier will report on a quarterly basis to SITA/Client during the duration of the maintenance contract at the SITA/Client on the progress of the preceding month.

  - The Supplier is required to generate regular reports as outputs during the maintenance and support cycle within the following service levels (the report type will drive the service level agreement; definition of the content of each report type will be finalised at the time of concluding the contracted service level agreement).

- CERTIFICATION, EXPERTISE AND QUALIFICATION

- The Bidder must be registered at the Department of Labour as an Electrical Contractor.

- The bidder must have executed maintenance of a Vented Lead Acid Battery Cells or similar at Data Centre or Equivalent High Availability Environment to in the last 10 years.

- The bidder must be registered with Construction Industry Development Board (CIDB) with a minimum rating, of 5EB PE or 5EP PE or 6EB or 6EP or higher

- The Supplier represents that,

  - it has the necessary expertise, skill, qualifications and ability to undertake the work required in terms of the Statement of Work or Service Definition with the technical personnel qualified and trained.

  - it is committed to provide the Services; and

  - perform all obligations detailed herein without any unplanned interruption to the Customer.

- The Supplier must provide the service in a good and workmanlike manner and in accordance with the practices and high professional standards used in well-managed operations performing services similar to the Services;

- The Supplier must perform the Services in the most cost-effective manner consistent with the level of quality and performance as defined in Statement of Work or Service Definition;

- Electrical Work. The Supplier must ensure that Electrical Work is performed as prescribed by the Occupation Health and Safety Act (Act 85 of 1993 as amended), Electrical Regulations 2009, including:

  - The standard of work conforms to SANS 10142-1: The code of practice for wiring of premises; and

  - Any Electrical installation or alteration is certified after completion of work by means of a Certificate of Compliance.

- LOGISTICAL CONDITIONS

- Hours of work, 08h00 – 16h00.

- Provision to be made for work which will be Saturday and Sunday.

- It must be noted that Beta, Numerus, Erasmuskloof and Pietermaritzburg Data Centres is a live site, and downtimes are limited. All site services will have to be restored at the end of the scheduled downtime. The Supplier to make sure all the resources, tools and equipment are available to work continuously during that period to complete all the scheduled tasks during that period.

- All the work that require downtime of services or have potential to cause unplanned downtime will have to be approved before commencing. The approval will have to follow SITA change management process.

- The scheduled work that does not require downtime, those can be completed during hours in 7(a) and 7(b).

- In the event that SITA grants the Supplier permission to access SITA's Environment including hardware, software, internet facilities, data, telecommunication facilities and/or network facilities remotely, the Supplier must adhere to SITA's relevant policies and procedures (which policy and procedures are available to the Supplier on request) or in the absence of such policy and procedures, in terms of, best industry practice.

- Tools of Trade. The Supplier must bring their necessary tools of trade in order for them to perform their duties adequately. This includes relevant software and passwords to access the UPS system diagnostic tools.

- On-site and Remote Support. The Supplier must give off-site and remote support, and only when off-site support is not sufficient, then on-site support will be required upon approval by SITA representative.

- Support and Help Desk. After hours helpdesk support is required for the period of the maintenance support.

- Emergency Maintenance & Call Outs: The activity involved with restoring, repairing or replacing on a non-scheduled maintenance basis. This maintenance activity would be a result of a service affecting or possible service affecting defect resulting in the loss of operation or potential loss of operation of any part or component of the electrical installation at the listed sites.

- Emergency Maintenance action shall be required at any time day or night including weekends and holidays. The Emergency maintenance response times shall meet or exceed the Service Level Agreements timelines set within this document.

- During Emergency Maintenance action the Support contractor’s objective shall always be to prevent a site failure or service failure by any means possible.

- Where the input power to an UPS unit on site will be interrupted for more than 10 minutes, the contractor must have technician in attendance on site to shut down and recommission the UPS units.

- Where the contractor will work on the input power to any UPS units, and the UPS units does not require an intentional shut down, the contractor must still have an technician on site to immediately recommission the UPS units in the event of an unintentional UPS shutdown.

- SITA has no As Built records available of the existing electrical installations or major electrical plant components.

- SKILLS TRANSFER AND TRAINING

  - The Supplier must provide training on the proposed solution or product to technical staff and operator to enable SITA to operate and support the product or solution after implementation.

- REGULATORY, QUALITY AND STANDARDS

  - The Supplier must for the duration of the contract ensure compliance with ISO/IEC General Quality Standards, and Protection of Personal Information Act (POPIA);

  - The Supplier must for the duration of the contract ensure compliance with General Quality Standards, ISO 9001;

  - The Supplier must for the duration of the contract ensure compliance with the project specification and listed standards.

- PERSONNEL SECURITY CLEARANCE

  - Company security screening: The supplier may be required to undergo a company security screening conducted by the State Security Agency (SSA). Should the SSA find the supplier not suitable after the conduct of the security screening, the business relationship will be terminated. The following documentation will be required for the company security screening process to be conducted:

    - Copy of company registration documentation;

    - Copy(ies) of identity documentation of Director(s), Member(s) or Trustee(s);

    - Copy of valid tax clearance certificate.

  - Security suitability check for individuals: SITA may, at its own discretion and in line with its policies and procedures, require employees of the supplier to be subjected to a security suitability check before commencement of a project or delivering of a service. The security suitability check is conducted by SITA in order to ensure that individuals meet the minimum-security requirements and also to verify personal information. The supplier will be required to replace any employee(s) who is found to be not suitable after the conduct of the security screening. The following documentation will be required for the security suitability check:

    - Copy of identity document;

    - Copy(ies) of qualification(s) if SITA requires verification thereof;

    - Fingerprints – will be taken electronically;

    - Signed consent form for the conduct of background checks.

  - Security clearance: A security clearance, issued by either the SSA or Defence Intelligence (DI) is required if any employee of the supplier will have or may gain access to classified information throughout the duration of the project or in the process of delivering a service. The level of security clearance required – Confidential, Secret or Top Secret, will be determined at the sole discretion of SITA. The supplier will have to replace any employee who do not qualify for a security clearance or is found not suitable by the SSA or DI. The following documentation will be required for the security clearance process:

    - Completed Z204 or DD1057 security clearance application form;

    - Fingerprints;

    - Personal documentation of the applicant, including but not limited to, identity document, passport, marriage certificate (if applicable), divorce order (if applicable), qualifications, salary advice and bank statements.

- CONFIDENTIALITY AND NON-DISCLOSURE CONDITIONS

- The Supplier, including its management and staff, must before commencement of the Contract, sign a non-disclosure agreement regarding Confidential Information.

- Confidential Information means any information or data, irrespective of the form or medium in which it may be stored, which is not in the public domain and which becomes available or accessible to a Party as a consequence of this Contract, including information or data which is prohibited from disclosure by virtue of:

    - the Promotion of Access to Information Act, 2000 (Act no. 2 of 2000);

    - being clearly marked "Confidential" and which is provided by one Party to another Party in terms of this Contract;

    - being information or data, which one Party provides to another Party or to which a Party has access because of Services provided in terms of this Contract and in which a Party would have a reasonable expectation of confidentiality;

    - being information provided by one Party to another Party in the course of contractual or other negotiations, which could reasonably be expected to prejudice the right of the non-disclosing Party;

    - being information, the disclosure of which could reasonably be expected to endanger a life or physical security of a person;

    - being technical, scientific, commercial, financial and market-related information, know-how and trade secrets of a Party;

    - being financial, commercial, scientific or technical information, other than trade secrets, of a Party, the disclosure of which would be likely to cause harm to the commercial or financial interests of a non-disclosing Party; and

    - being information supplied by a Party in confidence, the disclosure of which could reasonably be expected either to put the Party at a disadvantage in contractual or other negotiations or to prejudice the Party in commercial competition; or

    - information the disclosure of which would be likely to prejudice or impair the safety and security of a building, structure or system, including, but not limited to, a computer or communication system; a means of transport; or any other property; or a person; methods, systems, plans or procedures for the protection of an individual in accordance with a witness protection scheme; the safety of the public or any part of the public; or the security of property; information the disclosure of which could reasonably be expected to cause prejudice to the defence of the Republic; security of the Republic; or international relations of the Republic; or plans, designs, drawings, functional and technical requirements and specifications of a Party, but must not include information which has been made automatically available, in terms of the Promotion of Access to Information Act, 2000; and information which a Party has a statutory or common law duty to disclose or in respect of which there is no reasonable expectation of privacy or confidentiality;

- Notwithstanding the provisions of this Contract, no Party is entitled to disclose Confidential Information, except where required to do so in terms of a law, without the prior written consent of any other Party having an interest in the disclosure;

- Where a Party discloses Confidential Information which materially damages or could materially damage another Party, the disclosing Party must submit all facts related to the disclosure in writing to the other Party, who must submit information related to such actual or potential material damage to be resolved as a dispute;

- Parties may not, except to the extent that a Party is legally required to make a public statement, make any public statement or issue a press release which could affect another Party, without first submitting a written copy of the proposed public statement or press release to the other Party and obtaining the other Party's prior written approval for such public statement or press release, which consent must not unreasonably be withheld.

- GUARANTEE AND WARRANTIES

The Supplier warrants that:

- The warranty of goods supplied under this contract remains valid for twelve (12) months after the goods, or any portion thereof as the case may be, have been delivered to and accepted at the final destination indicated in the contract, or for eighteen (18) months after the date of shipment from the port or place of loading in the source country, whichever period concludes earlier;

- as at Commencement Date, it has the rights, title and interest in and to the Product or Services to deliver such Product or Services in terms of the Contract and that such rights are free from any encumbrances whatsoever;

- the Product is in good working order, free from Defects in material and workmanship, and substantially conforms to the Specifications, for the duration of the Warranty period;

- during the Warranty period any defective item or part component of the Product be repaired or replaced within 3 (three) days after receiving a written notice from SITA;

- the Products is maintained during its Warranty Period at no expense to SITA;

- the Product possesses all material functions and features required for SITA’s Operational Requirements;

- the Product remains connected or Service is continued during the term of the Contract;

- all third-party warranties that the Supplier receives in connection with the Products including the corresponding software and the benefits of all such warranties are ceded to SITA without reducing or limiting the Supplier’s obligations under the Contract;

- no actions, suits, or proceedings, pending or threatened against it or any of its third-party suppliers or sub-contractors that have a material adverse effect on the Supplier’s ability to fulfil its obligations under the Contract exist;

- SITA is notified immediately if it becomes aware of any action, suit, or proceeding, pending or threatened to have a material adverse effect on the Supplier’s ability to fulfil the obligations under the Contract;

- any Product sold to SITA after the Commencement Date of the Contract remains free from any lien, pledge, encumbrance or security interest;

- SITA’s use of the Product and Manuals supplied in connection with the Contract does not infringe any Intellectual Property Rights of any third party;

- the information disclosed to SITA does not contain any trade secrets of any third party, unless disclosure is permitted by such third party;

- it is financially capable of fulfilling all requirements of the Contract and that the Supplier is a validly organized entity that has the authority to enter into the Contract;

- it is not prohibited by any loan, contract, financing arrangement, trade covenant, or similar restriction from entering into the Contract;

- the prices, charges and fees to SITA as contained in the Contract are at least as favourable as those offered by the Supplier to any of its other customers that are of the same or similar standing and situation as SITA; and

- any misrepresentation by the Supplier amounts to a breach of Contract.

- INTELLECTUAL PROPERTY RIGHTS

- SITA retains all Intellectual Property Rights in and to SITA's Intellectual Property. As of the Effective Date, the Supplier is granted a non-exclusive license, for the continued duration of this Contract, to perform any lawful act including the right to use, copy, maintain, modify, enhance and create derivative works of SITA's Intellectual Property for the sole purpose of providing the Products or Services to SITA pursuant to this Contract; provided that the Supplier must not be permitted to use SITA's Intellectual Property for the benefit of any entities other than SITA without the written consent of SITA, which consent may be withheld in SITA's sole and absolute discretion. Except as otherwise requested or approved by SITA, which approval is in SITA's sole and absolute discretion, the Supplier must cease all use of SITA's Intellectual Property, at of the earliest of:

    - termination or expiration date of this Contract;

    - the date of completion of the Services; and

    - the date of rendering of the last of the Deliverables.

- If so required by SITA, the Supplier must certify in writing to SITA that it has either returned all SITA Intellectual Property to SITA or destroyed or deleted all other SITA Intellectual Property in its possession or under its control.

- SITA, at all times, owns all Intellectual Property Rights in and to all Bespoke Intellectual Property.

- Save for the license granted in terms of this Contract, the Supplier retains all Intellectual Property Rights in and to the Supplier’s pre-existing Intellectual Property that is used or supplied in connection with the Products or Services.

- COUNTER CONDITIONS

Bidders’ attention is drawn to the fact that amendments to any of the Bid Conditions or setting of counter conditions by bidders may result in the invalidation of such bids.

- FRONTING

  - The SITA supports the spirit of Broad Based Black Economic Empowerment and recognizes that real empowerment can only be achieved through individuals and businesses conducting themselves in accordance with the Constitution and in an honest, fair, equitable, transparent and legally compliant manner. Against this background the SITA any form of fronting.

  - The SITA, in ensuring that bidders conduct themselves in an honest manner will, as part of the bid evaluation processes, conduct or initiate the necessary enquiries/investigations to determine the accuracy of the representation made in bid documents. Should any of the fronting indicators as contained in the Guidelines on Complex Structures and Transactions and Fronting, issued by the Department of Trade and Industry, be established during such enquiry/investigation, the onus will be on the bidder / contractor to prove that fronting does not exist. Failure to do so within a period of fourteen (14) days from date of notification may invalidate the bid / contract and may also result in the restriction of the bidder/contractor to conduct business with the public sector for a period not exceeding ten (10) years, in addition to any other remedies SITA may have against the bidder/contractor concerned.

- BUSINESS CONTINUITY AND DISASTER RECOVERY PLANS

The bidder confirms that they have written business continuity and disaster recovery plans that define the roles, responsibilities and procedures necessary to ensure that the required services under this bid specification is in place and will be maintained continuously in the event of a disruption to the bidder’s operations, regardless of the cause of the disruption.

- FIRE SUPPRESSION AND FIRE DETECTION SYSTEMS

- The contractor must take care during his operations not to activate and discharge the automatic fire suppression system. SITA will place the automatic fire suppression system into Manual mode during the contractor’s work on site, should he request SITA to do so. Should the contractor or his sub-contractor(s) manage to activate and discharge the automatic fire suppression system, the refill of the suppression gas / agent shall be for the contractor’s account.

- The contractor must take care during his operations not to activate the fire detection system and cause an alarm on the fire panel. Should the contractor or his sub-contractor(s) manage to activate the fire detection system and in the process cause an alarm on the fire panel, the callout cost for the fire detection contractor to reset the panel and the air conditioning contractor to restart the air conditioning units shall be for the contractor’s account.

- OCCUPATIONAL HEALTH AND SAFETY

  - The contractor must provide within one month of contract commencement all his technical staff used on the SITA contract’s Occupational Health and Safety Training Certificates.

  - The contractor must provide within one week of contract commencement the details of his occupational health and safety representative for this contract.

  - The contractor must submit a Health and Safety plan to SITA covering the full scope of work under this document for approval within three weeks after signature of the contract. Any changes and or improvements as requested by SITA must be resubmitted within two weeks.

  - The safety of SITA personnel and visitors to SITA premises must be placed first, at all times and great care must be taken not to damage any infrastructure or equipment.

  - Provide SITA with the compliant safety file.

- SUPPLIER DUE DILIGENCE

SITA reserves the right to conduct supplier due diligence prior to final award or at any time during the Contract period and this may include pre-announced/non-announced site visits. During the due diligence process the information submitted by the Supplier will be verified and any misrepresentation thereof may disqualify the bid or Contract in whole or parts thereof.

- PREFERENCE GOAL REQUIREMENTS

  - The Bidder’s commitment for the Preference Goal Requirements in this tender will be legally binding and the Bidder needs to perform against their commitment for the duration of the contract which will form part of the Contractual Agreement.

  - The Bidder must sustain, or improve the company’s BBBEE Level for the duration of the contact which will form part of the Contractual Agreement.

  - Performance of Preference Goal Requirements will be determined annually. Bidders must submit their Preference status report to SITA indicating progress against the Bidder’s Preferential commitments within 30 days after each quarter from the commencement date of the contract.

  - Bidders need to keep auditable substantive records / evidence and upon request by SITA must be made available for audit and, or due diligence purposes.

  - SITA reserves the right to require from a Bidder, either before a bid is adjudicated or at any time subsequently, to substantiate any claim with regards to preferences, in any manner required by SITA.

  - SITA reserves the right to verify information / evidence provided by the Bidder.

  - SITA reserves the right to introduce a penalty of 1% of the overall annual year spent by SITA for the prior year if the Bidder fails to comply to paragraphs (a), (b) and (c) above.

## DECLARATION OF COMPLIANCE

| DECLARATION | ACCEPT ALL | DO NOT ACCEPT ALL |
| --- | --- | --- |
| - The bidder declares to ACCEPT ALL the Special Condition of Contract as specified in section 7.2 above by indicating with an “X” in the “ACCEPT ALL” column, OR - The bidder declares to NOT ACCEPT ALL the Special Conditions of Contract as specified in section 7.2 above by - - Indicating with an “X” in the “DO NOT ACCEPT ALL” column, and; - Provide reason and proposal for each of the conditions that is not accepted. |  |  |
| Comments by bidder: Provide reason and proposal for each of the conditions not accepted as per the format: Condition Reference: Reason: Proposal: |  |  |

COSTING AND PREFERENCE

# COSTING AND PREFERENCE

## COSTING AND PREFERENCE EVALUATION

- In terms of the SITA Preferential Procurement Policy (PPP), the following preference point system is applicable for this Bid:

  - the 80/20 system (80 Price, 20 Specific Goals) for requirements with a Rand value of up to R50 000 000 (all applicable taxes included); or

  - the 90/10 system (90 Price and 10 Specific Goals) for requirements with a Rand value above R50 000 000 (all applicable taxes included).

- The Bidder must complete either the 80/20 or 90/10 preference point system based on the offer submitted by the Bidder and submit proof of documentation required in terms of this tender.

- SITA reserve the right to apply either the 80/20, or 90/10 preference point system based on the following conditions:

  - If the lowest acceptable bid price is up to and including R50 000 000 (all applicable taxes included) then the 80/20 preferential point system will apply to all acceptable bids; or

  - If the lowest acceptable bid price is above R50 000 000 (all applicable taxes included) then the 90/10 preferential point system will apply to all acceptable bids;

- Points will be allocated for each of the Preferential Goal Requirements for this tender as indicated in table 3, dependant on paragraphs (2) and (3) above.

- Points for this tender shall be awarded for:

  - Price; and

  - Preference points for specific goals.

- The maximum points for this tender will be allocated as follows, subject to paragraph 4 above.

Table 2: Points allocation

| Description | Points Table 4A | Points Table 4B |
| --- | --- | --- |
| Price | 80 | 90 |
| Preference points for specific goals | 20 | 10 |
| Total points for Price and preference points for specific goals | 100 | 100 |

## COSTING CONDITIONS

- SOUTH AFRICAN PRICING

The total price must be VAT inclusive and be quoted in South African Rand (ZAR).

- TOTAL PRICE

  - Bidder will be bound by the following general costing and pricing conditions and SITA reserves the right to negotiate the conditions or automatically disqualify the bidder for not accepting these conditions:

  - All quoted prices are the total price for the entire scope of required services and deliverables to be provided by the bidder.

  - The cost of delivery, labour, S&T, overtime, etc. must be included in this bid.

  - All additional costs must be clearly specified.

  - The bidder to ensure the accuracy and calculation of the values used in the pricing schedule corresponds quantities and unit prices.

  - All the rates for specified/scheduled services must include travel to the relevant site, labour, material and tools and the specified service pack required to perform the specified services.

  - SITA will budget for provisional amounts for corrective/remedial materials and spares to be purchased.

  - Percentage mark-up on materials for corrective/remedial to be purchased may not exceed 15%.

  - Bidders will complete the bid pricing schedule in the Excel spreadsheet format provided and include this as part of their submission. The soft copy on USB shall be in excel format.

  - All the services will be on work order basis and actual quantities might change.

  - The indicative corrective maintenance rates will be used for payments of corrective/remedial maintenance.

  - All the rates for specified/scheduled services must include travel to the relevant site, labour, material and tools and the specified service pack required to perform the specified services.

Note:  SITA reserves the right to negotiate pricing with the successful bidder prior to the award as well as envisaged quantities.

  - These conditions will form part of the Contract between SITA and the bidder. However, SITA reserves the right to include or waive the condition in the Contract.

  - The bidder must complete the declaration of acceptance as per section 8.3 below by marking with an “X” either “ACCEPT ALL”, or “DO NOT ACCEPT ALL”, failing which the declaration will be regarded as “DO NOT ACCEPT ALL” and the bid will be disqualified.

## DECLARATION OF ACCEPTANCE

| DECLARATION | ACCEPT ALL | DO NOT ACCEPT ALL |
| --- | --- | --- |
| - The bidder declares to ACCEPT ALL the Costing and Pricing conditions as specified in section 8.2 above by indicating with an “X” in the “ACCEPT ALL” column, or - The bidder declares to NOT ACCEPT ALL the Costing and Pricing Conditions as specified in section 8.2 above by - - Indicating with an “X” in the “DO NOT ACCEPT ALL” column, and; - Provide reason and proposal for each of the condition not accepted. |  |  |
| Comments by bidder: Provide the condition reference, the reasons for not accepting the condition. |  |  |

## PREFERENCE REQUIREMENTS

# 8.4.1	INSTRUCTION AND POINT ALLOCATION

- The bidder must complete in full all the PREFERENCE requirements.

- Allocation of points per requirements: The points allocation of bidders’ responses to the requirements will be determined by the completeness, relevance and accuracy of substantiating evidence.

- Points will be allocated for each PREFERENCE requirement as per the criteria set in tables 4A, or 4B, based on the offer submitted by the Bidder.

- The bidder must provide a unique reference number (e.g. binder/folio, chapter, section, page) to locate substantiating evidence in the bid response. During evaluation, SITA reserves the right to treat substantiation evidence that cannot be located in the bid response, as “NOT COMPLY”. The evidence needs to be attached to ANNEX B.

- Preference Goal Requirements:

  - The Bidder must complete either the 90/10 or 80/20 preference point system based on the offer submitted by the Bidder and submit proof or documentation required in terms of this tender.

  - The specific Preferential Goal Requirements for this tender is indicated in table 3 below.

  - The Bidder must indicate their commitment to claim points for each of the preference points by signing at par 4.5 in the Invitation to Bid document.

  - Failure on the part of a bidder to submit proof or documentation required or to comply to paragraph (b) above in terms of this tender to claim preference points for the Preference Goal Requirements for this tender, will be interpreted to mean that preference points are not claimed.

  - The Bidder’s commitment for the Preference Goal Requirements in this tender will be legally binding and the Bidder needs to perform against their commitment for the duration of the contract which will form part of the Contractual Agreement.

  - The Bidder must sustain, or improve the company’s BBBEE Level for the duration of the contact which will form part of the Contractual Agreement.

  - Performance of Preference Goal Requirements will be determined annually. Bidders must submit their Preference status report to SITA indicating progress against the Bidder’s Preferential commitments within 30 days after each quarter from the commencement date of the contract.

  - Bidders need to keep auditable substantive records / evidence and upon request by SITA must be made available for audit and, or due diligence purposes.

  - SITA reserves the right to require from a Bidder, either before a bid is adjudicated or at any time subsequently, to substantiate any claim with regards to preferences, in any manner required by SITA.

  - SITA reserves the right to verify information / evidence provided by the Bidder.

  - SITA reserves the right to introduce a penalty of 1% of the overall annual year spent by SITA for the prior year if the Bidder fails to comply to paragraphs (e), (f) and (g) above.

Table 3 : Preference Goal Requirements (Specific Goals)

| Preference Goal Requirement # | Preferential Goal Requirements (Specific Goals) |  |  |
| --- | --- | --- | --- |
|  | Preferential Goal Requirements allocated for this tender | Substantiating evidence and evidence reference to be completed by bidder. Evaluation per requirement: Each requirement indicated in the table below must be completed and points will be allocated based on the evidence required below: | Evidence reference |
|  | B-BBEE Requirements |  |  |
| 1) | B-BBEE Requirements: Promotion of Transformational Objectives. | Evidence: The Bidder must provide a copy of relevant evidence for the Preferential Goal points which the Bidder qualifies for. Points allocation: Points will be allocated for bidders that meets the requirements as indicated in either table 4A, or 4B in section 8.4.1. | <provide unique reference to locate substantiating evidence in the bid response – Annex B, section 10.4> |

Table 4A: B-BBEE Points as part of the Preference Goal requirements

Note: Bidder to select the section for points they wish to claim (Mark as Y=Yes) in the table belo

|  |  |  |  | Ownership of at least 51% of People who are: |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Reference # | Contributor Level as defined in the Broad-Based Black Economic Empowerment Act | Local Entity | EME/QSEs | Woman Owned | Youth Owned | Owned by People living with disabilities | Score | Bidder to select the section for points they wish to claim (Mark as Y= Yes) |
|  | (A) | (B) | (C) | (D) | (E) | (F) | (G) |  |
| 1 | Level 1 | 0 | 4 | 8 | 6 | 2 | 20 |  |
| 2 | Level 1 | 0 | 4 | 8 | 6 | 0 | 18 |  |
| 3 | Level 1 | 0 | 4 | 8 | 0 | 0 | 12 |  |
| 4 | Level 2 and 3 | 0 | 2 | 4 | 2 | 2 | 10 |  |
| 5 | Level 2 and 3 | 0 | 2 | 4 | 2 | 0 | 8 |  |
| 6 | Level 2 and 3 | 0 | 2 | 4 | 0 | 0 | 6 |  |
| 7 | Level 4 and 5 | 0 | 1 | 2 | 1 | 1 | 5 |  |
| 8 | Level 4 and 5 | 0 | 1 | 2 | 1 | 0 | 4 |  |
| 9 | Level 4 and 5 | 0 | 1 | 2 | 0 | 0 | 3 |  |
| 10 | Level 6 | 0 | 0 | 0 | 0 | 0 | 0 |  |
| 11 | Level 7 | 0 | 0 | 0 | 0 | 0 | 0 |  |
| 12 | Level 8 | 0 | 0 | 0 | 0 | 0 | 0 |  |
| 13 | Non-Contributor | 0 | 0 | 0 | 0 | 0 | 0 |  |
|  | Total Maximum Score Allocation: 20 G= A+B+C+D+E+F |  |  |  |  |  |  |  |

Table 4 B: B-BBEE Points as part of the Preference Goal requirements (Preferential Goal Requirements for (90/10) system)

Note: Bidder to select the section for points they wish to claim (Mark as Y=Yes) in the table below.

|  |  |  |  | Ownership of at least 51% of People who are: |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Reference # | Contributor Level as defined in the Broad-Based Black Economic Empowerment Act | Local Entity | EME/QSEs | Woman Owned | Youth Owned | Owned by People living with disabilities | Score | Bidder to select the section for points they wish to claim (Mark as Y= Yes) |
|  | (A) | (B) | (C) | (D) | (E) | (F) | (G) |  |
| 1 | Level 1 | 0 | 2 | 4 | 3 | 1 | 10 |  |
| 2 | Level 1 | 0 | 2 | 4 | 3 | 0 | 9 |  |
| 3 | Level 1 | 0 | 2 | 4 | 0 | 0 | 6 |  |
| 4 | Level 2 and 3 | 0 | 1 | 2 | 1 | 1 | 5 |  |
| 5 | Level 2 and 3 | 0 | 1 | 2 | 1 | 0 | 4 |  |
| 6 | Level 2 and 3 | 0 | 1 | 2 | 0 | 0 | 3 |  |
| 7 | Level 4 and 5 | 0 | 0,5 | 1 | 0,5 | 0,5 | 2,5 |  |
| 8 | Level 4 and 5 | 0 | 0,5 | 1 | 0,5 | 0 | 2 |  |
| 9 | Level 4 and 5 | 0 | 0,5 | 1 | 0 | 0 | 1,5 |  |
| 10 | Level 6 | 0 | 0 | 0 | 0 | 0 | 0 |  |
| 11 | Level 7 | 0 | 0 | 0 | 0 | 0 | 0 |  |
| 12 | Level 8 | 0 | 0 | 0 | 0 | 0 | 0 |  |
| 13 | Non-Contributor | 0 | 0 | 0 | 0 | 0 | 0 |  |
| Total Maximum Score Allocation: |  |  | 10 |  |  |  |  |  |

G= A+B+C+D+E+F

- TERMS AND DEFINITIONS

# ABBREVIATIONS

BBBEE	Broad Based Black Economic Empowerment

CSD		Central Supplier Database

EME		Exempted Micro Enterprise

GCC		General Condition of Contract

ICT		Information and Communication Technology

IEC		International Electro-technical Commission

ISO		International Standardization Organization

N/A		Not Applicable

NT		National Treasury

OEM		Original Equipment Manufacturer

OSM		Original Software Manufacturer

POC		Proof of Concept

QSE		Qualifying Small Enterprise

RFA		Request for Accreditation

RFB		Request for Bid

RFP		Request for Proposal

RFQ		Request for Quotation

RSA		Republic of South Africa

SBD		Standard Bidding Document

SCC		Special Condition of Contract

SCM		Supplier Chain Management

SITA		State Information Technology Agency

SMME	Small Medium and Micro Enterprise

TCV		Total Contract Value

UPS		Uninterrupted Power Supply

USD		United States Dollar

VAT		Value Added Tax

VLA		Vented Lead Acid

ZAR 		South African Rand

BIDDER SUBSTANTIATING EVIDENCE

# MANDATORY REQUIREMENT EVIDENCE

## SUPPLIER CERTIFICATION / AFFILIATION REQUIREMENTS

- Attach a copy of documentation (valid certificate, license, or letter) from the Department of Labour as evidence that the bidder is registered as an Electrical Contractor here.

- Note:

SITA reserves the right to verify the information provided.

## BIDDER EXPERIENCE AND CAPABILITY

Complete table below, noting that:

      - The Bidder must provide all of the following reference details from at least two (2) customers to whom maintenance services was executed on VLA Battery Cells or similar for Data Centre or equivalent High Availability Environment (Hospital, Airport, Bank, or similar High Availability Environments) in the last ten (10) years:

  - Company name; and

  - Reference Person Name, Tel and/or email; and

  - Project Scope of Work; and

  - Project Start and End-date.

      - Project end-date must be current or not older than ten (10) years from date this bid is advertised

      - Scope of work must be related.

Table 5: References

| No | Company name | Reference Person Name, Tel and/or email | Project Scope of work | Project Start and End-date |
| --- | --- | --- | --- | --- |
| 1 | <Company name> <Site Address> | <Person Name> <Tel> <email> | <provide scope details of a project to whom maintenance and support services was executed on Vented Lead Acid Battery Cells or similar for Data Centre or equivalent High Availability Environment (Hospital, Airport, Bank, or similar High Availability Environments) in the last ten (10) years. > | Start Date: End Date: |
| 2 | <Company name> <Site Address> | <Person Name> <Tel> <email> | <provide scope details of a project to whom maintenance and support services was executed on Vented Lead Acid Battery Cells or similar for Data Centre or equivalent High Availability Environment (Hospital, Airport, Bank, or similar High Availability Environments) in the last ten (10) years. > | Start Date: End Date: |

Note (1):

Failure to complete Table 5 fully as indicated above will result in disqualification.

Note (2):

SITA reserves the right to verify information provided.

## CIDB REGISTRATION REQUIREMENTS

- The Bidder must complete and sign ANNEX C to confirm that the Bidder is registered with the Construction Industry Development Board (CIDB) with a minimum rating, of 5EB PE or 5EP PE or 6EB or 6EP or higher and attach it here.

Note:

SITA reserves the right to verify the information provided.

## PREFERENTIAL GOAL REQUIREMENTS

The Bidder must:

  - Preference Goal Requirements:

    - Provide a copy of relevant proof of B-BBEE status level of contributor as defined in the Broad-Based Black Economic Empowerment Act as set out in table 3 in section 8.4.1 and attach it here.

    - Bidder to select the section for points they wish to claim (Mark as Y=Yes) in either tables 4A or 4B in section 8.4.1, dependant on which preference system the Bidder selects in line with section 8.1; and

  - Indicate their commitment to claim points for each of the preference points by signing at par 4.5 in the Invitation to Bid document.

NOTE (1):

Failure on the part of a bidder to comply to paragraphs (a) and (b) above, will be interpreted to mean that preference points are not claimed.

:

CIDB REGISTRATION REQUIREMENT

The Bidder needs to complete and sign ANNEX C to confirm that the Bidder is registered with the Construction Industry Development Board (CIDB) with a minimum rating, of 5EB PE or 5EP PE or 6EB or 6EP or higher.

      - The Bidder needs to indicate the Bidder’s CIDB rating by ticking next to the relevant CIDB rating in the table below:

| Service and Support (Milestones) | CIDB Rating (Minimum or Higher) | Bidder to Indicate the Bidder CIDB Rating here |
| --- | --- | --- |
| CIDB Rating | 5EB PE |  |
|  | 5EP PE |  |
|  | 6EB |  |
|  | 6EP |  |
|  | Other, or Higher Rating |  |

      - The Bidder needs to provide the Bidder’s CRS number in the space in the table below:

| Requirement | Bidder’s CRS Number |
| --- | --- |
| Bidder CRS number relating to the minimum rating, of 5EB PE |  |
| Bidder CRS number relating to the minimum rating, of 5EP PE |  |
| Bidder CRS number relating to the minimum rating, of 6EB |  |
| Bidder CRS number relating to the minimum rating, of 6EP |  |
| Bidder CRS number relating to a higher rating, than the stipulated minimums |  |

      - The Bidder confirms and will ensure compliance to the CIDB Basic Guide General Conditions of Contract for Construction Works (GCC 2004) as referred to in Annex E for the Bid Specification Scope of work for the duration of the contract.

Note: SITA reserves the right to verify the information.

I, the Supplier (Full names) …………………………………………………. representing (company name) ……………………………………………………………. hereby confirm that the Bidder is registered with Construction Industry Development Board (CIDB) and understand that it will form part of the contract and is legally binding.

Thus done and signed at ……………………………………. On this………day of……………….20….

__________________

Signature

Designation:

MAINTENANCE REQUIREMENTS

# MAINTENANCE REQUIREMENTS

During Maintenance Support periods the Supplier is responsible to provide the following services on the UPS batteries as specified.

## UPS Batteries Maintenance Requirements.

- The scope of maintenance will cover:

- Meeting with the original equipment manufacturer of the battery units at the respective sites will be required.

- In consultation with the original equipment manufacturer of the battery units at the respective sites, draw up a step by step maintenance procedure for the respective battery units and submit to SITA for approval.

- Once SITA has approved the step by step battery maintenance procedure, the battery services to be strictly executed as per this procedure.

- The following minimum requirements must be incorporated into the battery maintenance procedure, and must be executed at least every three months:

    - All battery terminals must be checked and torqued to the correct tension.

    - All battery units and stands must be properly cleaned. Should any one battery unit have excessive deposits on it, it must be recorded as such as a comment in the battery service book.

    - The battery acid level must be topped up to the correct level.

    - The Specific Gravity level of each battery unit must be checked and recorded in the battery service book.

    - Each battery unit’s valves must be properly cleaned.

    - Inspect each Battery unit’s acid water level and record anomalies. Top up Cells with demineralised water to the maximum levels. This includes provision for 700 litres of distilled battery/ demineralised water for initial top-up for each battery bank.

    - Inspect each Battery unit for excessive sediment formation and record anomalies.

    - Ensure all distribution boards (doors and panels) in the Battery Room are fully closed, and record.

    - Apply petroleum jelly on battery terminals.

    - Inspect Clean and Re-torque battery terminals.

    - Measuring of voltage before and after distilled water top. The measurements should be for each battery. The second measurement should be at least two weeks after the initial top-up.

    - Checking of battery water SG levels after top-up. This should be done at least two weeks after initial top-up.

    - Clean and Re-torque

    - Perform Battery Charging and Discharge Test

## Plant Room Maintenance Requirements

- The contractor shall perform plant room maintenance at the frequencies as indicated under the detail scope of work per site.

- The plant room maintenance must be conducted in such a way to ensure that the plant inside the room is not taken out of service or its operation jeopardised.

- The plant room maintenance may be conducted during normal hours.

- The contractor shall meticulously clean the entire room (including walls, doors and floor).

- The contractor shall ensure the safety of his staff inside these plant rooms while performing the plant room maintenance. Non-skilled staff will not be allowed by SITA inside these areas. SITA will allow semi-skilled electrical staff inside these areas to perform the plant room maintenance.

- Passage ways leading to the respective plant rooms is deemed part of the plant room and all requirements specified for the plant room, applies to these passage ways as well.

## UPS Batteries Inspection Requirements

- The plant inspections must be conducted in such a way so that the respective unit is not taken out of service or its operation jeopardised.

- The plant inspections may be conducted during normal hours.

- The inspection report shall be part of the monthly report;

- The contractor shall notify SITA immediately should any damage, malfunction or alarm be observed on the Plant (being inspected).

- The contractor shall sign the plant room maintenance book during each plant inspection.

- The plant inspections must consist of the following:

- Ensure all distribution boards (doors and panels) in the Battery Room are fully closed, and record.

- Confirm all lights are functional inside the Battery room and record.

- Inspect condition anomality’s of the battery in terms of spillage, corrosion on the terminals and battery water level this to include any leaks of battery water.

- The battery cells and stands shall be cleaned of any dust/dirt.

- The contractor shall perform plant room maintenance at the frequencies as indicated under the detail scope of work per site.

- The plant room maintenance must be conducted in such a way to ensure that the plant inside the room is not taken out of service or its operation jeopardised.

- The plant room maintenance may be conducted during normal hours.

- The contractor shall meticulously clean the entire room (including walls, doors and floor).

- The contractor shall ensure the safety of his staff inside these plant rooms while performing the plant room maintenance. Non-skilled staff will not be allowed by SITA inside these areas. SITA will allow semi-skilled electrical staff inside these areas to perform the plant room maintenance.

- Passage ways leading to the respective plant rooms is deemed part of the plant room and all requirements specified for the plant room, applies to these passage ways as well

## Service Pack Requirements.

- The cost of the Plant Inspection reports is deemed included in the service / inspection costs quoted.

- Two service packs per equipment, per site to be provided. The service pack must conform to the following:

    - The service pack hard copy information must be contained within a file, of which each page must be in a plastic pocket, to ensure longevity of the documentation.

    - Upon SITA approval of the service pack contents, the one file must be inserted into the service folders on site, and the other file must be delivered to the SITA Centurion office for archiving.

    - The files must be clearly marked with a printed front page indicating the Erasmuskloof Site name

    - An electronic copy must be made of the entire service pack for the relevant to the equipment serviced, and be stored on an USB storage device. One USB storage device may be provided containing the information for all the serviced sites.

    - Should additional items been specified in this technical service requirements that does not appear on the given standard service sheet, it must be noted on a separate dated letterhead with associated test results.

CIDB BASIC GUIDE GENERAL CONDITIONS OF CONTRACT FOR CONSTRUCTION WORKS (GCC 2004)

Refer to Attached document.