Eskom Holdings SOC Ltd

Contract No. _________
TUTUKA POWER STATION ELECTROSTATIC PRECIPITATORS (ESP) UPGRADE PROJECT


Part 2: Pricing Data

ECC3 Option A
	Document reference
	Title
	No of pages

	C2.1
	Pricing assumptions: Option A
	5

	C2.2
	The activity schedule  
	1


C2.1 Pricing assumptions: Option A
1. How work is priced and assessed for payment
Clause 11 in NEC3 Engineering and Construction Contract, (ECC3) Option A states:

	Identified and defined terms
	11

11.2
	(20) The Activity Schedule is the activity schedule unless later changed in accordance with this contract.



	
	
	(27) The Price for Work Done to Date is the total of the Prices for 
· each group of completed activities and

· each completed activity which is not in a group.
A completed activity is one which is without Defects which would either delay or be covered by immediately following work.


	
	
	(30) The Prices are the lump sum prices for each of the activities on the Activity Schedule unless later changed in accordance with this contract.



This confirms that Option A is a lump sum form of contract where the work is broken down into activities, each of which is priced by the tendering contractor as a lump sum.   Only completed activities are assessed for payment at each assessment date; no part payment is made if the activity is not completed by the assessment date. 
2. Function of the Activity Schedule
Clause 54.1 in Option A states: “Information in the Activity Schedule is not Works Information or Site Information”.  This confirms that specifications and descriptions of the work or any constraints on how it is to be done are not included in the Activity Schedule but in the Works Information.  This is further confirmed by Clause 20.1 which states, “The Contractor Provides the Works in accordance with the Works Information”. Hence the Contractor does not Provide the Works in accordance with the Activity Schedule.  The Activity Schedule is only a pricing document.  
3. Link to the programme

Clause 31.4 states that “The Contractor provides information which shows how each activity on the Activity Schedule relates to the operations on each programme which he submits for acceptance”.  Ideally the tendering contractor will develop a high level programme first then resource each activity and thus arrive at the lump sum price for that activity both of which can be entered into the activity schedule.  

4. Preparing the activity schedule
Generally it is the tendering contractor who prepares the activity schedule by breaking down the work described within the Works Information into suitable activities which can be well defined, shown on a programme and priced as a lump sum.

The Employer, in his Instructions to Tenderers or in a Tender Schedule, may have listed some items that he requires the Contractor to include in his activity schedule and be priced accordingly. 

It is assumed that in preparing his activity schedule the Contractor:
· Has taken account of the guidance given in the ECC3 Guidance Notes pages 19 and 20;

· Understands the function of the Activity Schedule and how work is priced and paid for;
· Is aware of the need to link the Activity Schedule to activities shown on his programme;
· Has listed and priced activities in the activity schedule which are inclusive of everything necessary and incidental to Providing the Works in accordance with the Works Information, as it was at the time of tender, as well as correct any Defects not caused by an Employer’s risk;
· Has priced work he decides not to show as a separate activity within the Prices of other listed activities in order to fulfil the obligation to complete the works for the tendered total of the Prices. 
· Understands there is no adjustment to the lump sum Activity Schedule price if the amount, or quantity, of work within that activity later turns out to be different to that which the Contractor estimated at time of tender. The only basis for a change to the Prices is as a result of a compensation event. 
An activity schedule could have the following format: 

See attached Excel Spread Sheet titled: C2.2 Pricing Schedule FFP

NB: The Employer requires this group of activities as a minimum; the Contractor is required to break down the price schedule into detail as per the scope of work.

C2.2 the activity schedule
Use this page as a cover page to the Contractor’s activity schedule.  


[image: image1.emf]ESP  Spares Pricing  Schedule.xlsx




DOCUMENT C2.1
PAGE 2
PRICING DATA




Part C2: Pricing Data
PAGE 1
C2 ecc3/a Cover

Pricelist



				TUTUKA POWER STATION

				Units 2 & 6 ESP General Overhaul,

				Refurbishment of the LH & RH ESP Fields

				Contract works description:

				The works includes the supply of all the necessary Equipment to complete the works.

				 The Contractor provides all the associated Engineering, Management, Supervision Labour and Quality services to fulfil and fully execute the requrrements of the Works Information and to provide a fully operational system at the end of the project

				 The Contractor provides all Consumables, Materials, Fastening, Casketing & Spares (Mechanical) as per the works Information (PRICE LIST)

				 The works also include the de-and re-commissioning, removal, dismantling as well as making good of areas  affected  by the  removal; thereof  all  redundant  equipment  to  be removed by the Contractor to designated areas as agreed with Programme Manager.

				Contractor to start with preparation work once the contract is awarded, but access to start with construction work  as per  the contract  starting date

				The Labour activities for the refurbishment  of the Precipitators consists of but is not limited to the following  activities, and the main aim is to  do a complete replacement of the  internals of the 1st to 3rd field wire frames and collector plates & for the replacement of the 4th to 5th field wirre frames only and condition based refurbishment of all the other fields, dust hoppers, pental duct and all other areas of the system including installation of new inlet flow distribution screens.





		No.                                                                                      		DESCRIPTION      				UNIT OF 		 QTY 		 RATE		AMOUNT

																6 months

				Preliminary & General

		1		Site Establishment 		1 Sum		Sum						R   - 0

		2		Site De-Establishment		1 Sum		Sum						R   - 0

		3		Project Management, Site Management, Planning, Quality, Safety Management & Administration 		1 Sum		Sum						R   - 0		assuming this is the same as Supervision as included in original. That totalled to 2.5million if I remove the tower cranes the civils the mobile cranes the meals and geotech
		10000000

		4		Tooling, Equipment & Rigging Equipment to complete the SOW		1 Sum		Sum						R   - 0				R3,623,870.00

		5		Consumables requirement to Complete the SOW		1 Sum		Sum						R   - 0				R6,376,130.00

		6		Travelling & Transport to Complete the SOW		1 Sum		Sum						R   - 0		Not included previously

		7		Accommodation and Meals to complete the SOW		1 Sum		Sum						R   - 0		lower as previous almost the same

		8		Provision for Safety, Environment, Medicals, Inductions & required PPE		1 Sum		Sum						R   - 0

		9		Delivery & Transport Cost Spares		1 Sum		Sum						R   - 0

		10		Wireframe, Collector plate Cradles, Crating & Packaging		1 Sum		Sum						R   - 0

		11		CE & DE Erection & Lifting Lig Requirements		1 Sum		Sum						R   - 0

		12		Supply of The Required Tower Cranage For the duration of the Works Including Site Establishment, De-establishment, Safety, Quality,  		2 Sum		Sum						R   - 0		this and 1.4 seems to be the same

		13		Supply of the Required Mobile cranes Pre Shut and Shut to complete the required SOW		1 Sum		Sum						R   - 0		1mill more per crane included and 1.4 should be included in this price
previoulsy we had two mobile cranes priced 3mill. Now we have on mobile crane

		14		Civils the works Environmental, Labour lncluding bases 		2 Sum		Sum						R   - 0		this was not priced previously

		15		Geotechnical Study		1 sum		Sum						R   - 0		this was not priced previously

		16		Contract Skills Development Goal (CSDG) 0.25% of Tender Amount				Sum						R   - 0

		17		Entreprise Development				Sum						R   - 0

		18

		19		Preliminaries and General items Total 										R   - 0		General Labour was not included amounting to R444750362

		20

		21		DESCRIPTION      				UNIT 						AMOUNT

		22		LABOUR

		23		Disconnect and Remove the Rectifier Transformers/HFPS from the ESP roof (all fields)		20		ea								Was not priced before, will only be required for 5 units

		24		Replace and Connect the Rectifier Transformers/HFPS on the ESP roof (all  fields )		20		ea								this was not priced before

		25		Open all fields Gas tight Roofs, Replace and weld gas tight roof LH & RH (Expansion to be taken into Consideration)		30		ea								this was not priced before

		26		Open Electrical Supply Ducts Inspect & Report (all fields)		60		ea								this was not priced before

		27		Empty all the Precip Dust Hoppers LH & RH (all fields)		40		ea								this was not priced before
This should also be Eskom scope sp could be excluded

		28		Perform extensive dirty Inspections with the roof of the ESP open (Issue Report to Outage coordinator and Engineer)		N/A		    Detailed Report						N/A

		29		Perform Precip washing on both casings, down to the dust hoppers, and Oml		N/A		Sum								The washing will be done by Eskom.
Outage scope

		30		Remove all fields Old Wire Frames LH & RH (Top & Bottom)		264		ea								this was not priced previously

		31		Replace all fields with New Wire Frames LH & RH (Top & Bottom)  (Supply)		264		ea

		32		Remove & Replace the 1st, 2nd & 3rd fields Old Collector Plates LH & RH		8160		ea								Add 20% for rest of the scope
Thus the total must be R 19 307 569.80

		33		Supply the 1st, 2nd & 3rd fields Old Collector Plates LH & RH 		8160		ea								Add 20% for rest of the scope(fields 4&5)
Thus the total must be R 21 512 465.63

		34		Remove the Damaged Collector Plates LH & RH 4th to 5th field		tbc		ea						N/A		the contractor will have to replace 20-15 % of the last two fields added to 2.11 and 2.10

		35		Replace the new Collector Plates LH & RH 4th to 5th field		tbc		ea						N/A		the contractor will have to replace 20-15 % of the last two fields added to 2.11 and 2.10

		36		Remove & Replace  Cam Release Units including lifting tie Rod  LH & RH (1st, 2nd & 3rd field only)		40		ea						R   - 0		add 15-20% to price for field 4&5
Thus total to be 34 thus R 736 128.00

		37		Remove and Replace lifting Insulator Complete with Sellock Pins, bolt & washers LH & RH (1st, 2nd & 3rd field only)		40		ea						R   - 0		add 15-20% to price for field 4&5
Thus total to be 34 thus R 695 232.00

		38		Remove & replace all the Flow distribution Perforated Screen LH&RH
(Primary, Intermediate and Secondary Screens)		360		Sum						R   - 0		This was not priced before
this is fine for an estimate. We cannot say how much it will be the contractor will have to do inspect and tell us how much will be replaced. So we need a price per M2
Since they ar giving a price of  R 2 624 267.76 let budget for half of that
They did give a price of R 1 623.21 in 2,70 if we multiply that with 360m2 then we get R 584 356.90 
I am assuming that is their price per m2 for welding

		39		Clean Roof Beam Internally LH & RH (VACUM CLEAN) (1st, 2nd & 3rd field only)		36		ea						R   - 0		this should be all fields. 
This was not priced previously
Thus R 263 507.58

		40		Replace Roof Beam Access door Seals LH & RH (1st, 2nd & 3rd field only)		60		ea						R   - 0		This should be R 17 040.00 for all fields

		41		Replace Precip Access Door Seals LH & RH (1st, 2nd & 3rd field only)		30		ea						R   - 0		This should be R 2 130.00 for all fields

		42		Replace Dust Hopper Door seals LH & RH (1st, 2nd & 3rd field only)		60		ea						R   - 0		This should be R 8 520.00 for all fields

		43		Repair all Cam release Pedestals (clean & weld) LH & RH (1st, 2nd & 3rd field only)		40		ea						R   - 0		This was not priced previously. 
Added 15% for rest of fields

		44		Replace Damaged Coupling Taper Locks LH & RH (1st, 2nd & 3rd field only)		40		ea						R0.00		Added 15% for rest of fields

		45		Replace Damaged Fenner Flex Coupling LH & RH (1st, 2nd & 3rd field only)												was not priced previously

		46		Renew Gearbox oil and Inspect (Report) LH & RH  (1st, 2nd & 3rd field only) 		40		ea						R0.00		this was not priced before. This should be all fields R 17 643.63

		47		Clean Support Insulators LH & RH (1st, 2nd & 3rd field only)		120		ea						R0.00		this was not priced before. This should be all fields R 176 253.46

		48		Replace Deva Bushes (1st, 2nd & 3rd field only)		120		ea						R0.00

		49		Replace Deva bush 2" Cap LH & RH (1st, 2nd & 3rd field only)		60		ea						R0.00

		50		Clean Electrical Insulators LH & RH (1st, 2nd & 3rd field only)		40		ea						R0.00		this was not priced before. This should be all fields R 73 438.94

		51		Disconnect the CE and DE Electrical motors, Remove & Replace LH & RH (1st, 2nd & 3rd field only)		20		ea						R0.00		Was not priced before. This should be for all fields R 15 067.26

		52		Replace Damaged CE & DE Rapper Anvils LH & RH 1st field		990		ea						R0.00		rapper bars are included later on 
This should then be for the 1st field only but they multiplyed by 3 fields.
IT SHOULD BE;
DE anvils 66 rows x 2 (top & bottom) x 1 fields x 2 ESP's Thus R206 184

		53		Replace Damaged CE & DE Rapper Anvils LH & RH 2nd field		990		ea						R0.00		rapper bars are included later on 
This should then be for the 1st field only but they multiplyed by 3 fields.
IT SHOULD BE;
DE anvils 66 rows x 2 (top & bottom) x 1 fields x 2 ESP's Thus R206 184

		54		Replace Damaged CE & DE Rapper Anvils LH & RH 3rd field		990		ea						R0.00		rapper bars are included later on 
This should then be for the 1st field only but they multiplyed by 3 fields.
IT SHOULD BE;
DE anvils 66 rows x 2 (top & bottom) x 1 fields x 2 ESP's Thus R206 184

		55		Replace loose anvil clamp bolts M12 X 50 GB B Bolts nuts lock washers (TORQUE BOLTS 90NM) LH & RH 1st 2nd and 3rd field		1264		ea						R0.00		why  only 3rd field? Must be first 3 fields 
Contractor must do inspection and replace what is required thus R 67 308

		56		Replace Damaged Rapper Anvils LH & RH 4th and 5th field		40		ea						R0.00		they should inspect and replace what is damaged. This shoul be assumed to be 15-20% to be replaced
Included 15% for the 4th and 5th fields

		57		Replace loose anvil clamp bolts M12 X 50 GB B Bolts nuts lock washers (TORQUE BOLTS 90NM) LH & RH 4th and 5th field		1264		ea						R0.00		they should inspect and replace what is damaged. This shoul be assumed to be 15-20% to be replaced

		58		Replace Damaged Rapper Anvils LH & RH 5th field		40		ea						R0.00		
Contractor must do inspection and replace as required assume 15%
Included in 2.34

		59		Replace loose anvil clamp bolts M12 X 50 GB B Bolts nuts lock washers LH & RH 5th field		1246								R0.00		included in 2.35

		60		Replace DE Rapper Shaft 1st, 2nd & 3rd Field LH including Bearings		12		ea						R0.00		This should be all fields

		61		Replace DE Rapper Shaft 1st, 2nd & 3rd Field RH including bearings		12		ea						R0.00		This should be all fields

		62		Replace DE pedestal Bearing Shaft split collars (sets) (1st 2nd & 3rd field only)		256		ea						R0.00		discripition to be updated to include the 3rd field. But the calculation for the sum, by the Contractor, is currect.
I added 15% for field 4&5

		63		Align CE hammers to anvils LH & RH 1st Field to 5th field (1st 2nd & 3rd field only)		2040		ea						R0.00		should this not be all fields?
This was not priced before

		64		Replace complete tie rod Assembly including Turnbuckles, Studs, Axle Holder and Pins LH & RH (1st,2nd & 3rd field only)		120		ea						R0.00		Added 15% for rest of fields

		65		Set Rapping Mechanism as per OEM Procedure LH & RH (Cam, top rapping, Bottom rapping) (1st,2nd & 3rd field only)		20		ea						R0.00		This was not priced before
Should be all fields

		66		Re Align misaligned Wire Frames LH & RH (Top & Bottom)(1st & 2nd & 3rd field only)		3960		ea						R0.00		this should be all fields

		67		Clean Pental Tubing & repair Connections (1st & 2nd & 3rd field only)		60		ea						R0.00		This was not priced before
added 15%

		68		Remove Gearbox, Clean, inspect, re-grease (replace) pedestal bearing (report)(1st 7 2nd field only)		30		ea						R0.00		This was not priced before
This will have to be done for all fields

		69		Remove old and insert new Drive shaft gland seals LH & RH (1st & 2nd field only)		30		ea						R0.00		This was not priced before
This will have to be done for all fields

		70		Inspect Rapper shafts for Straightness and Pin couplings for wear LH & RH 1st Field to 3rd Field (Report)		30		ea						R0.00		This was not priced before
This will have to be done for all fields

		71		Replace Rapper Hammers LH & RH (1st & 2nd & 3rd  field only)		6000		ea						R0.00		Should be for all 5 fields
Added 15% for field 4&5

		72		Replace 1st field LH & RH Rapper Bars		816		ea						R0.00

		73		Replace 2nd field LH & RH Rapper Bars		816		ea						R0.00

		74		Replace 3rd field LH & RH Rapper Bars		816		ea						R0.00

		75		Replace 4th field LH & RH Rapper Bars		816		ea						R0.00		this cost should be included assumed to replace 15-20%

		76		Replace 5th field LH & RH Rapper Bars		816		ea						R0.00		this cost should be included assumed to replace 15-20%

		77		Replace Pedestal Bearings complete 1st Field LH & RH		96		ea						R0.00

		78		Replace shalt bearing rollers, bushes  3rd Field LH & RH		192		ea						R0.00		Field 1 and 2 is not included
The price they are using for this one is different than for field 1 and 2

		79		Inspect for wear and repair Drive Shaft pin couplings LH & RH		120		ea						R0.00		confirm quantity
this was not priced before

		80		Replace Damaged Collector Rapper guide plates LH & RH (60 x 60 x 6 x 120 angle)(1st & 2nd field only)		120		ea						R0.00

		81		Align  Drive shafts complete LH & RH (1st & 2nd & 3rd field only)		30		ea						R0.00		this should be all fields

		82		Hand test Rapping sequence hammer to anvil and adjust if required LH & RH (1st & 2nd 3rd  field only)		30		ea						R0.00

		83		Replace damaged Bearing Pedestal retaining plate (1st & 2nd 3rd  field only)		192		ea						R0.00

		84		Re-align misaligned collecting plates (1st & 2nd & 3rd field only)		20400		ea						R0.00

		85		Inspect Inlet slope, walls, and roof for wear (Random Thickness Test) LH & RH		6		Sum						R0.00		Its fine if they don’t have a separate price for the inspection

		86		Repair Inlet & Outlet slope, walls and roof LH & RH		3		M²						R0.00		Yes this will have to be M², They will have to inspect and repair as per the findings
This was not priced before

		87		Replace Toe plates on inlet side bottom of screens LH & RH		270		ea						R0.00		this is for all toe plates, this was not priced previously

		88		Replacement of Dust Hopper Heaters (1st & 2nd & 3rd field only)		120		ea						R0.00		This was not priced previously

		89		Repair the HT Ductings (1st & 2nd 3rd  field only)		60		ea						R0.00		This was not priced previously

		90		Inspect hopper for leaks report LH & RH (60 off Hoppers)				m						R0.00		they will have to be copensated for doing the inspection and then they will have to be paid for what they found they have to repair. They sould give a price in M2 as per 2.70
We need to add and repair to the description

		91		Remove and refurbish damaged agitators Handles LH & RH (1st & 2nd 3rd field only)		60		ea						R0.00		This was not priced previously
20% to be added for remaining 2 fields

		93		Seal weld protection lining (angle iron/flat bar) on hopper edges  LH & RH		960		m						R0.00		this is seal welding on regular carbon steal
This was not priced previously

		94		Repair Damaged Hopper Baffle Plates 3rd Field to 5th Field LH & RH		5		ea						R0.00		this is seal welding on regular carbon steal
This was not priced previously

		95		Repair damaged walkway buffer plates		6		ea						R0.00		Scope will be to inspect and repair.
They will have to price per M2
This was not included previously

		96		Commissioning of the Fields with Conventional/HF Controllers
(Fields 1-5)		60		ea						R0.00		This was not priced previously
All fields to be included they only included 2 fields
Total should be 20

		97		Commission DE rapping (run for 24 hours) Set rapping sequence LH & RH Fields 1 - 5		30		sum						R0.00		This was not priced previously
Should be all fields

		98		Commission CE rapping (run for 24 hours) Set rapping Sequence LH & RH Fields 1 - 5		30		sum						R0.00		This was not priced previously
All fields to be included they only included 2 fields
Total should be 10
Should be all fields

		99		Gas tight roof (field 1 -5 only)		Size (0.4*68*4.8)*5*2		m2						R0.00		This price is double then what is was previously

		100		Rain roof (field 1 -5 only)		Size (0.4*68*4.8)*5*2		m2						R0.00

		101		CE sidewall baffles (field 1 & 2 & 3 only)		 Size15*2*3*2		m						R0.00		this is 10times more than what it was previously

		102		Electrical Scope

		103		Prior to unit shutdown

		104		1.    On load readings.				sum						R0.00		This was not priced previously

		105		2.    Dirty Moving air test.				sum						R0.00		This was not priced previously

		106						sum						R0.00

		107						sum						R0.00

		ERROR:#REF!		3.    Dirty still air test.				sum						R0.00		This was not priced previously

		108						sum						R0.00

		109						sum						R0.00

		110		4.     OPEN CIRCUIT TEST ON ALL RECT/TRF TO ENSURE TE INTEGRITY OF THE RECT/TRF.				sum						R0.00		This was not priced previously

		111						sum						R0.00

		112		OUTAGE WORK.

		113		TYRISTOR PACK ASSEMBLY. 

		114		·  Thyristor pack need to be send to the OEM for testing and proper maintenance.				sum						R0.00		This was not priced previously

		115		· Complete Thyristor bank to be tested before repair and electrical engineering to verify readings.				sum						R0.00

		116		· Thyristors installation required a specified force for the device used +/- 7 Kn (kilotons) then test with specialised electrical equipment apparatus to test the breakdown violates break over and gate firing.				sum						R0.00

		117		.Re-service the heat sink to ensure that is smooth no pit marks or carbon traces. 				sum						R0.00

		118		·  New Thyristors to be installed as per OEM requirements.				sum						R0.00

		119		· Add the necessary amount of paste on to the Thyristor before installation.				sum						R0.00

		121		·  Special tool to be use:				sum						R0.00

		122		·  Clamping device with necessary pressure as per specification.				sum						R0.00

		123		·  Tool to calibrate and lock the clamping device.				sum						R0.00

		124		·  Calibrate thermostat on +/- 800C.				sum						R0.00

		125		·  Live trip test thermostat to ensure correct operation.				sum						R0.00

		126		·  Ensure cooling fan is good condition and correct operation. 				sum						R0.00

		127		·  Clean and check that Precip controllers are still in a good working condition, 				sum						R0.00

		128		Support Insulation.										R0.00

		129		·  Clean the support insulator externally and internally with a non-abrasive cleaner				Sum						R0.00		This was not priced previously

		130		·    Visually inspect evidence of electrical tracking, cracks, chips or misalignment.				Sum						R0.00

		131		·   Ensure the vent pipe is not blocked.				Sum						R0.00

		132		·   Ensure insulator bleed air hole is not blocked				Sum						R0.00

		133		·  All support insulators found to be defective must be replaced				Sum						R0.00

		134		 Support insulator heater thermostat.										R0.00

		135		·   Prior to Unit shut down each insulator heater test button to be press to ensure the electrical integrity of the circuit. The expected current reading should be 4.6 amps ± 5% all defects found must be repair during the outage. If this is not carry out prior to unit shutdown, do insulator resistance test on each heater element and replace if faulty.				Sum						R0.00		This was not priced previously

		ERROR:#REF!		· Visually inspected each heater element for signs of corrosion or excessive ash contamination, any damaged or badly corroded elements must be replace.				Sum						R0.00

		136		· Inspect thermostat bulb for integrity and replace those found to be broken. 				Sum						R0.00

		137		·  Clean and check for loose or damaged cables.				Sum						R0.00

		138		·  Remove thermostat and sent for calibration, settings to be between 70OC– 90OC and test for functionality. 				Sum						R0.00

		139		·  Install thermostat and do a live trip test on the plant to ensure the integrity of the thermostat and trip circuit, need to trip out on 70OC.				Sum						R0.00

		140		Rect / Trf sets.										R0.00

		141		·         Visually inspect transformers for any signs of oil leaks or external damage and record any defect.				Sum						R0.00		This was not priced previously

		142		·         Check oil level and top up if necessary.				Sum						R0.00

		143		·         Replace silica gel.				Sum						R0.00

		144		·         Visually inspect HV duct for any signs of arcing or excessive pit marks.				Sum						R0.00

		145		·         Clean all transformers HV bushing with a non-abrasive cleaner and visually inspect bushing for any signs of tracking, cracks or similar damage.				Sum						R0.00

		146		·         Ensure that the vent pipe is not block.				Sum						R0.00

		147		·         Ensure that the air bleed hole is not block. 				Sum						R0.00

		148		·         Check switchblade assembly for any burnt marks, corrosion, damage and loose connections.				Sum						R0.00

		149		·         Inspect knife blade and blade contact jaws, align knife blade with blade contact jaws, and lubricate.				Sum						R0.00

		150		·         Inspect and ensure each transformer earth mechanism is in tack, replace broken earth lead clamps. 				Sum						R0.00

		151		·         Clean secondary plate components and test the resistance thereof.				Sum						R0.00

		152		·         Ensure thermostat pocket oil level is +/- 80% full of transformer oil if not top up.				Sum						R0.00

		153		·         Remove thermostat and sent for calibration, settings to be between 70OC– 90OC and test for functionality. 				Sum						R0.00

		154		·         Install thermostat and do a live trip test on the plant to ensure the integrity of the thermostat and trip circuit, need to trip on 900C.				Sum						R0.00

		155		·         Check and clean Rect/Trf 380 volt connection box and ensure all electrical connections for tightness and signs of hot connection. 				Sum						R0.00

		157		·         Ensure that the following cables are not damaged: 										R0.00

		158		380 Volt Rect / Trf cable,       Heater cable,   Thermostat cable,  Control cable.				Sum						R0.00

		159		·         Check if the earth strap of the earth switch is still in place and connected to the main earth.										R0.00

		160		·         Check and repair any water penetration into cubicle.				Sum						R0.00

		161		Hopper Heaters.										R0.00

		162		·       Prior to Unit shut down, each insulator heater test button to be press to ensure the electrical				Sum						R0.00		This was not priced previously

		163		·       integrity of the circuit. The expected current reading should be 4.6 amps ± 5% all defects found				Sum						R0.00

		164		·       must be repair during the outage. If this is not carry out prior to unit shutdown, do insulator				Sum						R0.00

		165		·       resistance test on each heater element and replace if faulty.				Sum						R0.00

		166		·         The hopper heater switchgear should be vacuum clean, and inspected for loose connections or any signs of damage.				Sum						R0.00

		167		·         The marshalling boxes should be clean and visually inspected for any signs damage and ensure that the covers are properly secure to prevent dust and moisture ingress.				Sum						R0.00

		168		·         Megger heater elements to ground and replace those that fail. 				Sum						R0.00

		169		·         Remove thermostat and sent for calibration, settings to be between 70OC– 90OC and				Sum						R0.00

		170		·         test for functionality. 				Sum						R0.00

		171		·         Install thermostat and do a live trip test on the plant to ensure the integrity of the thermostat and trip circuit, need to trip out on 75OC.				Sum						R0.00

		172		·         The thermostat setting should be verify to be 75ºC.				Sum						R0.00

		173		 Discharge Rapper motor and control panel switchgears.										R0.00

		174		·         Visually inspect the discharge rapper motor switchgear for loose connections and vacuum clean switchgear cabinet.				Sum						R0.00		This was not priced previously

		175		·         Verify fuse integrity with multi-meter and verify motor overload setting to be 1.2 amps.				Sum						R0.00

		176		·         Clean and inspect local on/off switch and verify correct operation.				Sum						R0.00

		177		·         Verify correct operation of thermal overload relay.				Sum						R0.00

		178		·         All earth straps must be test for continuity using a megger.				Sum						R0.00

		179		·         Calibrate all ammeters and test accuracy with multi-meter.				Sum						R0.00

		180		·         Inspect and clean motor terminal box for loose connection.				Sum						R0.00

		181		·         Motor fan, motor cover and earth to be in place.				Sum						R0.00

		182		 Colleting Rapper motors and control panel switchgears.										R0.00

		183		·         Visually inspect the collector plate rapper motor switchgear for loose connections and vacuum clean switchgear cabinet.				Sum						R0.00		This was not priced previously

		184		·         Verify fuse integrity with multi-meter and verify motor overload setting to be 1.2 amps.				Sum						R0.00

		185		·         Clean and inspect local on/off switch and verify correct operation.				Sum						R0.00

		186		·         Visually inspect the collector plate rapper reset control cabinet for loose connections and clean cabinet.				Sum						R0.00

		187		·         Verify correct operation of thermal overload relay.				Sum						R0.00

		188		·         All earth straps must be test for continuity using a megger.				Sum						R0.00

		189		·         Calibrate all ammeters and test accuracy with multi-meter. 				Sum						R0.00

		190		·         Inspect and clean motor terminal box for loose connection.				Sum						R0.00

		191		·         Motor fan and cover to be in place.				Sum						R0.00

		192		·         Motor earth to be in place.				Sum						R0.00

		193		 Internal Inspection.										R0.00

		194		· Conduct internal inspection and remove any loose or slack DE wires or any other objects that may cause the field have a short circuit.				Sum						R0.00		This was not priced previously

		195		380V/11kV Precip supply Transformer.										R0.00

		196		· Vacuum the transformer windings and core to remove all dust deposits.				Sum						R0.00		This was not priced previously

		197		· Vacuum clean CT’s connected and check for loose connections.				Sum						R0.00

		198		·  Visually inspect and clean dust burden from the transformer and the panel.				Sum						R0.00

		199		·   Remove HV tape on and inspect for hot or loose connections and discolouring. 				Sum						R0.00

		200		·   Reapply appropriate insulation. 				Sum						R0.00

		201		·   Change Fluorescent tubes that are dead.				Sum						R0.00

		202		 VOLT PRECIP BOARDS.										R0.00

		203		·  Do a Ductor test on all 380 Volt isolator, electrical engineering to verify readings.				Sum						R0.00		This was not priced previously

		204		·   All 380 Volt panels to be vacuum clean out.				Sum						R0.00

		205		·  Check and ensure that there are no loose or hot connections on all 380 Volts panels.				Sum						R0.00

		206		·  Check and ensure panel wiring is still in a good reliable condition.				Sum						R0.00

		207		·  Verify fuse integrity on all 380 Volts panels.				Sum						R0.00

		208		· Ensure that all cable entrance properly sealed with vermiculite, to avoid dust enter the boards.   				Sum						R0.00

		209		· Clean and ensure that there are no hot or loose connection on the 380 Volt bus bars. 				Sum						R0.00

		210		·  Ensure that all panel doors sealed properly when close to avoid dust enter panels.				Sum						R0.00

		211		Commissioning to be done with controllers on contuinuios mode. 

		212		 INSPECTION.										R0.00		This was not priced previously

		214		· All tool and equipment to be remove before clearing the permit. Hopper and insulator heaters to be switch on auto mode 24 hours before still air can start, this is to ensure that there is no moister present  in the inside of the main support insulator that can cause electrical tracing. Ensure all heater are in a good working condition.				Sum

		215

		216		STILL AIR TEST.

		217		·         Start transformers one at a time and ensure that secondary current is +/- 800mA and voltage +/- 35kV with zero sparking and arcing. 				Sum						R0.00

		218		·         If not inspect cubicles then redo internal Precip field inspection for faults.				Sum						R0.00

		219		MOVING AIR TEST.

		220		·         Draught group to be on full load to conduct the moving test.				Sum						R0.00

		221		·         Start transformers one at a time and ensure that secondary current is +/-800mA and voltage +/- 35kV with zero sparking and arcing. 				Sum						R0.00

		222		·         If not inspect cubicles then redo internal Precip field inspection for faults.				Sum						R0.00

		223		             Insulator and hopper heaters.										R0.00

		224		·         Hopper and insulator heaters to be switch on auto mode 24 hours before unit start up and check for working condition.				Sum						R0.00

		225												R0.00

		226		 DHP to be on load before rapper can be test to avoid block hoppers and flooding of the DHP.

		227

		228		· Test Collector and Discharge rappers on manual and leave running for 10 minutes to ensure all rappers are operate as per Eskom requirement, then switch back to auto mode. All rappers to be switch on auto mode 24 hours before unit start up and check for working condition.				Sum						R0.00		This was not priced previously

				TOTAL COST OF SPARES & ELECTRICAL 										R   - 0		R162,699,665.53



				TOTAL COST OF SPARES & ELECTRICAL INCL  PRELIMINARIES & GENERAL ITEMS										R   - 0		ERROR:#REF!








