{"text_format":"3","workbook":"xlsx","n_sheets":5,"sheets":["Inverter Grid-Tie - 50 & 150kVA","Solar Panels 400W-550W","Li-Ion Battery","DC Fused Combiner DB","ChangeOver"],"read":"whole","date_system":"1900"}

{"sheet":"Inverter Grid-Tie - 50 & 150kVA","index":0,"n_rows":33,"n_cols":13,"rows_kept":33,"merged":[[4,5,4,6],[5,5,5,6],[6,1,14,1],[6,2,6,3],[14,2,14,3],[15,1,24,1],[19,2,19,3],[25,1,32,1]]}
[null,"SAA",{"$nulls":3},"2023-10-30"]
[null,"Solar Equipment Specifications"]
[]
[]
[]
[null,null,"Item #","Description","Units","Specification",null,"Required","Recommended","Specify"]
[null,"Inverter Type","INVERTER "]
[null,null,1,"Inverter Size","kVA","50 kVA","150kVA",null,"YES",". . . . . . . . . . . . . . . . . . . . . . . . . . . . "]
[null,null,2,"Grid-Tied / Hybrid / Off-Grid","N/A","Grid-Tied","Grid-Tied","YES",null,". . . . . . . . . . . . . . . . . . . . . . . . . . . . "]
[null,null,3,"Number of Channels","N/A","Four","Four minimum","YES",null,". . . . . . . . . . . . . . . . . . . . . . . . . . . . "]
[null,null,4,"Temperature","Deg C","-30 Dec C to +60 Deg C","-30 Dec C to +60 Deg C","YES",null,". . . . . . . . . . . . . . . . . . . . . . . . . . . . "]
[null,null,5,"Protective Class","Class","Class I","Class I","YES",null,". . . . . . . . . . . . . . . . . . . . . . . . . . . . "]
[null,null,4,"Inverter Topology","Isol/Non Isol","Non-Isolated","Non-Isolated","YES",null,". . . . . . . . . . . . . . . . . . . . . . . . . . . . "]
[null,null,6,"Index of Protection  (IP rating)","N/A","IP66","IP66","YES",null,". . . . . . . . . . . . . . . . . . . . . . . . . . . . "]
[null,null,"AC  - VOLTAGE  & CURRENT"]
[null,"Inverter Input",7,"Voltage Input Nominal (AC) , 3 / N / PE, 230/400V","Vac in","380 -420 V","380 -420 V","YES"]
[null,null,8,"Nr. Of Phases","Ph","3Ph","3Ph","YES"]
[null,null,9,"Input Frequency","F in","50 Hz","50 Hz","YES"]
[null,null,10,"Current Input (AC) AC supply Mains"," Amps","20A","20A - 50A",null,"YES"]
[null,null,"DC - VOLTAGE & CURRENT"]
[null,null,11,"Voltage Input (DC)  Vmax. PV","V DC in PV","1100","1100",null,"YES"]
[null,null,12,"MPPT Range","V DC  PV","200V  to 1000V","200V  to 1000V",null,"YES"]
[null,null,13,"Maximum Current Input (DC)","Imax. DC In","39A / 39A / 39A / 39A","39A / 39A / 39A / 39A",null,"YES"]
[null,null,14,"Short Circuit Current  PV","Isc  PV","48A / 48A / 48A / 48A","48A / 48A / 48A / 48A",null,"YES"]
[]
[null,"Inverter Output",15,"Nominal Voltage Output (AC)","Vac out","380 -420 V","380 -420 V","YES"]
[null,null,16,"Output Frequency","Hz","50 Hz","50 Hz","YES"]
[null,null,17,"Nr. Of Phases","Ph","3Ph","3Ph","YES"]
[null,null,18,"Output Current Maximum (Imax)","Amps","95.6 A","250A",null,"YES",null,{"$f":"SQRT(3)*L29*M29","v":59236.137618855595},380,{"$f":"90","v":90}]
[null,null,19,"Rated Power Output, Active","kW",50000,150000,null,"YES",null,{"$f":"50000","v":50000},{"$f":"380","v":380},{"$f":"K30/(SQRT(3)*L30)","v":75.9671406828455}]
[null,null,20,"Maximum Power Output, Apparent","kVA",59200,{"$f":"G30/0.8","v":187500},null,"YES",null,{"$f":"150000","v":150000},{"$f":"380","v":380},{"$f":"K31/(SQRT(3)*L31)","v":227.90142204853652}]
[null,null,21,"Power Factor Range","N/A","1.0  - 0.8","1.0  - 0.8",null,"YES"]
[{"$nulls":10},{"$f":"K31/0.8","v":187500}]

{"sheet":"Solar Panels 400W-550W","index":1,"n_rows":28,"n_cols":10,"rows_kept":28,"merged":[[1,5,1,6],[2,1,10,1],[2,2,2,3],[10,2,10,3],[11,1,20,1],[15,2,15,3],[21,1,28,1]]}
[]
[null,null,"Item #","Description","Units","Specification",null,"Required","Recommended","Specify"]
[null,"Solar Panel Type","Solar Panel "]
[null,null,1,"Solar Panel Size","kVA","50 kVA","150kVA",null,"YES"]
[null,null,2,"Grid-Tied / Hybrid / Off-Grid","N/A","Grid-Tied","Grid-Tied","YES"]
[null,null,3,"Number of Channels","N/A","Four","Four minimum","YES"]
[null,null,4,"Temperature","Deg C","-30 Dec C to +60 Deg C","-30 Dec C to +60 Deg C","YES"]
[null,null,5,"Protective Class","Class","Class I","Class I","YES"]
[null,null,4,"Solar Panel Topology","Isol/Non Isol","Non-Isolated","Non-Isolated","YES"]
[null,null,6,"Index of Protection  (IP rating)","N/A","IP66","IP66","YES"]
[null,null,"AC  - VOLTAGE  & CURRENT"]
[null,"Solar Input",7,"Voltage Input Nominal (AC) , 3 / N / PE, 230/400V","Vac in","380 -420 V","380 -420 V","YES"]
[null,null,8,"Nr. Of Phases","Ph","3Ph","3Ph","YES"]
[null,null,9,"Input Frequency","F in","50 Hz","50 Hz","YES"]
[null,null,10,"Current Input (AC) AC supply Mains"," Amps","20A","20A - 50A",null,"YES"]
[null,null,"DC - VOLTAGE & CURRENT"]
[null,null,11,"Voltage Input (DC)  Vmax. PV","V DC in PV","1100","1100",null,"YES"]
[null,null,12,"MPPT Range","V DC  PV","200V  to 1000V","200V  to 1000V",null,"YES"]
[null,null,13,"Maximum Current Input (DC)","Imax. DC In","39A / 39A / 39A / 39A","39A / 39A / 39A / 39A",null,"YES"]
[null,null,14,"Short Circuit Current  PV","Isc  PV","48A / 48A / 48A / 48A","48A / 48A / 48A / 48A",null,"YES"]
[]
[null," Output",15,"Nominal Voltage Output (AC)","Vac out","380 -420 V","380 -420 V","YES"]
[null,null,16,"Output Frequency","Hz","50 Hz","50 Hz","YES"]
[null,null,17,"Nr. Of Phases","Ph","3Ph","3Ph","YES"]
[null,null,18,"Output Current Maximum (Imax)","Amps","95.6 A","250A",null,"YES"]
[null,null,19,"Rated Power Output, Active","kW",50000,150000,null,"YES"]
[null,null,20,"Maximum Power Output, Apparent","kVA",59200,{"$f":"G26/0.8","v":187500},null,"YES"]
[null,null,21,"Power Factor Range","N/A","1.0  - 0.8","1.0  - 0.8",null,"YES"]

{"sheet":"Li-Ion Battery","index":2,"n_rows":28,"n_cols":10,"rows_kept":28,"merged":[[1,5,1,6],[2,1,10,1],[2,2,2,3],[10,2,10,3],[11,1,20,1],[15,2,15,3],[21,1,28,1]]}
[]
[null,null,"Item #","Description","Units","Specification",null,"Required","Recommended","Specify"]
[null,"Solar Battery Type","Solar Battery "]
[null,null,1,"Solar Battery Size","kVA","50 kVA","150kVA",null,"YES"]
[null,null,2,"Grid-Tied / Hybrid / Off-Grid","N/A","Grid-Tied","Grid-Tied","YES"]
[null,null,3,"Number of Channels","N/A","Four","Four minimum","YES"]
[null,null,4,"Temperature","Deg C","-30 Dec C to +60 Deg C","-30 Dec C to +60 Deg C","YES"]
[null,null,5,"Protective Class","Class","Class I","Class I","YES"]
[null,null,4,"Solar Battery Topology","Isol/Non Isol","Non-Isolated","Non-Isolated","YES"]
[null,null,6,"Index of Protection  (IP rating)","N/A","IP66","IP66","YES"]
[null,null,"AC  - VOLTAGE  & CURRENT"]
[null,"Solar Input",7,"Voltage Input Nominal (AC) , 3 / N / PE, 230/400V","Vac in","380 -420 V","380 -420 V","YES"]
[null,null,8,"Nr. Of Phases","Ph","3Ph","3Ph","YES"]
[null,null,9,"Input Frequency","F in","50 Hz","50 Hz","YES"]
[null,null,10,"Current Input (AC) AC supply Mains"," Amps","20A","20A - 50A",null,"YES"]
[null,null,"DC - VOLTAGE & CURRENT"]
[null,null,11,"Voltage Input (DC)  Vmax. PV","V DC in PV","1100","1100",null,"YES"]
[null,null,12,"MPPT Range","V DC  PV","200V  to 1000V","200V  to 1000V",null,"YES"]
[null,null,13,"Maximum Current Input (DC)","Imax. DC In","39A / 39A / 39A / 39A","39A / 39A / 39A / 39A",null,"YES"]
[null,null,14,"Short Circuit Current  PV","Isc  PV","48A / 48A / 48A / 48A","48A / 48A / 48A / 48A",null,"YES"]
[]
[null," Output",15,"Nominal Voltage Output (AC)","Vac out","380 -420 V","380 -420 V","YES"]
[null,null,16,"Output Frequency","Hz","50 Hz","50 Hz","YES"]
[null,null,17,"Nr. Of Phases","Ph","3Ph","3Ph","YES"]
[null,null,18,"Output Current Maximum (Imax)","Amps","95.6 A","250A",null,"YES"]
[null,null,19,"Rated Power Output, Active","kW",50000,150000,null,"YES"]
[null,null,20,"Maximum Power Output, Apparent","kVA",59200,{"$f":"G26/0.8","v":187500},null,"YES"]
[null,null,21,"Power Factor Range","N/A","1.0  - 0.8","1.0  - 0.8",null,"YES"]

{"sheet":"DC Fused Combiner DB","index":3,"n_rows":28,"n_cols":10,"rows_kept":28,"merged":[[1,5,1,6],[2,1,10,1],[2,2,2,3],[10,2,10,3],[11,1,20,1],[15,2,15,3],[21,1,28,1]]}
[]
[null,null,"Item #","Description","Units","Specification",null,"Required","Recommended","Specify"]
[null,"Solar PanelType","Solar Panel "]
[null,null,1,"Solar Panel Size","kVA","50 kVA","150kVA",null,"YES"]
[null,null,2,"Grid-Tied / Hybrid / Off-Grid","N/A","Grid-Tied","Grid-Tied","YES"]
[null,null,3,"Number of Channels","N/A","Four","Four minimum","YES"]
[null,null,4,"Temperature","Deg C","-30 Dec C to +60 Deg C","-30 Dec C to +60 Deg C","YES"]
[null,null,5,"Protective Class","Class","Class I","Class I","YES"]
[null,null,4,"Solar Panel Topology","Isol/Non Isol","Non-Isolated","Non-Isolated","YES"]
[null,null,6,"Index of Protection  (IP rating)","N/A","IP66","IP66","YES"]
[null,null,"AC  - VOLTAGE  & CURRENT"]
[null,"Solar Input",7,"Voltage Input Nominal (AC) , 3 / N / PE, 230/400V","Vac in","380 -420 V","380 -420 V","YES"]
[null,null,8,"Nr. Of Phases","Ph","3Ph","3Ph","YES"]
[null,null,9,"Input Frequency","F in","50 Hz","50 Hz","YES"]
[null,null,10,"Current Input (AC) AC supply Mains"," Amps","20A","20A - 50A",null,"YES"]
[null,null,"DC - VOLTAGE & CURRENT"]
[null,null,11,"Voltage Input (DC)  Vmax. PV","V DC in PV","1100","1100",null,"YES"]
[null,null,12,"MPPT Range","V DC  PV","200V  to 1000V","200V  to 1000V",null,"YES"]
[null,null,13,"Maximum Current Input (DC)","Imax. DC In","39A / 39A / 39A / 39A","39A / 39A / 39A / 39A",null,"YES"]
[null,null,14,"Short Circuit Current  PV","Isc  PV","48A / 48A / 48A / 48A","48A / 48A / 48A / 48A",null,"YES"]
[]
[null," Output",15,"Nominal Voltage Output (AC)","Vac out","380 -420 V","380 -420 V","YES"]
[null,null,16,"Output Frequency","Hz","50 Hz","50 Hz","YES"]
[null,null,17,"Nr. Of Phases","Ph","3Ph","3Ph","YES"]
[null,null,18,"Output Current Maximum (Imax)","Amps","95.6 A","250A",null,"YES"]
[null,null,19,"Rated Power Output, Active","kW",50000,150000,null,"YES"]
[null,null,20,"Maximum Power Output, Apparent","kVA",59200,{"$f":"G26/0.8","v":187500},null,"YES"]
[null,null,21,"Power Factor Range","N/A","1.0  - 0.8","1.0  - 0.8",null,"YES"]

{"sheet":"ChangeOver","index":4,"n_rows":28,"n_cols":10,"rows_kept":28,"merged":[[1,5,1,6],[2,1,10,1],[2,2,2,3],[10,2,10,3],[11,1,20,1],[15,2,15,3],[21,1,28,1]]}
[]
[null,null,"Item #","Description","Units","Specification",null,"Required","Recommended","Specify"]
[null,"Solar PanelType","Solar Panel "]
[null,null,1,"Solar Panel Size","kVA","50 kVA","150kVA",null,"YES"]
[null,null,2,"Grid-Tied / Hybrid / Off-Grid","N/A","Grid-Tied","Grid-Tied","YES"]
[null,null,3,"Number of Channels","N/A","Four","Four minimum","YES"]
[null,null,4,"Temperature","Deg C","-30 Dec C to +60 Deg C","-30 Dec C to +60 Deg C","YES"]
[null,null,5,"Protective Class","Class","Class I","Class I","YES"]
[null,null,4,"Solar Panel Topology","Isol/Non Isol","Non-Isolated","Non-Isolated","YES"]
[null,null,6,"Index of Protection  (IP rating)","N/A","IP66","IP66","YES"]
[null,null,"AC  - VOLTAGE  & CURRENT"]
[null,"Solar Input",7,"Voltage Input Nominal (AC) , 3 / N / PE, 230/400V","Vac in","380 -420 V","380 -420 V","YES"]
[null,null,8,"Nr. Of Phases","Ph","3Ph","3Ph","YES"]
[null,null,9,"Input Frequency","F in","50 Hz","50 Hz","YES"]
[null,null,10,"Current Input (AC) AC supply Mains"," Amps","20A","20A - 50A",null,"YES"]
[null,null,"DC - VOLTAGE & CURRENT"]
[null,null,11,"Voltage Input (DC)  Vmax. PV","V DC in PV","1100","1100",null,"YES"]
[null,null,12,"MPPT Range","V DC  PV","200V  to 1000V","200V  to 1000V",null,"YES"]
[null,null,13,"Maximum Current Input (DC)","Imax. DC In","39A / 39A / 39A / 39A","39A / 39A / 39A / 39A",null,"YES"]
[null,null,14,"Short Circuit Current  PV","Isc  PV","48A / 48A / 48A / 48A","48A / 48A / 48A / 48A",null,"YES"]
[]
[null," Output",15,"Nominal Voltage Output (AC)","Vac out","380 -420 V","380 -420 V","YES"]
[null,null,16,"Output Frequency","Hz","50 Hz","50 Hz","YES"]
[null,null,17,"Nr. Of Phases","Ph","3Ph","3Ph","YES"]
[null,null,18,"Output Current Maximum (Imax)","Amps","95.6 A","250A",null,"YES"]
[null,null,19,"Rated Power Output, Active","kW",50000,150000,null,"YES"]
[null,null,20,"Maximum Power Output, Apparent","kVA",59200,{"$f":"G26/0.8","v":187500},null,"YES"]
[null,null,21,"Power Factor Range","N/A","1.0  - 0.8","1.0  - 0.8",null,"YES"]