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Enquiries:







ONDERSTEPOORT BIOLOGICAL PRODUCTS LTD

PRIVATE BAG X7, ONDERSTEPOORT 0110


Ms. Mr, Dr.………………….............................. .
Kindly provide the quotation for the following:  OBP 114/2024/25
Period : 12 months 

	Compulsory Document Requirements
	Yes/No

	CSD Report (With a Tax Compliant status that is current)
	

	Declarations SBD4 (Completed, signed & submitted)
	

	Provide reference letters from customers of previous or similar service done as per scope of work (not older than 3 years)
	


NB: Please note that if any of the above requirements is not submitted with the quote it will be an immediate disqualification.

	Quantity
	Product/Item Code
	Specification

	To appoint a supplier for AN Service Level Agreement (SLA) for MAINTENANCE SERVICES & SUPPORT OF STANDBY DIESEL GENERATORS at OBP for a period of 12 months.


	· The Service Level Agreement includes routine maintenance and services, and demand maintenance/ breakdown repairs on the following standby Diesel generators. 
Service Interval: 

· Initial annual service (as per below list) 

· Ongoing 24/7/365 call-out service for the duration of the 12-month SLA period. 

· Final annual Service (as per below list) 



	1
	Cold-room Generator Set
	ENGINE: KIRLOSKAR

HOUR: 167hours

POWER :125KVA

ENGINE TYPE :6R1080TA

Sr No :6H.2514/O40005

Rated KW/HP:115/156

RPM:1500

Rating STD: BS

	2
	Boiler House Generator Set
	ENGINE: KIRLOSKAR

HOURS: 172hours

POWER: 200KVA

ENGINE TYPE:6SL1500TA

Sr No:F6.2511/0800016

Rated KW/HP:187/254

Rating STD:BS 5514

GOVERNIBG CLASS :A1

	3
	EA Generator Set
	ENGINE: SCANIA

TYPE :DC1457

VARIAT:A41D

ENGINE NO:6507476

RATING:500KVA

HOUR:436

	4
	Substation 8 Generator Set
	ENGINE: CATERPILLAR

RATING:500KVA

Ser NO:81Z09089

RPM:1500

POWER:540

HP:403.0KW

AR NO: IW9604

PERF SPEC:0T6506

	
	Procedural Requirements 
2 x Annual Maintenances (to be completed at the start and end of the 12-month SLA period):

For each of the 4 (four) Standby Generator Sets:

· Record and investigate any controller alarms.
· Record the total running hours.
· Record the battery voltage on standby, and during cranking.

· Record the battery charging voltage (both standby, and running)

· Check the starter battery terminals, lugs, and cables for corrosion or leakage. (clean / repair as required)

· Check the diesel tank level indicator / low switch if fitted.
· Inspect the engine governing mechanism and control.

· Thoroughly inspect the condition of cable harnesses, spade connectors, etc. Ensure that all engine-mounted electrical components, relays, and cabling is securely fastened.

· Thoroughly inspect the condition of hoses and clamps (fuel, coolant)

· Check the condition of engine mounts / isolators.
· Check the engine for any leaks (fuel, coolant, oil)

· Check the engine coolant pre-heating temperature.

· Replace Engine Oil & Engine Oil Filters

· Replace the Diesel Fuel Filters

· Clean the diesel fuel separator trap (if fitted)

· Replace the Air Intake Filter, and clean the centrifugal intake separator (if fitted)

· Flush and replace the Engine Coolant

· Clean the radiator core.
· Replace the Auxiliary Drive Belts (Fan & alternator belts)

· Clean and de-grease the engine

· Observe electrical lockout safety, check tightness of main electrical connections and lugs on the generator and electrical panel. Confirm the machine earthing.
· Start the engine on test, and monitor operation:

· Record the generator frequency and phase voltage.

· Switch the unit on load:
· Record the generator frequency, phase voltage, and phase amps.

· Restore the mains power; observe auto transfer delay time, and cooldown time.
· Ensure all electrical panels are closed and locked.

· Remove all used parts, fluids etc from the area. Clean the generator room / enclosure.

· Switch the generator to AUTO, and double check the unit is ready to run.

Technical requirements:

· Complete a detailed service record for each generator set.

· Inform the OBP Engineer immediately if any deficiencies were found.

· All service parts must be original equipment replacement parts.

· Oils must meet the original manufacturers recommendations for grade and viscosity.

· Coolant must meet the original manufacturers specification.

· All used parts, used oils, and coolants must be removed from site and disposed of by the supplier.

· Supplier must allow for any service parts, service equipment, tools and cleaning consumables required. (Filters, v-belts, oils, coolant, tools, cleaning equipment, degreaser, etc)



	
	COSTING BREAKDOWN:

SLA – service costing breakdown: FIXED COST for period of 12 months (EXCL VAT).

Equipment to be serviced / supported:
Quantity
Description
Initial Annual Service (Excl vat)
Final Annual service
(Excl vat)
1

Cold-room
1

Boiler House
1

EA Generator
Substation 8
Service parts, and consumables must be included in the SLA pricing with each service as listed above. 



	
	Additional Requirements: 

Call-out Service:

· An after-hours (24/7/365) call-out service must be available to attend to failures of the standby generating plant (including emergency fuel supply, diesel mechanical faults, electrical faults, batteries, etc). 

· The call-out service must remain in place for the duration of the 12-month SLA agreement. 

· Supplier must stipulate the committed call-out response time. 
· Any remedial work, including replacement of engine parts, contactors, controllers, batteries, etc must be quoted separately for prior authorization under the SLA.




	
	Additional Costing Breakdown:

Description

Per call out

Total cost (excl VAT)

Call out fee (additional work)

Travelling (full distance to OBP)

Description - Additional

Per hourly rate

Total cost (excl VAT)

Technician / Artisan
The above fees need to be a fixed amount for the period of 12 months.


	Supplier Requirements: 
· Supplier must have experience, competence, and expertise in the maintenance of Diesel Electric Generators, Automatic Transfer Panels, Generator Controls, etc (list of contactable references or agency agreements must be provided) 

· Supplier must have permanently employed technicians including. 
· Diesel Mechanics (trade tested), and 

· Electricians (trade tested) 

· Supplier must have an established service operation in the Gauteng area, (within 100km of OBP site) to provide 24/7/365 standby, and cost-effective site support. 


	Standard Submission guidelines and safety Requirements for this SLA.

· All quotations to be itemized. 

· A standard hard copy safety file must be allowed for and submitted before any on-site work commences.

· Service providers to engage with department head daily before proceeding with work.

· Service providers must ensure that job card/service report must be signed off by service representative and OBP personnel before leaving site.

· All work areas to be cleaned and tidied after work is done (no parts, equipment, consumables lying around)
· Should service providers note that during the course of their repairs that equipment requires additional attention such as servicing, repairs or refurbishment, then this must be indicated as such on the job card/service report.  This must be reported to the head of department who will decide on the further course of action.

· All repairs, tasks and services must have a minimum 6 month guarantee on parts and labor/workmanship.
· If any work is to be subcontracted, OBP must be notified. Subcontractors’ supervision is the responsibility of the service provider.  

· Supplier must provide all necessary PPE for service technicians (Gloves, Safety Shoes, Overalls, Hearing Protection, etc) 




SBD 4
BIDDER’S DISCLOSURE

1. PURPOSE OF THE FORM

Any person (natural or juristic) may make an offer or offers in terms of this invitation to bid. In line with the principles of transparency, accountability, impartiality, and ethics as enshrined in the Constitution of the Republic of South Africa and further expressed in various pieces of legislation, it is required for the bidder to make this declaration in respect of the details required hereunder.

Where a person/s are listed in the Register for Tender Defaulters and / or the List of Restricted Suppliers, that person will automatically be disqualified from the bid process. 

2. Bidder’s declaration

2.1 
Is the bidder, or any of its directors / trustees / shareholders / members / partners or any person having a controlling interest
 in the enterprise, 


employed by the state?





YES/NO


2.1.1
If so, furnish particulars of the names, individual identity numbers, and, if applicable, state employee numbers of sole proprietor/ directors / trustees / shareholders / members/ partners or any person having a controlling interest in the enterprise, in table below.
	Full Name
	Identity Number
	Name of State institution

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	


2.2
Do you, or any person connected with the bidder, have a relationship with any person who is employed by the procuring institution? YES/NO


                                          

2.2.1     If so, furnish particulars:

………………………………………………………………………………

………………………………………………………………………………

2.3 
Does the bidder or any of its directors / trustees / shareholders / members / partners or any person having a controlling interest in the enterprise have any interest in any other related enterprise whether or not they are bidding for this contract?



YES/NO
2.3.1 If so, furnish particulars:

…………………………………………………………………………….

…………………………………………………………………………….

3 DECLARATION

I, the undersigned, (name)……………………………………………………………………. in submitting the accompanying bid, do hereby make the following statements that I certify to be true and complete in every respect:

3.1 
I have read, and I understand the contents of this disclosure.
3.2
I understand that the accompanying bid will be disqualified if this disclosure is found not to be true and complete in every respect.

3.3 
The bidder has arrived at the accompanying bid independently from, and without consultation, communication, agreement, or arrangement with any competitor. However, communication between partners in a joint venture or consortium
 will not be construed as collusive bidding.

3.4 
In addition, there have been no consultations, communications, agreements, or arrangements with any competitor regarding the quality, quantity, specifications, prices, including methods, factors or formulas used to calculate prices, market allocation, the intention or decision to submit or not to submit the bid, bidding with the intention not to win the bid and conditions or delivery particulars of the products or services to which this bid invitation relates.
3.4
The terms of the accompanying bid have not been, and will not be, disclosed by the bidder, directly or indirectly, to any competitor, prior to the date and time of the official bid opening or of the awarding of the contract.

3.5 
There have been no consultations, communications, agreements, or arrangements made by the bidder with any official of the procuring institution in relation to this procurement process prior to and during the bidding process except to provide clarification on the bid submitted where so required by the institution; and the bidder was not involved in the drafting of the specifications or terms of reference for this bid.

3.6 I am aware that, in addition and without prejudice to any other remedy provided to combat any restrictive practices related to bids and contracts, bids that are suspicious will be reported to the Competition Commission for investigation and possible imposition of administrative penalties in terms of section 59 of the Competition Act No 89 of 1998 and or may be reported to the National Prosecuting Authority (NPA) for criminal investigation and or may be restricted from conducting business with the public sector for a period not exceeding ten (10) years in terms of the Prevention and Combating of Corrupt Activities Act No 12 of 2004 or any other applicable legislation.

I CERTIFY THAT THE INFORMATION FURNISHED IN PARAGRAPHS 1, 2 and 3 ABOVE IS CORRECT. 

I ACCEPT THAT THE STATE MAY REJECT THE BID OR ACT AGAINST ME IN TERMS OF PARAGRAPH 6 OF PFMA SCM INSTRUCTION 03 OF 2021/22 ON PREVENTING AND COMBATING ABUSE IN THE SUPPLY CHAIN MANAGEMENT SYSTEM SHOULD THIS DECLARATION PROVE TO BE FALSE.  

………………………………
 ..…………………………………………… 



Signature
                          Date

………………………………
………………………………………………
---------------------------------                           ---------------------------------------

Position 
Name of bidder

Terms and Conditions:
-Submission should be no later than           (2 June 2024, 15H00)  
-Please indicate your offer validity and lead time:


-All prices must be VAT exclusive, (Vat vendor please indicate as such) if no indication, prices will be evaluated as exclusive
-Quotation must be on a company letter head and strictly on a PDF format    
-Quotations sent on Word or Excel format will not be accepted  
-Quotations must be emailed back to: purchasing@obpvaccines.co.za   
 If no reply after 14 days of closing date your RFQ was unsuccessfully  

-Orders above 30K will be BEE evaluated

-Please indicate if you are unable to quote and state the reason why

-Please note that fluctuations in the exchange rate (where applicable) will not be for the account of OBP.

-Payment terms:  30 days after statement
Bidders must be registered on CSD (Central Supplier Data base National Treasury) and be tax complaint 

I agree that the offer herein shall remain binding upon me and open for acceptance by OBP during the validity period indicated.
Signature                                                                                                     Date




REQUEST FOR QUOTATION FOR GOODS AND SERVICES





� 


























From:  


Date: 20 May 2024


Tel:   012 522 1500


Fax:


Email: purchasing@obpvaccines.co.za





To:   


Supplier:


Tel:  


Fax:


Email: 








� the power, by one person or a group of persons holding the majority of the equity of an enterprise, alternatively, the person/s having the deciding vote or power to influence or to direct the course and decisions of the enterprise.








� Joint venture or Consortium means an association of persons for the purpose of combining their expertise, property, capital, efforts, skill and knowledge in an activity for the execution of a contract.
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