Specification for the Smart PDU:

Socket configuration		: IEC 60320 C19 (3)

: IEC 60320 C13 (21)

Input outlet			: IEC 60309

Nominal Voltage		: 100-240V AC

Max Current(output)		: 32A

Max current(outlet)		: C19 – 16A; C13 – 10A

Outlet switch 			: Yes, individual outlets

Environment sensor port	: minimum 4

Metering 			: PDU, Outlet Level Current, Voltage, VA, PF,KWh monitoring

Features:

- Supports 10 / 100Mbit Ethernet interface

- Supports TCP / IP, UDP, HTTP, HTTPS, SSL, DHCP, ARP, NTP,
DNS, Telnet, Auto Sense, Ping, SNMP V1,V2 and V3

- Supports three-level account/password security, IP / MAC
filter, 128 bit SSL, and RADIUS

- Supports CC2000, eco DC, multiple browsers (IE, Firefox,
Chrome, and Safari)

- Power-On sequencing – users can set the power-on
sequence and delay time for each outlet to allow equipment
to be powered on in the correct order

- Proactive overload protection (POP) – automatically powers
off the last outlet that causes the current overload while
allowing users to set shutdown priority

- Supports multiple power control methods – Wake on LAN,
System After AC Back, Kill the Power