Eskom Holdings SOC Ltd

Contract number _________
contract title: Provision of refurbishment and supply of turbine centreline Hydraulic pump at Medupi Power Station for a period of 60 months (5YEARS) 



	[image: image1.jpg]R Eskom






NEC3 Term Service Contract (TSC3)
	Between


	ESKOM HOLDINGS SOC Ltd 

(Reg No. 2002/015527/30)

	and


	[Insert at award stage]

(Reg No. ___________ )

	for


	Provision of refurbishment and supply of turbine centreline Hydraulic pump at Medupi Power Station for a period of 60 months (5YEARS) Insert title of the service

	
	

	Contents:


	
	No of pages

	Part C1
	Agreements & Contract Data
	[●]

	Part C2
	Pricing Data
	[●]

	Part C3
	Scope of Work
	[●]

	
	
	

	CONTRACT No.
	[Insert at award stage]

	
	

	
	

	
	


PART C1:
AGREEMENTS & CONTRACT DATA

	Contents:


	
	No of pages

	C1.1
	Form of Offer and Acceptance 

[to be inserted from Returnable Documents at award stage]
	[●]

	C1.2a
	Contract Data provided by the Employer
	[●]

	C1.2b
	Contract Data provided by the Contractor
[to be inserted from Returnable Documents at award stage]
	[●]

	C1.3
	Proforma Guarantees
	[●]


C1.1 Form of Offer & Acceptance

Offer

The Employer, identified in the Acceptance signature block, has solicited offers to enter into a contract for the procurement of:

Provision of refurbishment and supply of turbine centreline Hydraulic pump at Medupi Power Station for a period of 60 months (5YEARS)
The tenderer, identified in the Offer signature block, has examined the documents listed in the Tender Data and addenda thereto and by submitting this Offer has accepted the Conditions of Tender.

By the representative of the tenderer, deemed to be duly authorised, signing this part of this Form of Offer and Acceptance the tenderer offers to perform all of the obligations and liabilities of the Contractor under the contract including compliance with all its terms and conditions according to their true intent and meaning for an amount to be determined in accordance with the conditions of contract identified in the Contract Data. 

Delete the row for the Options which do not apply

	Options A 
	The offered total of the Prices exclusive of VAT is 
	Rate base

	
	Sub total
	Rate base

	
	Value Added Tax @ 15% is
	Rate base

	
	The offered total of the amount due inclusive of VAT is

	

	
	(in words) 



This Offer may be accepted by the Employer by signing the Acceptance part of this Form of Offer and Acceptance and returning one copy of this document including the Schedule of Deviations (if any) to the tenderer before the end of the period of validity stated in the Tender Data, or other period as agreed, whereupon the tenderer becomes the party named as the Contractor in the conditions of contract identified in the Contract Data.

	Signature(s)


	
	
	

	Name(s)


	
	
	

	Capacity


	
	
	

	For the tenderer:

	

	Name & signature of witness
	(Insert name and address of organisation)
	
	Date
	

	Tenderer’s CIDB registration number: 
	


Acceptance

By signing this part of this Form of Offer and Acceptance, the Employer identified below accepts the tenderer’s Offer.  In consideration thereof, the Employer shall pay the Contractor the amount due in accordance with the conditions of contract identified in the Contract Data.  Acceptance of the tenderer’s Offer shall form an agreement between the Employer and the tenderer upon the terms and conditions contained in this agreement and in the contract that is the subject of this agreement.

The terms of the contract, are contained in: 

Part C1

Agreements and Contract Data, (which includes this Form of Offer and Acceptance)

Part C2

Pricing Data

Part C3

Scope of Work: Service Information

and drawings and documents (or parts thereof), which may be incorporated by reference into the above listed Parts.

Deviations from and amendments to the documents listed in the Tender Data and any addenda thereto listed in the Returnable Schedules as well as any changes to the terms of the Offer agreed by the tenderer and the Employer during this process of offer and acceptance, are contained in the Schedule of Deviations attached to and forming part of this Form of Offer and Acceptance.  No amendments to or deviations from said documents are valid unless contained in this Schedule.

The tenderer shall within two weeks of receiving a completed copy of this agreement, including the Schedule of Deviations (if any), contact the Employer’s agent (whose details are given in the Contract Data) to arrange the delivery of any securities, bonds, guarantees, proof of insurance and any other documentation to be provided in terms of the conditions of contract identified in the Contract Data at, or just after, the date this agreement comes into effect.  Failure to fulfil any of these obligations in accordance with those terms shall constitute a repudiation of this agreement.

Notwithstanding anything contained herein, this agreement comes into effect on the date when the tenderer receives one fully completed and signed original copy of this document, including the Schedule of Deviations (if any).  

	Signature(s)


	
	
	

	Name(s)
	
	
	

	Capacity


	
	
	

	for the Employer


	

	Name & signature of witness
	(Insert name and address of organisation)
	
	Date
	


Note: If a tenderer wishes to submit alternative tenders, use another copy of this Form of Offer and Acceptance.

Schedule of Deviations to be completed by the Employer prior to contract award

Note:

1.  This part of the Offer & Acceptance would not be required if the contract has been developed by negotiation between the Parties and is not the result of a process of competitive tendering.
2. The extent of deviations from the tender documents issued by the Employer prior to the tender closing date is limited to those permitted in terms of the Conditions of Tender.

3. A tenderer’s covering letter must not be included in the final contract document.  Should any matter in such letter, which constitutes a deviation as aforesaid be the subject of agreement reached during the process of Offer and Acceptance, the outcome of such agreement shall be recorded here and the final draft of the contract documents shall be revised to incorporate the effect of it.

	No.
	Subject
	Details

	1
	[●]
	[●]

	2
	[●]
	[●]

	3
	[●]
	[●]

	4
	[●]
	[●]

	5
	[●]
	[●]

	6
	[●]
	[●]

	7
	[●]
	[●]

	
	
	


By the duly authorised representatives signing this Schedule of Deviations below, the Employer and the tenderer agree to and accept this Schedule of Deviations as the only deviations from and amendments to the documents listed in the Tender Data and any addenda thereto listed in the Tender Schedules, as well as any confirmation, clarification or changes to the terms of the Offer agreed by the tenderer and the Employer during this process of Offer and Acceptance.  

It is expressly agreed that no other matter whether in writing, oral communication or implied during the period between the issue of the tender documents and the receipt by the tenderer of a completed signed copy of this Form shall have any meaning or effect in the contract between the parties arising from this Agreement. 

	
	For the tenderer:


	
	For the Employer



	Signature


	
	
	

	Name
	
	
	

	Capacity


	
	
	

	On behalf of
	(Insert name and address of organisation)


	
	(Insert name and address of organisation)



	Name & signature of witness
	
	
	

	Date
	
	
	


C1.2 TSC3 Contract Data

Part one - Data provided by the Employer
	Clause
	Statement
	Data

	1
	General
	

	
	The conditions of contract are the core clauses and the clauses for main Option: 
	

	
	
	A:

Priced contract with price list

	
	dispute resolution Option
	W1:
Dispute resolution procedure

	
	and secondary Options
	

	
	
	X1:

Price adjustment for inflation

	
	
	X2

Changes in the law

	
	
	X17:
Low service damages

	
	
	X18:
Limitation of liability

	
	
	X19:
Task Order

	
	
	

	
	
	Z:

Additional conditions of contract

	
	of the NEC3 Term Service Contract April 2013
 (TSC3)
	If 2005 Edition is to be used delete “April 2013” and replace with “June 2005 with amendments June 2006”. Always delete this note before finalising this Data

	10.1
	The Employer is (name):
	Eskom Holdings SOC Ltd (reg no: 2002/015527/30), a state owned company incorporated in terms of the company laws of the Republic of South Africa

	
	Address
	Registered office at Megawatt Park, Maxwell Drive, Sandton, Johannesburg

	
	Tel No.
	[●]

	
	Fax No.
	[●]

	10.1
	The Service Manager is (name): 
	Lebo Pebane

	
	Address
	Medupi Power Station, Steenbokpan Road

	
	Tel
	

	
	Fax
	N/A

	
	e-mail
	MedupiGxTenders@eskom.co.za

	11.2(2)
	The Affected Property is
	Medupi Power Station

	11.2(13)
	The service is 
	Provision of refurbishment and supply of turbine centreline Hydraulic pump at Medupi Power Station for a period of 60 months (5YEARS) 

	11.2(14)
	The following matters will be included in the Risk Register
	All risks will be identified prior and addressed and registered during the risk register meeting that will take place as agreed between the parties

	11.2(15)
	The Service Information is in 
	Part 3: Scope of Work and all documents and drawings to which it makes reference.

	12.2
	The law of the contract is the law of 
	the Republic of South Africa

	13.1
	The language of this contract is 
	English

	13.3
	The period for reply is
	 Two (2) weeks

	2
	The Contractor’s main responsibilities
	Data required by this section of the core clauses is also provided by the Contractor in Part 2 and terms in italics used in this section are identified elsewhere in this Contract Data

	21.1
	The Contractor submits a first plan for acceptance within
	1 week/s of the Contract Date

	3
	Time
	

	30.1
	The starting date is.
	TBC

	30.1
	The service period is
	60 Months (5 Years)

	4
	Testing and defects
	As per NEC TSC 3 clause 40

	5
	Payment
	

	50.1
	The assessment interval is 
	between the 25 day of each successive month.

	51.1
	The currency of this contract is the 
	South African Rand

	51.2
	The period within which payments are made is
	4 weeks.

	51.4
	The interest rate is 


	the publicly quoted prime rate of interest (calculated on a 365 day year) charged by from time to time by the Standard Bank of South Africa Limited (as certified, in the event of any dispute, by any manager of such bank, whose appointment it shall not be necessary to prove) for amounts due in Rands and 

(ii) the LIBOR rate applicable at the time for amounts due in other currencies.  LIBOR is the 6 month London Interbank Offered Rate quoted under the caption “Money Rates” in The Wall Street Journal for the applicable currency or if no rate is quoted for the currency in question then the rate for United States Dollars, and  if no such rate appears in The Wall Street Journal then the rate as quoted by the Reuters Monitor Money Rates Service (or such service as may replace the Reuters Monitor Money Rates Service) on the due date for the payment in question, adjusted mutatis mutandis every 6 months thereafter (and as certified, in the event of any dispute, by any manager employed in the foreign exchange department of The Standard Bank of South Africa Limited, whose appointment it shall not be necessary to prove.

	6
	Compensation events
	As per NEC TSC 3 clause 60

	7
	Use of Equipment Plant and Materials
	As per NEC TSC 3 clause 70

	8
	Risks and insurance
	

	80.1
	These are additional Employer's risks  
	1. [●]

	
	
	2. [●]

	
	
	3. [●]

	9
	Termination
	As per NEC TSC 3 clause 90

	10
	Data for main Option clause
	

	A
	Priced contract with price list
	

	20.5
	The Contractor prepares forecasts of the final total of the Prices for the whole of the service at intervals no longer than 
	4 weeks.

	11
	Data for Option W1
	

	W1.1
	The Adjudicator 
	the person selected from the ICE-SA Division (or its successor body) of the South African Institution of Civil Engineering Panel of Adjudicators by the Party intending to refer a dispute to him.  (see www.ice-sa.org.za). If the Parties do not agree on an Adjudicator the Adjudicator will be appointed by the Arbitration Foundation of Southern Africa (AFSA).

	
	Address
	[●]

	
	Tel No.
	[●]

	
	Fax No.
	[●]

	
	e-mail
	[●]

	W1.2(3)
	The Adjudicator nominating body is: 
	the Chairman of ICE-SA a joint Division of the South African Institution of Civil Engineering and the Institution of Civil Engineers (London) (see www.ice-sa.org.za ) or its successor body.

	W1.4(2)
	The tribunal is: 
	arbitration

	W1.4(5)
	The arbitration procedure is 
	the latest edition of Rules for the Conduct of Arbitrations published by The Association of Arbitrators (Southern Africa) or its successor body.

	
	The place where arbitration is to be held is
	 South Africa

	
	The person or organisation who will choose an arbitrator 

· if the Parties cannot agree a choice or

· if the arbitration procedure does not state who selects an arbitrator, is
	the Chairman for the time being or his nominee of the Association of Arbitrators (Southern Africa) or its successor body.

	12
	Data for secondary Option clauses
	

	X1
	Price adjustment for inflation 
	 Suggested CPA

	X1.1
	The base date for indices is 
	Rates are fixed and firm for first 12 months after first order placement date. There after CPA escalation will apply. Base date will be the month before the month which the enquiry closes.

	
	The proportions used to calculate the Price Adjustment Factor are:
	proportion
	linked to index for
	Index prepared by

	
	
	0,15
	[Labour]
	[SEIFSA TABLE C3 AHPE]

	
	
	0,50
	[Material]
	[SEIFSA TABLE G 1]

	
	
	0.20
	[Transport]
	SEIFSA Table L2 a

	
	
	[0,15]
	non-adjustable
	

	
	
	1.00


	
	

	X2
	Changes in the law
	There is no reference to Contract Data in this Option and terms in italics are identified elsewhere in this Contract Data.

	X17
	Low service damages
	

	X17.1
	The service level table is in
	

	
	
	


	No
	Item
	Employers Requirements/ Descriptions
	Damages payable by contractor

	1
	SDL&I Compliance
	Contractor is expected to comply to SD&LI requirements as per contract. 
	2,5 % retention of monthly fixed rate per month not complying.

	2
	 Poor workmanship 
	Through an investigation and findings that proof poor workman ship. 
	Contractor to carry corrective cost 

	3
	Response time to urgent breakdowns
	Beyond 1 hour of being notified of urgent breakdowns during office hours
	1% of monthly fixed cost per incident/ call-out.


	
	
	

	X18
	Limitation of liability
	

	X18.1
	The Contractor’s liability to the Employer for indirect or consequential loss is limited to
	R0.0 (zero Rand)

	X18.2
	For any one event, the Contractor’s liability to the Employer for loss of or damage to the Employer’s property is limited to
	the amount of the deductibles relevant to the event 

	X18.3
	The Contractor’s liability for Defects due to his design of an item of Equipment is limited to
	The greater of 

the total of the Prices at the Contract Date

and 

the amounts excluded and unrecoverable from the Employer’s insurance) plus the applicable deductibles

	X18.4
	The Contractor’s total liability to the Employer, for all matters arising under or in connection with this contract, other than the excluded matters, is limited to
	the total of the Prices other than for the additional excluded matters.

The Contractor’s total liability for the additional excluded matters is not limited. 

The additional excluded matters are amounts for which the Contractor is liable under this contract for

Defects due to his design, plan and specification,

Defects due to manufacture and fabrication outside the Affected Property, 

loss of or damage to property (other than the Employer’s property, Plant and Materials),

death of or injury to a person and

infringement of an intellectual property right.

	X18.5
	The end of liability date is 
	12 months after the end of the service period.

	X19
	Task Order
	

	X19.5
	The Contractor submits a Task Order programme to the Service Manager within 
	7 days of receiving the Task Order

	Z
	The additional conditions of contract are
	Z1 to Z14 always apply.

	
	

	Z1
	Cession delegation and assignment

	Z1.1
	The Contractor does not cede, delegate or assign any of its rights or obligations to any person without the written consent of the Employer.

	Z1.2
	Notwithstanding the above, the Employer may on written notice to the Contractor cede and delegate its rights and obligations under this contract to any of its subsidiaries or any of its present divisions or operations which may be converted into separate legal entities as a result of the restructuring of the Electricity Supply Industry. 

	
	

	Z2
	Joint ventures

	Z2.1
	If the Contractor constitutes a joint venture, consortium or other unincorporated grouping of two or more persons or organisations then these persons or organisations are deemed to be jointly and severally liable to the Employer for the performance of this contract.

	Z2.2
	Unless already notified to the Employer, the persons or organisations notify the Service Manager within two weeks of the Contract Date of the key person who has the authority to bind the Contractor on their behalf.

	Z2.3
	The Contractor does not alter the composition of the joint venture, consortium or other unincorporated grouping of two or more persons without the consent of the Employer having been given to the Contractor in writing.

	
	

	Z3
	Change of Broad Based Black Economic Empowerment (B-BBEE) status

	Z3.1
	Where a change in the Contractor’s legal status, ownership or any other change to his business composition or business dealings results in a change to the Contractor’s B-BBEE status, the Contractor notifies the Employer within seven days of the change.

	Z3.2
	The Contractor is required to submit an updated verification certificate and necessary supporting documentation confirming the change in his B-BBEE status to the Service Manager within thirty days of the notification or as otherwise instructed by the Service Manager.

	Z3.3
	Where, as a result, the Contractor’s B-BBEE status has decreased since the Contract Date the Employer may either re-negotiate this contract or alternatively, terminate the Contractor’s obligation to Provide the Service.

	Z3.4
	Failure by the Contractor to notify the Employer of a change in its B-BBEE status may constitute a reason for termination. If the Employer terminates in terms of this clause, the procedures on termination are P1, P2 and P4 as stated in clause 92, and the amount due is A1 and A3 as stated in clause 93.

	
	

	Z4
	Confidentiality

	Z4.1
	The Contractor does not disclose or make any information arising from or in connection with this contract available to Others. This undertaking does not, however, apply to information which at the time of disclosure or thereafter, without default on the part of the Contractor, enters the public domain or to information which was already in the possession of the Contractor at the time of disclosure (evidenced by written records in existence at that time).  Should the Contractor disclose information to Others in terms of clause 25.1, the Contractor ensures that the provisions of this clause are complied with by the recipient.

	Z4.2
	If the Contractor is uncertain about whether any such information is confidential, it is to be regarded as such until notified otherwise by the Service Manager.

	Z4.3
	In the event that the Contractor is, at any time, required by law to disclose any such information which is required to be kept confidential, the Contractor, to the extent permitted by law prior to disclosure, notifies the Employer so that an appropriate protection order and/or any other action can be taken if possible, prior to any disclosure.  In the event that such protective order is not, or cannot, be obtained, then the Contractor may disclose that portion of the information which it is required to be disclosed by law and uses reasonable efforts to obtain assurances that confidential treatment will be afforded to the information so disclosed.

	Z4.4
	The taking of images (whether photographs, video footage or otherwise) of the Affected Property or any portion thereof, in the course of Providing the Service and after the end of the service period, requires the prior written consent of the Service Manager.  All rights in and to all such images vests exclusively in the Employer.  

	Z4.5
	The Contractor ensures that all his subcontractors abide by the undertakings in this clause.

	
	

	Z5
	Waiver and estoppel: Add to core clause 12.3:

	Z5.1
	Any extension, concession, waiver or relaxation of any action stated in this contract by the Parties, the Service Manager or the Adjudicator does not constitute a waiver of rights, and does not give rise to an estoppel unless the Parties agree otherwise and confirm such agreement in writing.

	
	

	Z6
	Health, safety and the environment:  Add to core clause 27.4

	Z6.1
	The Contractor undertakes to take all reasonable precautions to maintain the health and safety of persons in and about the execution of the service. Without limitation the Contractor:

accepts that the Employer may appoint him as the “Principal Contractor” (as defined and provided for under the Construction Regulations 2014 (promulgated under the Occupational Health & Safety Act 85 of 1993) (“the Construction Regulations”) for the Affected Property;

warrants that the total of the Prices as at the Contract Date includes a sufficient amount for proper compliance with the Construction Regulations, all applicable health & safety laws and regulations and the health and safety rules, guidelines and procedures provided for in this contract and generally for the proper maintenance of health & safety in and about the execution of the service; and

undertakes, in and about the execution of the service, to comply with the Construction Regulations and with all applicable health & safety laws and regulations and rules, guidelines and procedures otherwise provided for under this contract and ensures that his Subcontractors, employees and others under the Contractor’s direction and control, likewise observe and comply with the foregoing.

	Z6.2
	The Contractor, in and about the execution of the service, complies with all applicable environmental laws and regulations and rules, guidelines and procedures otherwise provided for under this contract and ensures that his Subcontractors, employees and others under the Contractor’s direction and control, likewise observe and comply with the foregoing.

	
	

	Z7
	Provision of a Tax Invoice and interest.  Add to core clause 51

	Z7.1
	Within one week of receiving a payment certificate from the Service Manager in terms of core clause 51.1, the Contractor provides the Employer with a tax invoice in accordance with the Employer's procedures stated in the Service Information, showing the amount due for payment equal to that stated in the payment certificate.

	Z7.2
	If the Contractor does not provide a tax invoice in the form and by the time required by this contract, the time by when the Employer is to make a payment is extended by a period equal in time to the delayed submission of the correct tax invoice.  Interest due by the Employer in terms of core clause 51.2 is then calculated from the delayed date by when payment is to be made.

	Z7.3
	The Contractor (if registered in South Africa in terms of the companies Act) is required to comply with the requirements of the Value Added Tax Act, no 89 of 1991 (as amended) and to include the Employer’s VAT number 4740101508 on each invoice he submits for payment.

	
	

	Z8
	Notifying compensation events

	Z8.1
	Delete the last paragraph of core clause 61.3 and replace with:

If the Contractor does not notify a compensation event within eight weeks of becoming aware of the event, he is not entitled to a change in the Prices.

	
	

	Z9
	Employer’s limitation of liability

	Z9.1
	The Employer’s liability to the Contractor for the Contractor’s indirect or consequential loss is limited to R0.00 (zero Rand)

	Z9.2
	The Contractor’s entitlement under the indemnity in 82.1 is provided for in 60.1(12) and the Employer’s liability under the indemnity is limited to compensation as provided for in core clause 63 and X19.11 if Option X19 Task Order applies to this contract. 

	
	

	Z10
	Termination: Add to core clause 91.1, at the second main bullet point, fourth sub-bullet point, after the words "against it":  

	Z10.1
	   or had a business rescue order granted against it.

	
	

	Z11
	Ethics

	For the purposes of this Z-clause, the following definitions apply:

	Affected Party
	means, as the context requires, any party, irrespective of whether it is the Contractor or a third party, such party’s employees, agents, or Subcontractors or Subcontractor’s employees, or any one or more of all of these parties’ relatives or friends,

	Coercive Action
	means to harm or threaten to harm, directly or indirectly, an Affected Party or the property of an Affected Party, or to otherwise influence or attempt to influence an Affected Party to act unlawfully or illegally,

	Collusive Action
	means where two or more parties co-operate to achieve an unlawful or illegal purpose, including to influence an Affected Party to act unlawfully or illegally,

	Committing Party
	means, as the context requires, the Contractor, or any member thereof in the case of a joint venture, or its employees, agents, or Subcontractors or the Subcontractor’s employees,

	Corrupt Action
	means the offering, giving, taking, or soliciting, directly or indirectly, of a good or service to unlawfully or illegally influence the actions of an Affected Party,

	Fraudulent Action
	means any unlawfully or illegally intentional act or omission that misleads, or attempts to mislead, an Affected Party, in order to obtain a financial or other benefit or to avoid an obligation or incurring an obligation,

	Obstructive Action
	means a Committing Party unlawfully or illegally destroying, falsifying, altering or concealing information or making false statements to materially impede an investigation into allegations of Prohibited Action, and

	Prohibited Action
	means any one or more of a Coercive Action, Collusive Action Corrupt Action, Fraudulent Action or Obstructive Action.

	Z11.1
	A Committing Party may not take any Prohibited Action during the course of the procurement of this contract or in execution thereof.

	Z11.2
	The Employer may terminate the Contractor’s obligation to Provide the Services if a Committing Party has taken such Prohibited Action and the Contractor did not take timely and appropriate action to prevent or remedy the situation, without limiting any other rights or remedies the Employer has. It is not required that the Committing Party had to have been found guilty, in court or in any other similar process, of such Prohibited Action before the Employer can terminate the Contractor’s obligation to Provide the Services for this reason.

	Z11.3
	If the Employer terminates the Contractor’s obligation to Provide the Services for this reason, the amounts due on termination are those intended in core clauses 92.1 and 92.2.

	Z11.4
	A Committing Party co-operates fully with any investigation pursuant to alleged Prohibited Action. Where the Employer does not have a contractual bond with the Committing Party, the Contractor ensures that the Committing Party co-operates fully with an investigation.


Z12

Insurance

Z _12_.1
Replace core clause 83 with the following:
	Insurance cover
	83
	

	
	83.1
	When requested by a Party, the other Party provides certificates from his insurer or broker stating that the insurances required by this contract are in force.



	
	83.2
	The Contractor provides the insurances stated in the Insurance Table A from the starting date until the earlier of Completion and the date of the termination certificate. 

INSURANCE TABLE A

Insurance against
Minimum amount of cover or minimum limit of indemnity
Loss of or damage caused by the Contractor to the Employer’s property
The replacement cost where not covered by the Employer’s insurance.

The Employer’s policy deductible as at Contract Date, where covered by the Employer’s insurance.
Loss of or damage to Plant and Materials
The replacement cost where not covered by the Employer’s insurance.

The Employer’s policy deductible as at Contract Date, where covered by the Employer’s insurance.
Loss of or damage to Equipment
The replacement cost where not covered by the Employer’s insurance.

The Employer’s policy deductible as at Contract Date, where covered by the Employer’s insurance.
The Contractor’s liability for loss of or damage to property (except the Employer’s property, Plant and Materials and Equipment) and liability for bodily injury to or death of a person (not an employee of the Contractor) arising from or in connection with the Contractor’s Providing the Service
Loss of or damage to property

The replacement cost

Bodily injury to or death of a person

The amount required by the applicable law.

Liability for death of or bodily injury to employees of the Contractor arising out of and in the course of their employment in connection with this contract
The amount required by the applicable law



	
	
	

	
	
	


Z __12.2
Replace core clause 86 with the following:

	Insurance by the Employer
	86
	

	
	86.1
	The Employer provides the insurances stated in the Insurance Table B

	
	
	

	
	
	INSURANCE TABLE B
Insurance against or name of policy

Minimum amount of cover or minimum limit of indemnity

Assets All Risk

Per the insurance policy document

Contract Works insurance

Per the insurance policy document

Environmental Liability

Per the insurance policy document

General and Public Liability

Per the insurance policy document

Transportation (Marine)

Per the insurance policy document

Motor Fleet and Mobile Plant

Per the insurance policy document

Terrorism

Per the insurance policy document

Cyber Liability

Per the insurance policy document

Nuclear Material Damage and Business Interruption

Per the insurance policy document

Nuclear Material Damage Terrorism

Per the insurance policy document




	Z13
	Nuclear Liability

	Z13.1
	The Employer is the operator of the Koeberg Nuclear Power Station (KNPS), a nuclear installation, as designated by the National Nuclear Regulator of the Republic of South Africa, and is the holder of a nuclear licence in respect of the KNPS.

	Z13.2
	The Employer is solely responsible for and indemnifies the Contractor or any other person against any and all liabilities which the Contractor or any person may incur arising out of or resulting from nuclear damage, as defined in Act 44 of 1999, save to the extent that any liabilities are incurred due to the unlawful intent of the Contractor or any other person or the presence of the Contractor or that person or any property of the Contractor or such person at or in the KNPS or on the KNPS site, without the permission of the Employer or of a person acting on behalf of the Employer.

	Z13.3
	Subject to clause Z13.4 below, the Employer waives all rights of recourse, arising from the aforesaid, save to the extent that any claims arise or liability is incurred due or attributable to the unlawful intent of the Contractor or any other person, or the presence of the Contractor or that person or any property of the Contractor or such person at or in the KNPS or on the KNPS site, without the permission of the Employer or of a person acting on behalf of the Employer.

	Z13.4
	The Employer does not waive its rights provided for in section 30 (7) of Act 44 of 1999, or any replacement section dealing with the same subject matter.

	Z13.5
	The protection afforded by the provisions hereof shall be in effect until the KNPS is decommissioned.

	
	

	Z14
	Asbestos

	For the purposes of this Z-clause, the following definitions apply:

	AAIA
	means approved asbestos inspection authority.

	ACM
	means asbestos containing materials.

	AL
	means action level, i.e. a level of 50% of the OEL, i.e. 0.1 regulated asbestos fibres per ml of air measured over a 4 hour period. The value at which proactive actions is required in order to control asbestos exposure to prevent exceeding the OEL.

	Ambient Air
	means breathable air in area of work with specific reference to breathing zone, which is defined to be a virtual area within a radius of approximately 30cm from the nose inlet.

	Compliance Monitoring
	means compliance sampling used to assess whether or not the personal exposure of workers to regulated asbestos fibres is in compliance with the Standard’s requirements for safe processing, handling, storing, disposal and phase-out of asbestos and asbestos containing material, equipment and articles.

	OEL
	means occupational exposure limit.

	Parallel Measurements
	means measurements performed in parallel, yet separately, to existing measurements to verify validity of results.

	Safe Levels
	means  airborne asbestos exposure levels conforming to the Standard’s requirements for safe processing, handling, storing, disposal and phase-out of asbestos and asbestos containing material, equipment and articles.

	Standard
	means the Employer’s Asbestos Standard 32-303: Requirements for Safe Processing, Handling, Storing, Disposal and Phase-out of Asbestos and Asbestos Containing Material, Equipment and Articles.

	SANAS
	means the South African National Accreditation System.

	TWA
	means the average exposure, within a given workplace, to airborne asbestos fibres, normalised to the baseline of a 4 hour continuous period, also applicable to short term exposures, i.e. 10-minute TWA.

	Z14.1
	The Employer ensures that the Ambient Air in the area where the Contractor will Provide the Services conforms to the acceptable prescribed South African standard for asbestos, as per the regulations published in GNR 155 of 10 February 2002, under the Occupational Health and Safety Act, 1993 (Act 85 of 1993) (“Asbestos Regulations”). The OEL for asbestos is 0.2 regulated asbestos fibres per millilitre of air as a 4-hour TWA, averaged over any continuous period of four hours, and the short term exposure limit of 0.6 regulated asbestos fibres per millilitre of air as a 10-minute TWA, averaged over any 10 minutes, measured in accordance with HSG248 and monitored according to HSG173 and OESSM.

	Z14.2
	Upon written request by the Contractor, the Employer certifies that these conditions prevail. All measurements and reporting are effected by an independent, competent, and certified occupational hygiene inspection body, i.e. a SANAS accredited and Department of Employment and Labour approved AAIA. The Contractor may perform Parallel Measurements and related control measures at the Contractor’s expense. For the purposes of compliance the results generated from Parallel Measurements are evaluated only against South African statutory limits as detailed in clause Z14.1. Control measures conform to the requirements stipulated in the AAIA-approved asbestos work plan.

	Z14.3
	The Employer manages asbestos and ACM according to the Standard.

	Z14.4
	In the event that any asbestos is identified while Providing the Services, a risk assessment is conducted and if so required, with reference to possible exposure to an airborne concentration of above the AL for asbestos, immediate control measures are implemented and relevant air monitoring conducted in order to declare the area safe.

	Z14.5
	The Contractor’s personnel are entitled to stop working and leave the contaminated area forthwith until such time that the area of concern is declared safe by either Compliance Monitoring or an AAIA approved control measure intervention, for example, per the emergency asbestos work plan, if applicable.

	Z14.6
	The Contractor continues to Provide the Services, without additional control measures presented, on presentation of Safe Levels. The contractually agreed dates to Provide the Services, including the Completion Date, are adjusted accordingly. The contractually agreed dates are extended by the notification periods required by regulations 3 and 21 of the Asbestos Regulations, 2001.

	Z14.7
	Any removal and disposal of asbestos, asbestos containing materials and waste, is done by a registered asbestos contractor, instructed by the Employer at the Employer’s expense, and conducted in line with South African legislation.


C1.2 Contract Data

Part two - Data provided by the Contractor
[Instructions to the contract compiler:  (delete this notes before issue to tenderers with an enquiry)
Whenever a cell is shaded in the left hand column it denotes this data is optional and would be required in relation to the option selected.  In the event that the option is not required select and delete the whole row.]

Notes to a tendering contractor:

1. Please read both the both the NEC3 Term Service Contract April 2013 and the relevant parts of its Guidance Notes (TSC3-GN)
 in order to understand the implications of this Data which the tenderer is required to complete.

2. The number of the clause which requires the data is shown in the left hand column for each statement however other clauses may also use the same data.

3. Where a form field like this [     ] appears, data is required to be inserted relevant to the option selected. Click on the form field once and type in the data.  Otherwise complete by hand and in ink.

Completion of the data in full, according to Options chosen, is essential to create a complete contract.

	Clause
	Statement
	Data

	10.1
	The Contractor is (Name):
	     

	
	Address
	     

	
	Tel No.
	     

	
	Fax No.
	     

	11.2(8)
	The direct fee percentage is
	     %

	
	The subcontracted fee percentage is
	     %

	11.2(14)
	The following matters will be included in the Risk Register
	     

	11.2(15)
	The Service Information for the Contractor’s plan is in:
	     

	21.1
	The plan identified in the Contract Data is contained in:
	     

	24.1
	The key people are:
	

	
	1

Name:
	     

	
	

Job:
	     

	
	

Responsibilities:
	     

	
	

Qualifications:
	     

	
	

Experience:
	     

	
	2

Name:
	     

	
	

Job
	     

	
	

Responsibilities:
	     

	
	

Qualifications:
	     

	
	

Experience:
	     

	
	
	     

	
	
	CV's (and further key person's data including CVs) are in      .

	A
	Priced contract with price list
	

	11.2(12)
	The price list is in
	     

	11.2(19)
	The tendered total of the Prices is
	R     

	C
	Target contract with price list
	

	11.2(12)
	The price list is in
	     

	11.2(20)
	The tendered total of the Prices is
	R     

	E
	Cost reimbursable contract
	

	11.2(12)
	The price list is in
	     


Part 2: Pricing Data

TSC3 Option A

	Document reference
	Title
	No of pages

	C2.1
	Pricing assumptions: Option A
	2

	C2.2
	The price list 
	[●]


C2.1 Pricing assumptions: Option A

How work is priced and assessed for payment

Clause 11 in NEC3 Term Service Contract (TSC3) core clauses and Option A states:

	Identified and defined terms
	11

11.2
	(12) The Price List is the price list unless later changed in accordance with this contract.



	
	
	(17) The Price for Services Provided to Date is the total of 

· the Price for each lump sum item in the Price List which the Contractor has completed and
· where a quantity is stated for an item in the Price List, an amount calculated by multiplying the quantity which the Contractor has completed by the rate.


	
	
	(19) The Prices are the amounts stated in the Price column of the Price List. Where a quantity is stated for an item in the Price List, the Price is calculated by multiplying the quantity by the rate.




This confirms that Option A is a priced contract where the Prices are derived from a list of items of service which can be priced as lump sums or as expected quantities of service multiplied by a rate or a mix of both.

Function of the Price List

Clause 54.1 in Option A states: “Information in the Price List is not Service Information”.  This confirms that instructions to do work or how it is to be done are not included in the Price List but in the Service Information.  This is further confirmed by Clause 20.1 which states, “The Contractor Provides the Service in accordance with the Service Information”. Hence the Contractor does not Provide the Service in accordance with the Price List.   The Price List is only a pricing document.  

Link to the Contractor’s plan

Clause 21.4 states “The Contractor provides information which shows how each item description on the Price List relates to the operations on each plan which he submits for acceptance”.  Hence when compiling the price list, the tendering contractor needs to develop his first clause 21.2 plan in such a way that operations shown on it can be priced in the price list  and result in a satisfactory cash flow in terms of clause 11.2(17). 

Preparing the price list
Before preparing the price list, both the Employer and tendering contractors should read the TSC3 Guidance Notes pages 14 and 15.  In an Option A contract, either Party may have entered items into the price list either as a process of offer and acceptance (tendering) or by negotiation depending on the nature of the service to be provided.  Alternatively the Employer, in his Instructions to Tenderers or in a Tender Schedule, may have listed some items that he requires the Contractor to include in the price list to be prepared and priced by him. 

It is assumed that in preparing or finalising the price list the Contractor:
· Has taken account of the guidance given in the TSC3 Guidance Notes relevant to Option A;

· Understands the function of the Price List and how work is priced and paid for;

· Is aware of the need to link operations shown in his plan to items shown in the Price List;

· Has listed and priced items in the price list which are inclusive of everything necessary and incidental to Providing the Service in accordance with the Service Information, as it was at the time of tender, as well as correct any Defects not caused by an Employer’s risk;
· Has priced work he decides not to show as a separate item within the Prices or rates of other listed items in order to fulfil the obligation to complete the service for the tendered total of the Prices. 
· Understands there is no adjustment to items priced as lump sums if the amount, or quantity, of work within that item later turns out to be different to that which the Contractor estimated at time of tender. The only basis for a change to the (lump sum) Prices is as a result of a compensation event. 
Format of the price list
(From the example given in an Appendix within the TSC3 Guidance Notes)

Entries in the first four columns in the price list in section C2.2 are made either by the Employer or the tendering contractor. 

If the Contractor is to be paid an amount for the item which is not adjusted if the quantity of work in the item changes, the tendering contractor enters the amount in the Price column only, the Unit, Expected Quantity and Rate columns being left blank.

If the Contractor is to be paid an amount for an item of work which is the rate for the work multiplied by the quantity completed, the tendering contractor enters the rate which is then multiplied by the Expected Quantity to produce the Price, which is also entered.

If the Contractor is to be paid a Price for an item proportional to the length of time for which a service is provided, a unit of time is stated in the Unit column and the expected length of time (as a quantity of the stated units of time) is stated in the Expected Quantity column.

C2.2 the price list
1.  Supply of Turbine Centreline Hydraulic Pumps








	Item No.
	Mat No
	Description
	Unit
	Qty over 5 years
	 Rate 

	1
	645239
	PUMP, ROTARY:
TYPE: HYDRAULIC, SCREW;
PORT SIZE: DN80;
CAPACITY: 92 DM3/S;
SPEED: 2900 RPM;
RATING: 40 BAR;
SPECIFICATION: L3MF60/120;
	Each
	6
	 







2. Refurbishment of Turbine Centreline Hydraulic Pumps



	Item No.
	Mat No
	Description
	Unit
	 Qty over 5 years
	 Rate 

	1
	645239
	PUMP, ROTARY:
TYPE: HYDRAULIC, SCREW;
PORT SIZE: DN80;
CAPACITY: 92 DM3/S;
SPEED: 2900 RPM;
RATING: 40 BAR;
SPECIFICATION: L3MF60/120;
	Each
	6
	 







Note: 1. Quantities are provisional

2. Contract period is 60 Months (5 years)

Part 3: Scope of Work

	Document reference
	Title
	No of pages

	
	This cover page
	1

	C3.1
	Employer’s Service Information
	

	C3.2
	Contractor’s Service Information

(insert at award stage or delete if not applicable)
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	Total number of pages
	


C3.1: Employer’s service Information

Contents

1Part 3: Scope of Work

C3.1: Employer’s service Information
2
1
Description of the service
4
1.1
Executive overview
4
1.2
Employer’s requirements for the service
4
1.3
Interpretation and terminology
4
2
Management strategy and start up.
5
2.1
The Contractor’s plan for the service
5
2.2
Management meetings
5
2.3
Contractor’s management, supervision and key people
6
2.4
Provision of bonds and guarantees
6
2.5
Documentation control
6
2.6
Invoicing and payment
6
2.7
Contract change management
6
2.8
Records of Defined Cost to be kept by the Contractor
7
2.9
Insurance provided by the Employer
7
2.10
Training workshops and technology transfer
7
2.11
Design and supply of Equipment
7
2.12
Things provided at the end of the service period for the Employer’s use
7
2.12.1
Equipment
7
2.12.2
Information and other things
7
2.13
Management of work done by Task Order
8
3
Health and safety, the environment and quality assurance
9
3.1
Health and safety risk management
9
3.2
Environmental constraints and management
9
3.3
Quality assurance requirements
9
4
Procurement
10
4.1
People
10
4.1.1
Minimum requirements of people employed
10
4.1.2
BBBEE and preferencing scheme
10
4.1.3
Accelerated Shared Growth Initiative – South Africa (ASGI-SA)
10
4.2
Subcontracting
10
4.2.1
Preferred subcontractors
10
4.2.2
Subcontract documentation, and assessment of subcontract tenders
10
4.2.3
Limitations on subcontracting
11
4.2.4
Attendance on subcontractors
11
4.3
Plant and Materials
11
4.3.1
Specifications
11
4.3.2
Correction of defects
11
4.3.3
Contractor’s procurement of Plant and Materials
11
4.3.4
Tests and inspections before delivery
11
4.3.5
Plant & Materials provided “free issue” by the Employer
12
4.3.6
Cataloguing requirements
12
5
Working on the Affected Property
13
5.1
Employer’s site entry and security control, permits, and site regulations
13
5.2
People restrictions, hours of work, conduct and records
13
5.3
Health and safety facilities on the Affected Property
13
5.4
Environmental controls, fauna & flora
13
5.5
Cooperating with and obtaining acceptance of Others
13
5.6
Records of Contractor’s Equipment
13
5.7
Equipment provided by the Employer
14
5.8
Site services and facilities
14
5.8.1
Provided by the Employer
14
5.8.2
Provided by the Contractor
14
5.9
Control of noise, dust, water and waste
14
5.10
Hook ups to existing works
14
5.11
Tests and inspections
14
5.11.1
Description of tests and inspections
14
5.11.2
Materials facilities and samples for tests and inspections
14
6
List of drawings
15
6.1
Drawings issued by the Employer
15


1 Description of the service
1.1 Executive overview 

The service involves the supply of new hydraulic pumps and the refurbishment of existing L3MF-060 rotary screw hydraulic pumps used for the HP and IP turbine control and stop valves at Medupi Power Station, located in Limpopo, South Africa. 
The hydraulic system operates in a 2 x 100% configuration (one pump in service, one on standby) and plays a critical role in turbine safety and control. This long-term contract ensures reliable operation through: 

· Supply of new pumps according to OEM specifications. 

· Full refurbishment of existing pumps, including disassembly, inspection, repair, testing, and documentation. 
· Engineering services to ensure compatibility, design improvements, and technical verification. 

· Quality assurance, NDT, and certification in line with Eskom and internal standards. 

The Contractor must have multidisciplinary capabilities in mechanical engineering, non-destructive testing (NDT), quality assurance (QA/QC) logistics, and document control. The majority of the work, particularly refurbishment, engineering assessment, and testing, will take place off-site at the Contractor’s workshop, with delivery and collection occurring at Medupi Power Station. 
1.2 Employer’s requirements for the service
The Employer requires the Contractor to: 
· Supply new OEM-equivalent L3MF-60 rotary screw hydraulic pumps, with associated technical documentation, quality certificates, and preservation standards. 

· Refurbish existing pumps, including: 

· Collection from Medupi Power Station 

· Complete disassembly and inspection 

· Repair and replacement of components (spindles, bearings, seals, etc) using OEM parts, 

· Reassembly and pressure testing

· Vibration testing per ISO 20816-1:2016

· Delivery back to site after acceptance

The Contractor shall submit and obtain approval for: 

· Quality Control Plans (QCPs) and Inspection and Test Plans (ITPs) before starting any work 

· Engineering assessments, and manufacturing schedules, 

· A complete data pack post-refurbishment containing inspection reports, certificates, drawings, NCR close-out reports, and personnel qualifications. 

The Contractor is also responsible for compliance with: 

· Eskom’s Supplier Quality Management Specification (240-105658000), 
· Eskom’s NDT Standard (240-83540088), 

· All relevant safety, quality, and environmental regulations. 

A Spare Contract Bill of Materials (BOM) listing the expected components and quantities for the 5-year contract is provided in the Scope of Work Annexure (241- 20221135 Medupi Power Station Scope of Work for Supply and Refurbishment of Turbine Hydraulic Pumps). 

1.3 Interpretation and terminology

Interpretations:
· Suppler refers to the Contractor appointed to perform the services. 

· Employer refers to Eskom Holding SOC Ltd – Medupi Power Station. 

· Pump refers specifically to the rotary screw hydraulic pumps installed in the turbine hydraulic system. 
The following abbreviations are used in this Service Information:

	Abbreviation
	Meaning given to the abbreviation

	BOM 
	Bill of Materials 

	EoMR
	End of Manufacturing Report 

	FAT
	Factory Acceptance Testing 

	ITP
	Inspection and Test Plan 

	NCR
	Non-Conformance Report 

	NDT 
	Non-Destructive Testing 

	OEM 
	Original Equipment Manufacturer 

	PMA
	Particular Material Appraisal 

	QCP
	Quality Control Plan 

	SAT 
	Site Acceptance Testing 

	URS 
	User Requirement Specification 


2 Management strategy and start up.
2.1 The Contractor’s plan for the service
The Contract is required to develop and submit a detailed plan that outlines how the service will be executed in accordance with clause 21.2 of the TSC3 conditions of contract. The plan must cover the following aspects throughout the 5-year contract period: 
a) Execution Strategy: 

· The Contract shall provide a schedule for both the supply of new pumps and the refurbishment of existing pumps, clearly identifying: 

· Collection dates from Medupi Power Station 

· Workshop refurbishment phases (disassembly, inspection, repairs, reassembly, and testing)

· Delivery of refurbished pumps back to site

· Procurement and delivery schedule for new pumps

b) Refurbishment Sequence and Dependencies: 

· No work may commence until the Contractor’s Quality Control Plan (QCP) and Inspection and Test Plan (ITP) are accepted by the Employer. 

· Refurbishment shall follow a serial batch approach, with minimal turnaround times to ensure system availability. 

· Any subcontracted work (e.g., NDT) must be done by Employer-approved service providers and planned accordingly. 

c) Technical and Engineering Submissions: 

· The Contractor shall submit:

· Engineering assessments of components

· Revised or updated manufacturing drawings if modifications are proposed

· Material traceability summaries and PMAs (where applicable)

· Welding procedures if required

d) Documentation and Compliance: 

· Submission shall meet Eskom standards, including: 

· Material certificates (EN 10204 3.1 or 3.2  as applicable)

· NDT results and NCR close-outs 

· Final data books and End of Manufacturing Reports (EoMR)

e) Reporting and Scheduling Requirements: 
· The Contract shall provide:

· Monthly progress reports with key milestones 

· Updated delivery schedules 

· Notification of planned inspections at least 4 weeks in advance for off-site inspections

· Test results and compliance documentation post-refurbishment or delivery
2.2 Management meetings

Regular meetings of a general nature may be convened and chaired by the Supply Manager as follows:

	Title and purpose
	Approximate time & interval
	Location
	Attendance by:

	Risk register and compensation events
	As and when required
	
	Employer, Contractor

	Overall contract progress and feedback
	As and when required
	
	Employer, Contractor 

	Kick-off
	Once off
	
	Employer, Contractor

	
	
	
	


Meetings of a specialist nature may be convened as specified elsewhere in this Service Information or if not so specified by persons and at times and locations to suit the Parties, the nature and the progress of the service.  Records of these meetings shall be submitted to the Service Manager by the person convening the meeting within five days of the meeting.  

All meetings shall be recorded using minutes or a register prepared and circulated by the person who convened the meeting.   Such minutes or register shall not be used for the purpose of confirming actions or instructions under the contract as these shall be done separately by the person identified in the conditions of contract to carry out such actions or instructions.  

2.3 Contractor’s management, supervision and key people

The Contractor shall provide and maintain a competent management and supervision team for the duration of the contract. The team shall be adequately staffed to ensure that all activities (including the supply, refurbishment, quality control, documentation, and delivery) are executed efficiently, safely, and in compliance with the Employer’s requirements. 
Minimum Requirements: 

1. Dedicated Project Manager: 

· Responsible for overall contract delivery, communication with the Employer, and decision-making. 

· Acts as the Contractor’s primary point of contact. 

2. Quality Assurance / Quality Control (QA/QC) Representative:

· Oversees compliance with Eskom’s Supplier Quality Management Specification (240-105658000). 

· Ensures proper implementation of QCPs, ITPLs, and documentation of NCRs. 

3. Lead Mechanical Engineer / Technical Manager: 

· Responsible for the engineering execution, technical compliance, and coordination with OEM requirements. 

· Provides technical support for refurbishment processes and new pump specifications. 

4. Workshop Supervisor: 

· Manages on-site execution of refurbishment, disassembly, testing, and packaging operations. 

· Ensures safe handling, preservation, and transportation of equipment.

5. Document Controller: 

· Manages the collation, control, and submission of all documentation including data packs, test certificates, and drawings. 

6. Health, Safety, and Environmental (HSE) Officer: 
· Ensures all refurbishment and transport activities comply with applicable health and safety laws and Eskom’s safety standards. 

Additional Requirements: 

The Contractor shall submit an organogram within 7 days of contract award, detailing: 

· All key personnel 

· Reporting lines 

· Communication responsibilities 

· Contact details and backup personnel

The Employer reserves the right to review, reject, or request replacement of any key personnel deemed unfit or unable to fulfil contractual duties. 

Any changes to key personnel during the contract shall be communicated in writing and subject to the Employer’s approval. 

2.4 Provision of bonds and guarantees

The form in which a bond or guarantee required by the conditions of contract (if any) is to be provided by the Contractor is given in Part 1 Agreements and Contract Data, document C1.3, Sureties.  

The Employer may withhold payment of amounts due to the Contractor until the bond or guarantee required in terms of this contract has been received and accepted by the person notified to the Contractor by the Service Manager to receive and accept such bond or guarantee.  Such withholding of payment due to the Contractor does not affect the Employer’s right to termination stated in this contract. 
2.5 Documentation control

Document management control will be handled as per The Employer’s document and records management procedure 32-1216 which is obtainable from The Employer’s Representative, All communication will be in writing. All NEC standard forms shall be used, e.g Task Order, Early warnings, Defect notifications and Assessments.
2.6 Invoicing and payment
Within one week of receiving a payment certificate from the Service Manager in terms of core clause 51.1, the Contractor provides the Employer with a tax invoice showing the amount due for payment equal to that stated in the Service Manager’s payment certificate.  
The Contractor shall address the tax invoice to 

_________________________ 

and include on each invoice the following information:

· Name and address of the Contractor and the Service Manager; 

· The contract number and title;

· Contractor’s VAT registration number;

· The Employer’s VAT registration number 4740101508;

· Description of service provided for each item invoiced based on the Price List;

· Total amount invoiced excluding VAT, the VAT and the invoiced amount including VAT;

· (add other as required)

Add procedures for invoice submission and payment (e. g. electronic payment instructions)

2.7 Contract change management 
a) The Service Manager issues a Task order to The Contractor to authorise the execution of the work.

b) In the event where it is identified that there is additional work to be done outside the scope of work on the Task order, the Contractor will give The Service Manager an early warning with a written quotation.

c) If agreed, the Service Manager issues a revised Task Order or additional Task Order.

d) The Contractor starts the work on the starting date of the Task Order. 

e) In case of compensation event either party will notify the other. And NEC3 TSC clause 60 has to be followed. 
f) Refers to Z-Claus 8.1
2.8 Records of Defined Cost to be kept by the Contractor
In order to substantiate the define Cost of compensation events, the Employer may require the Contractor to keep records of amounts paid by him for people employed by the Contractor, Plant and Materials, work subcontracted by the Contractor and Equipment. The Contractor will complete the site daily log and this will be submitted to the Employers Representatives for signature before 12am of the following day barring weekends. The Friday and weekend logs will be submitted before 12am Mondays. The log will include but not be limited to the following:

a) Date and day.

b) Site Conditions.

c) Work Done.

d) Labour on site.

e) Any incidents during that period.

f) Any communication that took place.

2.9 Insurance provided by the Employer
Reference to TSC3 Core Clause 86.1

2.10 Training workshops and technology transfer

The Contractor shall provide training and technology transfer to support operational readiness and knowledge retention for the Employer’s maintenance and engineering teams. 
Training Workshops: 

· A minimum of one (1) hands-on on-site training workshop shall be conducted annually during the contract period, aligned with the delivery, or return of refurbished pumps. 
· Training shall cover: 

· Hydraulic pump function and system integration 

· Disassembly and reassembly procedures 

· Inspection criteria and common failure modes 

· Interpretation of test results (e.g., pressure and vibration tests)

· Preservation and handling requirements for long-term storage

· The Contractor shall provide training materials, including presentations, manuals, checklists, and handouts for reference. 

Technology Transfer: 

· The Contractor shall include a comprehensive Operation and Maintenance (O&M) manual update, incorporating learnings from the refurbishment process and any design enhancements. 
· Recommendations for lifecycle improvements and historical defect trends shall be included in the final data pack. 

· Where new equipment or technology is introduced, the Contractor shall supply training to ensure Employer understanding and operational capacity.  
2.11 Design and supply of Equipment

The Contractor is responsible for the design, manufacture, supply, and validation of any specialised tools or equipment required for the safe handling, disassembly, testing, or reassembly of the rotary screw hydraulic pumps. 
· Design documents, including lifting plans, jigs, fixtures, and transport cradles, must be submitted for information purposes to the Service Manager. While no formal acceptance is required, the Employer reserves the right to raise concerns and request justification or modification. 
· All equipment used in the refurbishment or testing processes must comply with relevant safety standards and Eskom technical specifications. 
· The Contractor retains full liability for the design, safe use, and integrity of all tools and equipment supplied or used under this contract. 

· The Employer reserves the right to witness and/or place hold points at key stages of equipment manufacturing, assembly, or final testing.
2.12 Things provided at the end of the service period for the Employer’s use

2.12.1 Equipment
None. 
The Contractor shall retain responsibility for all tools and handling equipment used during the service period. No transfer of ownership or continued use by the Employer is anticipated or required. 

2.12.2 Information and other things

At the end of service period, the Contractor shall provide the following to the Employer: 
· Finalised O&M manuals including updates and design enhancements

· A full set of data books for all supplied and refurbished pumps, including: 

· Test reports 

· Material certificates 

· NCRs and corrective actions 

· Engineering drawings and as-built documentation 

· Summary of training conducted and technology transfer documentation
· Status report on remaining spare inventory, with recommendations for future use or procurement
2.13 Management of work done by Task Order

A Task Order will be issued for tasks at hand as per descriptions form the Employer’s Representative who will be managing this Contract on behalf of the Employer.

3 Health and safety, the environment and quality assurance

3.1 Health and safety risk management

3.1.1. Health and safety risk management

Eskom Medupi Power Station’s responsibility and commitment is to ensure a safe working environment is in line with its Safety, Health, Environmental and Quality Policy, along with legislative obligations. The SHE Specification will be issued through Tender Bulletin, and it is compulsory for the appointed contractor to comply with the requirements of the SHE Specification
The Contractor will be required to comply with the following legal and other requirements throughout the duration of the contract:

· Occupational Health and Safety Act 85 of 1993

· Contract and Contractor OHS Management (32-726)

· Eskom Life Saving Rules

· Eskom OHS Specification

· Eskom SHEQ Induction

· COIDA Act

· Eskom Incident Management Procedure (32-95)

· Monthly Safety File Evaluation Checklist

3.1.2. Occupational Hygiene Programme

Occupational Hygiene Programme (OHP) are programme devoted to the recognition, evaluation and control of those environmental factors, arising in or from the workplace that may cause illness, injury, or discomfort. 
The main objective of the OHP is to help reduce the risk of hazardous exposures, ensure regulatory compliance and to improve working conditions. Appropriate occupational hygiene practices needs to be applied to the various departmental areas in accordance with the Occupational Health & Safety Act in order to fulfil this requirement.
The Occupational Hygiene Programme clearly defines and stipulates the responsibilities of all workplace parties involved in its development, administration and implementation of the program.

       Occupational Hygiene Programme within the workplace should be an integral part of the    

       Overall appointed contractor strategy for a healthy workplace. Occupational Health and safety 
       Legislation and other workplace policies or programs can provide a basis for a healthier 
       Workplace.
       The contractor must conduct the following Occupational Hygiene Survey during the first year   

       of the duration of the contract:

· Illumination Survey

· Noise Survey

· Indoor Air Quality Survey

· Ergonomic Surveys 

· Silica or Dust Survey
3.2 Environmental constraints and management

The Contract shall conduct all activities in a manner that ensures minimal environmental impact and complies with Eskom’s environmental management standards. 
The Contractor shall adhere to the environmental constraints outlines in the Medupi Power Station Environmental Requirements for Contractors and Suppliers, document 240-90508511. 

Key environmental constraints include, but not are not limited to: 

· Waste management: All waste materials generated during the refurbishment or packaging process must be handled, stored, and disposed of in accordance with Eskom and legal requirements. Hazardous waste (e.g., oil-contaminated materials) must be disposed of at a licensed facility. 
· Oil handling and spill prevention: Proper procedures must be followed to prevent leaks or spills of lubricating oil during disassembly, testing, or transport. Spill kits must be available, and spill incidents must be reported immediately. 

· Noise and emissions: The Contractor shall ensure that workshop operations (e.g., pressure testing, machining) comply with applicable noise and emission regulations. 

· Transport and packaging: All components delivered to or from Medupi must be adequately sealed and protected to prevent environmental contamination or deterioration. 

Environmental Management Plan (EMP):

· The Contractor shall develop and submit a site-specific EMP that includes:

· Risk assessment of activities 

· Control measures 

· Emergency response plans 

· Compliance monitoring mechanisms 

· The EMP must be submitted for Employer acceptance at least 1 week prior to any on-site activities. 

Failure to comply with the above may result in penalties or suspension of work. 
The Contractor shall comply with the environmental criteria and constraints stated in Medupi Power Station Environmental Requirements for Contractors and Suppliers 240-90508511_ 
3.3 Quality assurance requirements

The Contractor shall implement and maintain a Quality Management System that meets or exceeds the requirements of ISO 9001:2015.
All quality assurance activities shall comply with the Eskom Supplier Quality Management Specification (240-105658000) and include the following minimum requirements:  

Quality Plan and Work Procedures: 

· Submission of a Quality Control Plan (QCP) and/or Inspection and Test Plan (ITP) for each major activity (supply, refurbishment, testing). 

· The QCP/ITP must: 

· Identify hold points and witness points, including:

· Initial acceptance of QCP 

· Final inspection and pressure testing 

· Review of NDT reports 

· Material certificate conformity checks 

· PMA and NCR reviews (if applicable)

· Final data book submission 

· Be submitted to the Employer for acceptance at least 1 week before work starts. 

Document Control and Submission: 

· The Contractor shall maintain a traceable record of all QA documentation including: 
· Material certificates 

· NDT results 

· NCRs and corrective actions 

· Conformance certificates 

· Signed checklists and inspection records

· All quality documentation shall be compiled into a final data book for each pump or batch of pumps delivered/refurbished and submitted to the Employer for review and record-keeping. 

Work Outside Affected Property: 

· For off-site activities (e.g., at the Contractor’s workshop), the Contractor must notify the Employer at least four (4) weeks in advance of any required inspections or witness points.  

· Random audits may be conducted by the Employer or its appointed representative to verify quality and conformance. 

Failure to comply with the quality requirements may result in rejection of the goods or services and withholding of payment until corrective actions are completed. 
4 Procurement
Local Procurement Content 

“Local Procurement Content” refers to value added in South Africa by South African resources. Where a single contract involves a combination of local and imported goods and/or services, the tender response must be separated into its components as per the Price Schedule included with the tender documents. Local procurement content is total spending minus the imported component. 

Tenderers are required to submit their proposals in the table below.

	Local Procurement Content 
	Eskom target
	Tenderer Proposal

	
	100%
	


Jobs. Tenderers are required to submit proposals for the type and number of jobs that will be created and retained in South Africa as a direct result of being awarded a contract.
	Type of Jobs to be created
	Number of Jobs to be created

	
	


	Type of Jobs to be retained
	Number of Jobs to be retained

	
	


4.1 People

4.1.1 Minimum requirements of people employed
Before starting work on a Task the Contractor shall provide to the Service Manager for their acceptance outline details of persons to be employed for work in the Task, to the extent that the Service Manager has requested in the Task Order.

The Contractor shall not commence work in a Target Order until such a person to be employed have been accepted by the Service Manager. The Service Manager may not accept persons who are in their opinion not adequately qualified or experienced to undertake the work in the task.

The Contractor shall provide for the Service Manager’s acceptance similar details for new or replacement persons employed after work in the Task Order has commenced.

Notwithstanding this requirement, the Service Manager or SSM may at any time instruct the Contractor to provide the full Curriculum Vitae of a person to be employed if they consider the outline details to be insufficient.

For the purpose of this contract, persons employed for work in the Task Order shall include any person, whether under contract of employment to the Contractor, Subcontractor or others.

Skills development

Tenderers are required to submit proposals in a table below for developing the skills of unemployed candidates in the country. Skills development is intended to address Eskom’s core, scarce and critical skills and the scarce and critical skills.  These skills are also included in a 2020 list of occupations in high demand as stipulated in the Government Gazette 43937.   Candidates shall be from all provinces in the country, and their composition shall be representative of the population demographics of South Africa
	Skill type / Occupation
	Eskom target
	Proposed Number of Candidates

	
	
	

	
	
	


The process of developing these skills shall involve the participation by tenderers directly and through their supply network.  In certain cases, the SETA’s accredited training providers can be approached to participate in developing critical and scarce skills.

4.1.2 BBBEE and preferencing scheme

The Contractor shall ensure that it maintains the B-BBEE’s level of contribution with which it was awarded a contract. Should the Contractor for any reason, including a change in legislation, lose its status then it will be given 184 days to comply.

4.1.3 Accelerated Shared Growth Initiative – South Africa (ASGI-SA) 

The Contractor complies with and fulfils the Contractor’s obligations in respect of the Accelerated and Shared Growth Initiative - South Africa in accordance with and as provided for in the Contractor’s ASGI-SA Compliance Schedule stated below

.
[Insert the agreed ASGI-SA Compliance Schedule here]

The Contractor shall keep accurate records and provide the Service Manager with reports on the Contractor’s actual delivery against the above stated ASGI-SA criteria.   [Elaborate on access to and format of records and frequency of submission etc.]

The Contractor’s failure to comply with his ASGI-SA obligations constitutes substantial failure on the part of the Contractor to comply with his obligations under this contract.
4.2 Subcontracting
4.2.1 Preferred subcontractors

Only sub- Contractors authorized by the Employer will carry out work on the equipment in terms of this contract.

a)
Preferred subcontractors

b)
If the Contractor subcontracts work, he is responsible for providing the Service as per the contract.

c)
This implies that the Subcontractor’s employees and equipment is the Contractor’s.

d)
Limitations on subcontracting

i.
The Contractor submits in writing the name of each propose Subcontractors with certificates and registration documentation to the Employers Representative for acceptance/ rejection.

ii.
The Contractor does not appoint a proposed Subcontractor until the Employers Representative has accepted him.

e)
 Possession, Control of Equipment

f)
 The contractor will not assume possession or control of any part of the equipment all of                    which shall remain exclusively the property of the Employer.

4.2.2 Subcontract documentation, and assessment of subcontract tenders

As per SDL&I strategy

4.2.3 Limitations on subcontracting

As per SDL&I strategy

4.2.4 Attendance on subcontractors

As per SDL&I strategy

4.3 Plant and Materials

4.3.1 Specifications
All Plant and Materials supplied under this contract must meet the following criteria: 
· Be fit for purpose, compliant with OEM specifications, and suitable for integration with Medupi Power Station’s existing hydraulic systems. 
· Conform to Eskom’s technical and procurement standards, including: 

· SABS ISO 9000 for quality assurance 

· ISO 20816-1:2016 for vibration levels 

· Eskom Drawing Standard 240-86973501

· Eskom Corrosion Protection Standard 240-1063656933

· Turbine Centreline Material Procurement Standard 240-95144948

· The Contractor shall ensure all materials are certified in accordance with EN 10204 Type 3.1 or 3.2, with traceability to heat numbers. 

4.3.2 Correction of defects

· Any Plant or Materials found to be defective before or after delivery shall be:
· Replaced with new OEM-compliant items, or 

· Repaired only if repair restores full compliance with specifications and is approved by the Employer. 

· No unauthorised substitutions are allowed without written approval from the Employer. 

· All defective components must be returned with a Non-Conformance Report (NCR) and detailed repair documentation. 

4.3.3 Contractor’s procurement of Plant and Materials

The Contractor is responsible for the complete procurement cycle including: 
· Placing orders with approved OEMs or equivalent 

· Expediting, tracking, and documenting orders 

· Ensuring safe packaging and preservation for storage up to 10 years 

· Delivery to Medupi Power Station as per the approved schedule 

· Submission of vendor warranties in favour of the Employer 

· Providing a vendor data pack for each component including datasheets, certification, material traceability, and performance curves
4.3.4 Tests and inspections before delivery

· All pumps and major components shall undergo: 
· Functional testing at 4.0 MPa 

· Vibration testing (ISO 20816-1 compliance)

· NDT as per Eskom standard 240-83540088

· The Employer reserves the right to witness FAT (Factory Acceptance Tests) and to appoint third-party inspectors, including for overseas inspections. 
4.3.5 Plant & Materials provided “free issue” by the Employer
None
4.3.6 Cataloguing requirements by the Contractor
If applicable, the Contractor shall catalogue all supplied items per Procurement Instruction Number 1 of 2018 – Incorporating Cataloguing into the Procurement Environment (240-1289988974). Catalogue information shall include: 
· KKS numbers 

· Part descriptions and OEM part numbers 

· Material and serial numbers 

· Storage conditions and shelf-life information 
5 Working on the Affected Property

This part of the Service Information addresses constraints, facilities, services and rules applicable to the Contractor whilst he is doing work on the Affected Property. 

5.1 Employer’s site entry and security control, permits, and site regulations
· All personnel must comply with Medupi Power Station’s security protocols, including: 
· Pre-clearance and induction 

· Valid ID/passport and PPE compliance 

· Site-specific permits (e.g., Hot Work, Confined Space)

· Movement is restricted to designated areas and roads; barricades must be erected where required. 

· Contractors must be aware of and comply with all site regulations and emergency procedures. 
5.2 People restrictions, hours of work, conduct and records

· Standard working hours: Monday to Friday, 07:00 – 16:15
· Work outside these hours requires prior approval. 

· Contractor shall maintain a daily attendance register for all staff and subcontractors. 

· These records must be available to the Service Manager upon request and will be used for performance evaluation and event investigation. 

5.3 Health and safety facilities on the Affected Property

· First Aid Stations and emergency response facilities are located at designated areas on site. 
· Emergency contacts, evacuation routes, and muster points will be provided during induction. 

· All personnel must undergo a Medupi HSE induction prior to accessing the site. 

5.4 Environmental controls, fauna & flora

The Contractor shall comply with Medupi Power station Environmental requirements for Contractors and Suppliers Doc 240-90508511.
5.5 Cooperating with and obtaining acceptance of Others

· The Contractor must cooperate with Other contractors, Eskom departments (e.g., Operations, Maintenance), and statutory bodies such as NERSA or SANAS if inspections are required. 

· All coordination with external inspection agencies and regulatory authorities must be documented and made available to the Employer. 
5.6 Records of Contractor’s Equipment

· The Contractor shall maintain a register of all equipment brought onto the Affected Property, including: 
· Ownership (owned vs. hired)

· Certification (load testing, calibration)

· Deployment and removal dates 

· Special lifts, rigs, or cranes must be approved by the Service Manager and removed once work is completed. 
5.7 Equipment provided by the Employer
None.
5.8 Site services and facilities
5.8.1 Provided by the Employer
· The Employer shall provide the following at designated hookup points: 
· Electrical power 

· Potable water 

· Ablutions and wash facilities 

· General lighting and fire protection 

· Hookups must be approved and performed under the supervision of the Employer. 

All other services and facilities required by the Contractor shall be provided by the Contractor. 
5.8.2 Provided by the Contractor
· The Contractor shall provide: 
· Temporary site accommodation or rest area if needed

· Secure tool and material storage 

· Vehicles for personnel and material transport 

· Office equipment (laptops, Wi-Fi, printers) for its own team

· All temporary facilities must be removed and the site restored upon completion of the contract. 
5.9 Control of noise, dust, water and waste 

· The Contractor shall: 
· Minimise dust and noise during packaging, transport, or offloading

· Prevent oil or water leaks 

· Dispose of waste in accordance with the Medupi Environmental Standard 

· Water use for cleaning must not be discharged into drains without approval. 
5.10 Hook ups to existing works

· No modification, tie-in, or hookup to existing systems or infrastructure is permitted unless authorised in writing by the Employer. 
· All hookup work must follow documented change control procedures. 
5.11 Tests and inspections

5.11.1 Description of tests and inspections
· The following inspection/tests will be conducted by the Contractor with potential witness by the Employer: 
· Disassembly and dimensional inspection 
· NDT (visual, ultrasonic, magnetic particle) as per Eskom standard 240-83540088

· Pressure testing 

· Vibration testing in accordance with ISO 20816-1:2016

· FAT and SAT as applicable

5.11.2 Materials facilities and samples for tests and inspections 
· The Contractor shall provide: 
· All materials, test rigs, calibrated instruments, and access for inspections

· Sample components or test coupons if required 

· The Employer may provide: 

· Observation personnel 

· Access to site-based test areas (subject to approval)
6 List of drawings

6.1 Drawings issued by the Employer
This is the list of drawings issued by the Employer at or before the Contract Date and which apply to this contract.

N/A
� This total is required by the Employer for budgeting purposes only.  Actual amounts due will be assessed in terms of the conditions of contract.


� Available from Engineering Contract Strategies Tel 011 803 3008 Fax 086 539 1902 � HYPERLINK "http://www.ecs.co.za" �www.ecs.co.za� 


� Available from Engineering Contract Strategies Tel 011 803 3008 Fax 086 5391902 or � HYPERLINK "http://www.ecs.co.za" �www.ecs.co.za� 







Contract
- ii -
TSC3 Cover pages


_1812866309.unknown

_1812866310.unknown

_1812866307.unknown

_1812866308.unknown

_1812866306.unknown

_1812866305.unknown

