Eskom Holdings SOC Ltd

Contract number _____________

project & contract title




Part 3: Scope of Work

	Document reference
	Title
	No of pages

	
	This cover page
	1

	C3.1
	Employer’s Works Information
	

	C3.2
	Contractor’s Works Information

(insert at award stage or delete if not applicable)
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	Total number of pages
	


C3.1: Employer’s works Information

Contents

When the document is complete, insert a ‘Table of Contents’.  To do this go to:  Insert, → Reference, → Index and tables → Table of Contents.  Three levels and the title (but not the subtitle) may be shown if the formats used in this template are retained.   
1Part 3: Scope of Work

C3.1: Employer’s works Information
2
1
Description of the works
6
1.1
Executive overview
6
1.2
Employer’s objectives and purpose of the works
7
1.3
Definition
7
1.4
Interpretation and terminology
7
2
Management and start up.
8
2.1
Management meetings
8
2.2
Documentation control
9
2.3
Health and safety risk management
9
2.4
Environmental constraints and management
9
2.5
Quality assurance requirements
9
2.6
Programming constraints
10
2.7
Contractor’s management, supervision and key people
10
2.8
Invoicing and payment
10
2.9
Insurance provided by the Employer
11
2.10
Contract change management
11
2.11
Provision of bonds and guarantees
11
2.12
Records of Defined Cost, payments & assessments of compensation events to be kept by the Contractor
11
2.13
Training workshops and technology transfer
11
3
Engineering and the Contractor’s design
12
1.1
Employer’s design
12
3.1.1
Emulsifier System
12
3.1.2
The emulsifier main piping
12
3.1.3
The emulsifier pumping system specification
12
3.2
Parts of the works which the Contractor is to design
13
3.2.1
Implement new operating philosophy for the fire pumping system
13
3.2.2
Install control and instrumentation system
15
3.2.3
Electrical pump house.
16
3.2.4
Electrical installations
17
3.2.5
Increment of fire protection mains to respective 200mm and 250mm nominal bores
18
3.2.6
Water Storage Tank
19
3.3
Procedure for submission and acceptance of Contractor’s design
20
3.4
Other requirements of the Contractor’s design
21
3.4.1
Physical Characteristics Requirements
21
3.4.2
Fire Protection
21
3.4.3
Corrosion Protection
21
3.4.4
Testing and Commissioning
21
3.5
Use of Contractor’s design
22
3.6
Design of Equipment
22
3.7
Equipment required to be included in the works
22
3.8
As-built drawings, operating manuals and maintenance schedules
22
3.8.1
TECHNICAL, OPERATING AND MAINTENANCE MANUALS
23
4
Procurement
25
4.1
People
25
4.1.1
Minimum requirements of people employed on the Site
25
4.1.2
BBBEE and preferencing scheme
25
4.1.3
Accelerated Shared Growth Initiative – South Africa (ASGI-SA)
25
4.2
Subcontracting
25
4.2.1
Preferred subcontractors
25
4.2.2
Subcontract documentation, and assessment of subcontract tenders
25
4.2.3
Limitations on subcontracting
25
4.2.4
Attendance on subcontractors
25
4.3
Plant and Materials
26
4.3.1
Quality
26
4.3.2
Plant & Materials provided “free issue” by the Employer
26
4.3.3
Contractor’s procurement of Plant and Materials
26
4.3.4
Spares and consumables
26
4.4
Tests and inspections before delivery
27
4.5
Marking Plant and Materials outside the Working Areas
27
4.6
Contractor’s Equipment (including temporary works).
27
4.7
Cataloguing requirements by the Contractor
27
The Contractor to provide a list of all material and component used in the project with full description or specification.
27
5
Construction
28
5.1
Temporary works, Site services & construction constraints
28
5.1.1
Employer’s Site entry and security control, permits, and Site regulations
28
5.1.2
Restrictions to access on Site, roads, walkways and barricades
28
5.1.3
People restrictions on Site; hours of work, conduct and records
28
5.1.4
Health and safety facilities on Site
28
5.1.5
Environmental controls, fauna & flora, dealing with objects of historical interest
28
5.1.6
Title to materials from demolition and excavation
28
5.1.7
Cooperating with and obtaining acceptance of Others
29
5.1.8
Publicity and progress photographs
29
5.1.9
Contractor’s Equipment
29
5.1.10
Equipment provided by the Employer
29
5.1.11
Site services and facilities
29
5.1.12
Roads
30
5.1.13
.First Aid and Fire Fighting
30
5.1.14
Sanitary Facilities
30
5.1.15
Facilities provided by the Contractor
30
1.1.1
Lay Down Areas
30
5.1.16
Security
30
5.1.17
Giving Notice of Work to be Covered Up
31
5.1.18
Existing premises, inspection of adjoining properties and checking work of Others
31
5.1.19
Survey control and setting out of the works
31
5.1.20
Excavations and associated water control
31
5.1.21
Underground services, other existing services, cable and pipe trenches and covers
31
5.1.22
Control of noise, dust, water and waste
31
5.1.23
Sequences of construction or installation
31
5.1.24
Giving notice of work to be covered up
31
5.1.25
Hook ups to existing works
32
5.2
Completion, testing, commissioning and correction of Defects
32
5.2.1
Work to be done by the Completion Date
32
5.2.2
Use of the works before Completion has been certified
32
5.2.3
Materials facilities and samples for tests and inspections
32
5.2.4
Commissioning
32
5.2.5
Start-up procedures required to put the works into operation
32
5.2.6
Take over procedures
32
5.2.7
Access given by the Employer for correction of Defects
32
5.2.8
Performance tests after Completion
32
5.2.9
Training and technology transfer
33
5.2.10
Operational maintenance after Completion
33
6
Plant and Materials standards and workmanship
34
6.1
Investigation, survey and Site clearance
34
6.2
Building works
34
6.3
Civil engineering and structural works
34
6.4
Restricted Working Conditions
34
6.5
Electrical & mechanical engineering works
34
6.6
Process control and IT works
35
6.6.1
Document Management
35
6.6.2
Document Identification
35
6.6.3
Document Submission
35
6.6.4
Email Subject
35
6.6.5
Engineering Change Management
35
6.6.6
General Requirement
36
6.6.7
Configuration Management
36
6.6.8
Change Management
36
6.6.9
Design Review Documentation
36
7
Normative/Informative References
37
7.1
Normative
37
7.2
Informative
38
7.3
List of drawings
39
7.3.1
Drawings issued by the Employer
39
C3.2
Contractor’s Works Information
40


1 Description of the works
1.1 Executive overview 
Hendrina Power Station (HPS) is located within the Middleburg Magisterial District, approximately 35 km south-east of the town Middleburg and on the south-western border of the town Pullenshope. The Power Station is located in the south of Optimum Colliery Mine

At HPS the water storage and pumping redundancy requirements for the worst case scenario was not provided.  The requirements have been determined and are documented in the HPS Worst Case Scenario report. The report is based on the requirements as stated in the Employer’s Fire Protection and Life Safety Design Standard [2].

“5.10.1 Water Supplies

The water supply or supplies for fixed fire protection installations shall as a minimum be based on the fire scenario with the largest designed fire water demand taken from activation of the fixed suppression systems, plus the maximum hose stream demand of not less than two (2) hydrants for a minimum duration of two (2) hours.

5.10.5 Fire Water Pumps

The fire water pumps are required to meet the fire flow requirements determined by the largest fire area demand. A sufficient number of pumps shall be provided to ensure 100% redundancy in fire water pump capacity.

To meet the abovementioned requirement, the detailed technical specification for HPS’s fire protection system upgrade is initiated to design, manufacture, procure, supply, remove, replace, install, test decommission old system and commission new system. The scope incorporates the following i.e.
1. Implement new operating philosophy for the fire pumping system. 

a. Replace 2 engines with controller and ancillary equipment. For detailed requirements see section 3.2.1.1
b. Install 2 pumping set of electrical driven fire water pumps equivalent the one situated in the pump house. For detailed requirement see section 3.2.1.2
c. Install a 300ℓ/min jockey pump equivalent to 10 hose reels streams. For detailed requirements see section 3.2.1.3
2. Install control and instrumentation. For detailed requirements see 3.2.2
3. Electrical pumps location. For detailed requirement see section 3.2.3
a. Option 1 – Extend existing pump house 

b. Option 2 - Containerise pump house

c. Option 3 – Erect a separate pump house

4. Electrical installations. For detailed requirement see section 3.2.4
5. Upgrade fire protection mains to respective 200mm and 250mm nominal bores. For detailed requirement see section for detailed requirement see section 3.2.5. 

6. Water storage tank. For detailed requirement see section 3.2.6
a. Option 1 - Refurbish existing water storage tank 

b. Option2 – Provide at least 740m3 new water storage tank.
Furthermore the mechanical scope will interface with the following disciplines: 

· Civil i.e. civil structure for pipe supports, refurbishment of steel storage panel tank and pump house. 

· Electrical i.e. new electrical supply to electrical and diesel driven pumps and pump house.

C&I i.e. an interface to existing fire alarm system at SOR and new one at Operator’s Office to flag the status of emulsifier pumping system

For further details pertain to affected disciplines is summarised below in table 1

	Item
	Plant/System Change
	Change Description
	Affected Disciplines

	1
	Emulsifier System Fire Water Supply System -which includes water pumping system, piping and water storage tank
	Worst case fire scenario identified the requirements for the water tank, pumping system and fire water piping.
	· Mechanical (LPS)

· C&I

· Civil

· Electrical


Table 1: Detailed summary of affect disciplines

1.2 Employer’s objectives and purpose of the works
The purpose of this technical specification is to describe technical requirements to procure the service of the construction contractor to design, manufacture, supply, install, replace, remove and commission fire protection upgrade to address worst case fire scenario.

1.3 Definition

	Definition
	Description

	System 
	An integrated set of constituent pieces that are combined in an operational or support environment to accomplish a defined objective. These pieces include people, hardware, software, firmware, information, procedures, facilities, services and services and other support facets.

	Fire pump 
	A device that provides the required water flow and pressure for a fire protection system. The fire pump unit itself consists of a pump, a drive, a driver coupling connecting the two, and a base plate.

	Pump set
	A unit comprised of the driver, pump, control panel and ancillary equipment

	Stakeholder
	Is considered to be anyone that has an interest in the outcome of the project.

	Approve 
	The functional responsible person determines if the document is fit for purpose and approves the document content and therefore takes responsibility and accountability for the document content. 

	Authorise 
	The document authoriser authorises the release and application of the document and is accountable for document implementation. 

	Risk 
	Risk is a function of both the likelihood of a specific hazard being realised and the consequence of that realisation. 

	Unit 
	It comprised of boiler, turbine and generator set and all its dedicated auxiliaries 


1.4 Interpretation and terminology
The following abbreviations are used in this Works Information:

	Abbreviation
	Meaning given to the abbreviation

	ASIB
	Automatic Sprinkler Inspection Bureau

	C&I
	Control and Instrumentation

	FPC
	Fire Protection Contractor

	FPS
	Fire Protection System

	ITP
	Inspection and Testing Plan

	LPS
	Low Pressure Services

	N/A
	Not applicable

	NEC
	New Engineering Contracts

	OHSA
	Occupational Health and Safety Act

	HPS
	Hendrina Power Station

	SAICE
	South African Institute of Civil Engineering

	P&ID
	Piping and Instrumentation Diagram

	PSR
	Plant Safety Regulations

	SANS
	South African National Standard

	SRD
	Stakeholder Requirements Definition

	Symbols
	Description

	V
	Volt

	m3
	Cubic meter

	K
	kilo

	ℓ
	litre

	min
	minutes

	W
	Watt

	M
	meter

	Pa
	Pascal


2 Management and start up.

2.1 Management meetings

Regular meetings of a general nature may be convened and chaired by the Project Manager as follows:

	Title and purpose
	Approximate time & interval
	Location
	Attendance by:

	Overall contract progress and feedback
	Every second week on a day and time agreed upon by Parties. This is subject to change depending on the requirement.
	To be confirmed by the Project Manager 
	Contractor/s, Supervisor, Project Manager , System Engineer, and Others

	Early Warning (Risk reduction) meeting
	As and when required
	To be confirmed by the Project Manager 
	Contractor/s, Supervisor, Project Manager , System Engineer, and Others

	Kick-off meeting
	Third working day after official contract is placed.
	To be confirmed by the Project Manager 
	Contractor/s, Supervisor, Project Manager , System Engineer, and Others

	Interfacing meetings
	As and when required
	To be confirmed by the Project Manager 
	Contractor/s, Supervisor, Project Manager , System Engineer, and Others

	Risk register and compensation events
	As and when required
	To be confirmed by the Project Manager 
	Contractor/s, Supervisor, Project Manager , System Engineer, and Others


Meetings of a specialist nature may be convened as specified elsewhere in this Works Information or if not so specified by persons and at times and locations to suit the Parties, the nature and the progress of the works.  Records of these meetings shall be submitted to the Project Manager by the person convening the meeting within five days of the meeting.  
All meetings shall be recorded using minutes or a register prepared and circulated by the person who convened the meeting.   Such minutes or register shall not be used for the purpose of confirming actions or instructions under the contract as these shall be done separately by the person identified in the conditions of contract to carry out such actions or instructions.  

2.2 Documentation control

All contractual communications will be in pdf format or forms attached to emails and not as a message in the email itself. Letters are typed and signed by the Contractor, and delivered either in hardcopy or e-mailed to the Service Manager. 

The routing of all written communications to be between the Project Manager and the Contractor only. Any agreements between the Contractor and any other person representing the Employer which has not been routed via the Project Manager to be unacceptable and invalid.

Any instructions written or verbal resulting in any changes to the duration, quality, and cost of the project to only be received from the Project Manager.

All reports are compiled in Word format, in English, and submitted electronically as pdf to Service Manager. Hardcopy reports (which are deemed originals) are counter signed by the Contractor’s line of authority for authenticity and quality verification after finalisation for purposes of record keeping.

Copies of all documents relating to the works are retained by the Contractor in hardcopy format as well as electronic format (pdf format for signed documents) for 5 years.

2.3 Health and safety risk management
The Contractor is to:

· Comply with the latest revision of Eskom Hendrina Power Station’s Health, Safety and Environmental Specifications for Principal Contractor’s requirements as mentioned in Section 8

· Perform the works in a safe manner and comply with the Employer’s Safety, Health and Environmental specifications for Principal Contractors (HSPHO/058).

· Maintain a protected environment around the work areas, and control access to the Generator relay room, for the full duration of the works.

· Provide a First Aid service to employees. In the event of serious injury, the Employer’s Medical centre and facilities will be available. The Employer recovers the cost incurred for the use of facilities from the contractor.

· Provide a safety file and keep the file up to date for the duration of the Contract

· Do induction courses (given on Mondays, Wednesdays and Fridays at 09:00)

· Supply daily updated copies of: Toolbox Talks, Job Observations and Job risk Assessments

· NB: No personnel may be transported on any open vehicles.  Personnel may only travel in a vehicle with SABS seating and safety belts.

2.4 Environmental constraints and management
All personnel involved in the implementation of the project are to abide by the SHE requirements of Hendrina PS. These include all the relevant legislations, applicable licences and permits, and environmental procedures and shall be adhered to at all times. All the documents can be obtained from the environmental department.

•
Assessment of impact on operational conditions affecting discharge to atmosphere

•
Assessment of impact on operational conditions affecting waste removal and processing

•
Assessment of impact of accidental release of pollutants (oils, gases, waste water, etc.)

2.5 Quality assurance requirements

Contractor conforms to the following Quality Management systems:

· Quality requirements as per ISO 9001:2015

· QM 58 and Hendrina Power Station HSSPPA 006 “ Quality requirements for quality related items”

· Contractor provides a detailed Quality Control Plan for acceptance within 3 working days of the Contract Date identifying how use of labour, machinery and equipment suffice to successfully execute the required services according to the methodology provided by the Contractor. Ultimately the Quality control plan shall be approved by the Project Manager.
· Quality control plan is compatible to the site conditions and project constraints. This aligns with the Employer’s Quality criteria and adheres to the Employer’s Safety, Health, and Environmental requirements.

Contractor compiles QIP according to Hendrina Power Station’s standard QIP format (reference no. HSPPA/014).QIP stipulates hold points; witness points and verification points approved and documented before the works commence
2.6 Programming constraints 

Contractor provides a hardcopy and an electronic copy of a pdf Gantt chart programme, identifying how the execution of the works is achieved within the specified project duration.

Programme summarizes the major work activities, estimated durations, and relationships to the other activities of the project. This includes demonstrating how quickly labour, machinery and equipment to execute the required works will arrive and be secured on site. Programme is approved by the Contract Manager before the required works commences.

Programme submitted by the Contractor shall be compatible with the site conditions and constraints of the project.

2.7 Contractor’s management, supervision and key people

Contractor submits an organogram to the Project Manager with key personnel. Contractor appoints qualified and competent Site manager, supervisor, skilled people and safety officer.  Resource allocation abides to their respective function. These resources are present for the duration of the works. Daily site register are signed with all the resources specified.

Contractor provides the key people required to successfully provide the works. The allocation of the key people is clearly reflected on the activity programme, with the required activities to execute and duration stipulated. During the execution of the works, registers or time sheets of the Contractor’s employees is kept for contract records.

Management as indicated on the Contractor’s organogram avail themselves immediately when required to resolve matters that may impact on the accomplishment of the works.

Reference is to be made to the technical evaluation criteria for further requirements documenting the control measures to mitigate technical risks.

2.8 Invoicing and payment

Within one week of receiving a payment certificate from the Project Manager in terms of core clause 51.1, the Contractor provides the Employer with a tax invoice showing the amount due for payment equal to that stated in the Project Manager’s payment certificate.  

The Contractor shall address the tax invoice to Eskom Holdings SOC Ltd and include on each invoice the following information:

· Name and address of the Contractor and the Project Manager; 

· The contract number and title;

· Contractor’s VAT registration number;

· The Employer’s VAT registration number 4740101508;

· Description of service provided for each item invoiced based on the Price List;

· Total amount invoiced excluding VAT, the VAT and the invoiced amount including VAT;

· (add other as required)

Add procedures for invoice submission and payment (e. g. electronic payment instructions)

2.9 Insurance provided by the Employer
As per ECC3 Core Clause 87.1.
2.10 Contract change management 

Contractor provides daily site register/diaries of planned working versus work completed to the Service Manager. Following information is stipulated on the daily site diary:

· Task based risk assessments and Toolbox Talks

· Signed time sheets

· Weather conditions

· Site conditions

· Locations where work was being undertaken together with resources being utilised

· Any delays noted (for whatever reason), any notification by people employed by the Contractor regarding difficulties encountered

· Complaints by third parties

· Any work done by Others at the site

No standing time claims will be accepted without relevant proof of presence and activity in the form of these records and the early warning process to be followed

Contractor provides proof of expenses to the Employer in the form of a hardcopy as well as a soft copy.

2.11 Provision of bonds and guarantees

The form in which a bond or guarantee required by the conditions of contract (if any) is to be provided by the Contractor is given in Part 1 Agreements and Contract Data, document C1.3, Sureties.  
The Employer may withhold payment of amounts due to the Contractor until the bond or guarantee required in terms of this contract has been received and accepted by the person notified to the Contractor by the Project Manager to receive and accept such bond or guarantee.  Such withholding of payment due to the Contractor does not affect the Employer’s right to termination stated in this contract. 
2.12 Records of Defined Cost, payments & assessments of compensation events to be kept by the Contractor
Not Applicable to this contract
2.13 Training workshops and technology transfer

The contractor appoints one person to attend Authorised Supervisors and one person to attend Responsible Person Plant Safety Regulation Course. No work will commence without an Accredited Authorised Supervisor and Authorised Responsible Person on site.
3 Engineering and the Contractor’s design

1.1 Employer’s design

3.1.1 Emulsifier System

There are two diesel emulsifier pumps each rated for 3666.67ℓ/min at 1200kPa and both taking suction from the 480m3 storage tank with suction head of ±50kPa. The diesel pumps discharge at the common manifold of 200mm bore. 

To maintain the emulsifier system pressure at 1000kPa, a jockey pump sized for 105ℓ/min at 1100kPa is installed at system discharge manifold. To compensate for minor system pressure loses, the jockey pump will cut-in and cut-out between ±830kPa and ±1000kPa respectively. 

Should the pressure drop exceeds makeup capability of the jockey pump, then emulsifier pump 1 will cut-in at ±700 kPa. A further drop in pressure to ±550kPa will bring in emulsifier pump 2. These diesel pumps are automated but can be operated manually

3.1.2 The emulsifier main piping

The emulsifier piping mains changes their sizes from 200mm to 150mm and 100 mm diameters respectively along units 1 to 10 boiler and turbine ring mains. The fixed fire protection for unit transformers, generator transformers, turbine transformers, standby transformers and distribution transformers taps from the ring mains. Furthermore fixed fire protection for units’ 1-10 boilers, main oil tanks, clean and used oil tanks, diesel generators, boiler feed pumps, cable tunnel and cable spread also taps off water supply from the same ring mains. 

3.1.3 The emulsifier pumping system specification

The below specification provides details of existing emulsifier diesel pumps, electrical jockey pump, water storage tank and piping for mains. Refer to table 2. 

	EMULSIFIER DIESEL PUMP 1 & 2
	JOCKEY PUMP

	KKS Number
	00SGA41 and 00SGA40
	00SGA41

	Pump Name
	SPP Pump HSR2B6
	Grandfos CR3-17 AFGJ-A-E-HUBE

	Pump Head
	1200kPa
	1100kPa

	Flow Rate
	220m3/h or 3666.67ℓ/min
	6.3m3/h – 105 ℓ/min recommended 

	Rated Speed
	1450rpm
	

	Stage
	2 Stage (double suction)
	Multiple stage

	Driver
	Diesel Engine
	Electrical Motor

	Engine Model
	Deutz Diesel Power BF12L413F
	

	Rated Power
	320kW
	

	Water Storage tank
	480m3

	Mains Pipe Sizes
	100mm, 150mm, 200mm


Table 2: Emulsifier Pumping System Specification

3.1.3.1 Emulsifier diesel pumps curve

Figure 1 provides pump curve for existing emulsifier diesel pumps 1 and 2. 

[image: image1.png]200

180

6o

140

120

100

Head - m

Power - kW
g 8 8

o

—— Minimum Continuous Safe Flow (MCSF)
[ Preferred operating region
445 mm 50 0
65
™ e 70 734
7 7 75
74 g
L Vs
- I~
SesTIT -
f s Y
~
| NPSHr
[—
| 2
0 50 100 150 200 250 300 350 400

Flow - m3/h

450




Figure 1: SPP pump curve (HSR2B6) for emulsifier diesel pump 1 and 2
3.2 Parts of the works which the Contractor is to design

3.2.1 Implement new operating philosophy for the fire pumping system

The Contractor designs, manufactures, supplies, installs and commissions emulsifier system with the following operating philosophy.

· The jockey pump, the electrical driven fire pumps and diesel driven fire pumps will be on auto-starting mode during normal operating conditions.

· The jockey pump will cut in automatically through a pressure switch when the fire system pressure drops to 1 000kPa and cut out automatically when the system pressure reaches pump churning pressure of 1 200kPa. A jockey pump running warning alarm will be sent to the control room / SOR and Coal Plant Shift Supervisor’s Office. 

· The first electrical driven fire pump (primary pump) will cut in automatically through a pressure switch when the fire system pressure drops to 800kPa. A fire pump running fire alarm will be sent to the Control Room / SOR and Coal Plant Shift Supervisor’s Office.

· The second electrical driven fire pump (secondary pump) will cut in automatically through a pressure switch when the fire system pressure drops to 650kPa below the cut in pressure of the electrical driven primary pump. A fire pump running warning alarm will be sent to the Control Room / SOR and Coal Plant Shift Supervisor’s Office.

· The first diesel driven fire pump will start automatically through a pressure switch when the fire system pressure drops to 500kPa below the cut in pressure of the electrical driven secondary pump. A fire pump running fire alarm will be sent to the Control Room / SOR and Coal Plant Shift Supervisor’s Office.

· The second diesel driven fire pump will cut in automatically through a pressure switch when the system pressure drops further to 350kPa below the cut in pressure of the first diesel driven fire pump. A fire pump running fire alarm will be sent to the Control Room / SOR and Coal Plant Shift Supervisor’s Office.

· Both diesel driven fire pumps through pressure switch will cut out automatically when the pressure through the system becomes stable at 1200kPa for almost 30 minutes.

The diesel driven fire pumps will automatically cut out when their diesel engine tanks level is almost empty i.e. before the pump sucks in air from the tank. Thus, the fire warning alarm will be sent via pressure switch to Control Room / SOR and Coal Plant Shift Supervisor’s Office. 

When pump failed to start, then then the fire warning alarm will be sent to the Control Room / SOR and Coal Plant Shift Supervisor’s office in order to manually start the pumps in case of emergency.

The below information details the scope requirements of the new fire water pumping system:

3.2.1.1 Replace 2 diesel engines with controller and ancillary equipment 

The Contractor designs, manufactures, supplies, installs, tests, and commissions equivalent diesel engines or driver with controller and all ancillary equipment. 

The Contractor supplies diesel engine with hour meters to monitor the running time and heating elements / heater plugs to improve cold starting.

The Contract shall supply equivalent diesel engines agreed upon with the Employer. Thus, the Contractor must obtain approval from the Employer. The existing diesel engines are obsolete and their specification is found in table 2. 

The Contractor designs, manufacture, supplies and installs baseplate to accommodate the recommended diesel engine and pump.

The Contractor shall install, couple, align and commission existing horizontal split casing pump, double suction, model HSR2B6 (BM06F) referred to in table 1.

The Contractor designs, manufacture, supplies, installs and commissions common manifold piping that will be connected to the pumps and the storage tank/s.

The Contractor conducts dynamometer testing of diesel engines for performance, exhaust emissions, surface temperatures and fuel consumption. 

The Contractor conducts site acceptance test to prove the functionality of the newly installed system.

3.2.1.2 Install 2 pumping sets of electrical driven fire water pump equivalent to the one situated in the pump house.

The Contractor designs, manufactures, supplies, installs, tests and commissions 2 (two) electrical driven pumps with driver and all ancillary equipment.

The Contractor shall install, couple, supply two horizontal split casing model HSR2B6 (BM06F) specification shown in table 2. In case of equivalent pumps to be supplied, then approval to be obtain from the Employer.
The Contractor designs, manufactures, supplies and installs baseplate to accommodate recommended electrical driver (motor) and pumps.

The Contractor shall supply, install, couple, align and commission horizontal split casing pump, double suction, model HSR2B6 (BM06F) as shown in table 2.

The Contractor designs, manufacture, supplies, installs and commissions common manifold piping that will be connected to the pumps and the storage tank/s.

3.2.1.3 Install 300ℓ/min jockey pump equivalent to 10 x hose reels streams. 

The Contractor designs, manufactures, supplies, installs, tests and commissions electrical jockey pump that will discharge at least 10 x hose reels streams equivalent to 300ℓ/min at churn pressure of at least 1200kPa. The jockey pump capacity must be larger than the existing pump shown in table 2. It must take suction from emulsifier storage tank with suction head of ±50kPa.

The Contractor designs, manufactures, supplies, installs and commissions piping that will connect to both water storage tank and discharge common manifold of the pumps.

The Contractor shall install sectional valve and union in such a manner to enable jockey pump and non-return valve along with other miscellaneous fittings accessible for repair or removal and replacement as per SANS 10287 [26] section 14.12

The Contractor shall supply centrifugal pump having:

· Design discharge pressure sufficient to maintain the fire protection system pressure of 1200kPa.
· The kilowatt rating sufficient to drive the jockey pump from no flow to maximum flow condition without overloading. 
3.2.2 Install control and instrumentation system

The Contractor designs, manufactures, supplies, installs, tests and commissions fire warning alarm system that will interface with the fire warning system at Control Room / SOR. In addition the fire warning alarm system shall be installed at Coal Plant Shift Supervisor’s office for emergency response purpose.

The Contractor shall install fire warning alarm in accordance with SANS 10287 [26] section 14.9 for annunciators for sprinkler pump room installations and section 14.11 for pump house remote alarm notification and data logger module at SOR. The Contractor shall install common fire alarm annunciator at the Coal Plant Supervisor’s Office as well.

For the mounting of field instruments and junction boxes, the Contractor ensures that these comply with Field Instrumentation standard [5] and Junction boxes and Cable Termination Standard [6].

If PLC has to be used, the Contractor must use Siemen made PLC for standardisation purpose. 

The Contractor provides the following warning alarms on respective panel of annunciator, jockey pump, electrical driven pumps and diesel driven pump as shown in table 3

	Panel Name
	Alarm input

	Panel 
	Maintenance mode switch

	Jockey controller panel 
	ALARM – Pump RUN

	Jockey controller panel 
	ALARM – Pump FAIL

	Electric motor driven pump controller panel 
	ALARM – Fire ALARM

	Electric motor driven pump controller panel 
	ALARM – Pump RUN

	Electric motor driven pump controller panel 
	ALARM – Mains FAIL

	Electric motor driven pump controller panel 
	ALARM – Control circuit FAIL

	Electric motor driven pump controller panel 
	ALARM – Pump FAIL

	Diesel engine driven pump controller panel 
	ALARM – Fire ALARM

	Diesel engine driven pump controller panel 
	ALARM – Pump RUN

	Diesel engine driven pump controller panel 
	ALARM – Pump FAIL

	Diesel engine driven pump controller panel 
	ALARM – Mains FAIL

	Diesel engine driven pump controller panel 
	ALARM – Control circuit FAIL

	Diesel engine driven pump controller panel 
	ALARM – Low oil pressure FAIL

	Diesel engine driven pump controller panel 
	ALARM – Battery charger FAIL

	Diesel engine driven pump controller panel 
	ALARM – Engine over temperature FAIL


Table 3: Alarm inputs are to be connected directly to the electric, diesel, jockey or annunciator panels.

3.2.3 Electrical pump house.

There are three options to choose from regarding electrical pumps location and these options are:

a. Option 1 – Extend existing pump house

b. Option 2 - Containerise pump house

c. Option 3 – Erect a separate pump house

The Contractor provides pricing for each options listed above and in his/her report shall include the all related requirements. 

The Contractor designs, manufactures, supplies, installs, tests, and commissions selected pump house to accommodate the new pumps pending approval of Employer and the outcomes of the geotechnical study.

The Contractor shall ensure that his / her designs and construction conforms to Eskom standards.  

The Contractor must ensure that his/her designs includes installation of a crawl beam above the pumps for maintenance purpose.  

The Contractor provides the following technical requirements in the designs: 

· A full Geotechnical survey. 

· Designs for pump bases and crawl beam support footings.

· Design of Earthworks based on Geotechnical study. 

· All access and drainage requirements as well as future maintenance requirements.

· Structural drawings as per Employer’s requirements i.e. Engineering Drawing Standard: Common Requirements [27]. Furthermore all designs must be done by a Registered Professional Civil engineer and must comply with Employer’s standard mentioned above.

· All designs shall be reviewed and approved by Employer before construction work commences.

· Maintenance manuals must handed over to Employer upon completion of construction.

3.2.3.1 Geotechnical Investigations

The Contractor provides a Geotechnical Investigation, which shall include a desk study review of all existing geotechnical information, and all field and laboratory testing required to obtain the geotechnical parameters required for the civil engineering design. 

After completion of fieldworks and laboratory testing, the Contractor’s professional engineering geologist or geotechnical engineer prepares and submits a consolidated geotechnical report. 

The report shall contain as a minimum:

· Factual information and interpretive results.

· Site Location & Description.

· Project Geological Setting both Regional and Local; inclusive of geological and geo-hydrological hazards (where applicable).

· Description of fieldwork including equipment used.

· All Geological and Geo-hydrological surface and sub-surface conditions as determined by intrusive ground testing, with related drawings. 

· The geotechnical testing shall contain a minimum of four (4) trail pits and six (6) Dynamic Probe Super Heavy (DPSH) tests at the proposed location/s for the new storage tank and pump house.

· The laboratory testing shall contain the following tests as a minimum:

· Foundation Indicator including Hydrometer.

· In situ Moisture Content.

· Undisturbed Dry Density.

· Shear Box testing. 

· Double Oedometer (if deemed required).

· Soil pH and Electrical Conductivity. 

· Sampling conducted on representative disturbed and undisturbed samples. Samples are collected, stored and labelled as per the relevant South African Institute of Civil Engineering (SAICE) standards.

· The Contractor ensures that no services are impacted during intrusive excavation. It is the responsibility of the Contractor to conduct a geophysical survey of the proposed area prior to excavations. 

· Should impedances occur, the Contractor shall inform the Employer with a written notice of the impedance location and depth, and recommendations on how to proceed?

· The Employer accepts the recommendations put forth by the Contractor prior to commencement of field works.

· Discussions of all in situ and laboratory tests and classifications.

3.2.3.2 Analysis and Recommendations.

This shall include all recommendations for bearing capacities, settlements, foundations, earthworks and excavation (as deemed necessary by the proposed layout).

The Contractor makes written recommendations to the Employer should he/she be of the opinion that additional tests are required.

3.2.4 Electrical installations

The Contractor provides electrical installation in the following areas:

•
Lighting and small power for the new pump house.

•
Earthling and lightning protection of the new pump house. 

•
Power supply for two 132kW electrical pumps or equivalent.

•
Power supply for one jockey pump (new jockey pump)

•
Motors and cabling.

3.2.4.1 Lighting and small power

The Contractor designs, manufactures, supplies, installs, tests, certify and commissions lighting and small power circuits (distribution boards, plug sockets, welding plugs/sockets etc.) for the new pump house. These must comply with Coal Fired Power Stations Lighting and Small Power Installation Standard [3] as well as SANS 10114-1 [12] and SANS 10142 [11] requirements. 

Adequate lighting in the vicinity of the new pump house must be provided by the Contractor.

3.2.4.2 Earthing and Lightning protection

The Contractor designs, procures, transports, supplies, installs, tests and commissions the earthing and lightning protection system and its components, these must be in line with Earthing and Lighting Protection [7].

Earth resistance and earth continuity tests of the existing earthing system to determine the status of the earthing point must be performed by the Contractor.

The Contractor shall propose and implement lightning protection interventions

3.2.4.3 Power supply

The bulk power supply points will be identified by the Employer for the Contractor. This will be done for two electrical pump motors and jockey pump motor as well as for lighting and small power requirements. The total power requirements will be required and these must be given to the Employer. 

The diesel and electrical pumps control panels will be given the bulk power supply points by Employer using the existing voltage levels (400/380V AC) at the station. 

he designs, testing, installation and commissioning of the control panels of both diesel and electrical pumps as supplied by the Contractor must adhere to LV Switchgear Control Gear Assembly Associated Equipment for Voltage 1 000V AC and 1 500V Standard [34]. The power supply of the existing jockey pump will be assessed for its adequacy for the new jockey pump by the Employer. This will be used to supply the new jockey pump if found to be adequate. 

The two switchgear breakers required at the switchgear for the supply of the two electrical pumps will be specified by the Employer and these will be supplied by the Contractor. Breakers must comply with LV Switchgear Control Gear Assembly Associated Equipment for Voltage 1 000V AC and 1 500V Standard [34].

3.2.4.4 Motors

The motors will come as a package with the pumps and control panels as supplied by the Contractor.

The detailed designs, manufacturing/procurement, delivery, supply, installation, testing and commissioning of the motors must be in line with Procurement of Power Station Low Voltage Electric Motors Specification Standard [10].

3.2.4.5 Cabling, Racking and Routing

Cable design, manufacturing/procurement, transport, installation, testing and commissioning must be performed by the Contractor. The Contractor provides Test certificates.

The design and implementation of the optimised cable routing must be performed by the Contractor. This must cater for cable servitudes and as well as cable racking. 

The cables for the two electrical pumps and one jockey pump, welding sockets, plugs and small power requirements including cables needed for the 220V AC supply to C&I field panels as well as cables needed for earthing requirements must be catered for by the Contractor. 

The Employer will identify the supply points for the Contractor. 

Adhere to the Requirements for Control and Power Cables for Power stations Standard [4].

3.2.5 Increment of fire protection mains to respective 200mm and 250mm nominal bores
The Contractor designs, manufactures, supplies, installs, replaces, tests and commissions fire protection mains of around 1800m. See figure 1 regarding proposed replacement fire protection mains.

· The Contractor provides relevant piping, bends, reducers, flanges, valves, non-return valves, bolts, supports, fittings and other ancillary spares and material to merge the new installation with the existing system. 

· The Contractor shall decommission old piping and discard them at designated areas as approved by the Employer.
· The Contractor shall replace all damaged or corroded discharge piping from the ring main to inlet isolating valve of the deluge valve. The decision shall taken after intense evaluation of the piping condition is conducted.
· The Contractor’s modifications shall be approved by Employer before proceeding with the designs.
3.2.5.1 Design Basis for Pipework 
All pipes shall conform to SANS 62 [24] and SAN719 [25]
Fabricated flanged steel pipe and fittings used shall comply with the requirements of SANS 1476 [28].

3.2.5.2 Design basis for Pipe Supports

Pipe supports are to be provided for all the pipework installed 

All hangers and hanging material shall be hot dipped galvanized to SANS 121 [23] after fabrication and either welded or bolted on site. Site repairs and welding will be touched up with cold galvanizing in accordance with SANS 121 [23].
The fire protection system pipe supports shall be capable of supporting the loads of the system without exceeding the maximum permissible deflection. Pipes shall be positioned to maintain a clearance to any other fixed structure, except the members to which such pipes are clamped. Supports shall be designed in accordance with SANS 10287 [26].
Structural pipe supports are to be provided at intervals not exceeding 6m. Pipe supports not conforming to this requirement must be signed off by a professional engineer.

3.2.5.3 Galvanising Specification

All the pipework for fire water systems shall be hot dipped galvanized steel specified in SANS 121[23].

3.2.5.4 Design Requirements for Painting Specification for the Pipework
All fire system equipment shall be fully painted signal red colour code A11 in accordance with SANS 10140 [35].

NB. The replacement shall be carefully planned and coordinated with the site team to ensure the Power Station fire system is not impaired for longer than 12hrs

The proposed fire protection system main piping is shown below in figure 1

[image: image2.png]Legend  ———— 250mm pipe diameter
"200mm pipe diameter




Figure 2: Proposed main piping 

3.2.6 Water Storage Tank

The Contractor provides outpricing cost for the following two options provided by the Employer.

3.2.6.1.1 Option 1: Refurbishment existing water storage tank

The Contractor designs, manufactures, supplies, installs and commissions roof profiles for 480 m3 emulsifier panel storage tank with equivalent galvanised profiles preferably longline 305®.

The Contractor removes, supplies, installs and replaces damaged or corroded galvanised steel panel or structure. 

3.2.6.1.2 Option 2: Provide at least 740m3 new water storage tank

The Contractor designs, prepares, manufactures, supplies, constructs, installs and commissions at least 740m3 storage tank to meet largest designed fire water demand plus the maximum hose stream demand of not less than two (2) hydrants for a minimum duration of two (2) hours. The new storage tank shall be placed in the area approved by the Employer. 

The Contractor designs and constructs foundation in line with capacity requirements of the tank. 

Technical requirements include: 

· A full Geotechnical survey.

· The new tank foundation shall as a minimum consist of a reinforced concrete slab foundation (subject to geotechnical survey).

· All access and drainage requirements should be considered in the design.

· All designs must be done by a Registered Professional Civil engineer and comply to relevant Eskom standard as mentioned above.

· As built drawings to be provided to Employer as per the requirements of Engineering Drawing Standard: Common Requirements [27].

· Maintenance manuals to be handed over to Employer after construction.

· All designs shall be reviewed and approved by Employer before construction work.

3.3 Procedure for submission and acceptance of Contractor’s design

The Contractor shall establish a document tracking system to record the dates for the supply and receipt of all design drawings, calculations, requests for information and design documentation.
The Contractor shall supply the following documentation as the minimum requirements of this specification in the design package before any manufacturing, construction or commissioning commences:
· Document submittal schedule indicating when all documents shall be submitted
· Drawing Register indicating when drawings shall be submitted
· Complete detailed design file
· Functional Specifications
· Line Sizing Calculations and Material Selection
· Final isometric and general arrangements illustrating pipe dimensions, pipeline layouts and showing pipe supports
· General Arrangement Drawing of System and boundaries
· Piping and Instrument Diagrams
· Component material datasheets
· Quality Control Procedures
· Quality Control Plan and Inspection and Test Plan
· Method Statements
· Hydraulic calculations - with design point
· Hydraulic calculations - without design point (utilising the site input pressure)

· Commissioning  procedures

· Assembly procedures

· Technical, Operation and Maintenance Manuals of all plant equipment

· Operating and Control Philosophies

· Maintenance Philosophy

· Maintenance schedules

· Pipeline Schedule

· Mechanical Hook-up diagrams

· Critical Spares List

· Welding Procedure Specifications

· Welding Procedure Qualification Record

· Operating, Maintenance and Engineering Training Manuals

The Contractor shall seek acceptance of the detailed designs from the Employer. The detailed design is reviewed internally by Eskom utilising the Eskom Design Review Procedure. This process can take up to 14 days. Only drawings and designs accepted by the Employer shall be used for construction.
3.4 Other requirements of the Contractor’s design

3.4.1 Physical Characteristics Requirements

The Contractor shall ensure that the design of the system is consistent throughout. All equipment shall be protected from external ingress, corrosion and explosion proof where applicable.

3.4.2 Fire Protection

The Contractor shall provide a fire risk analysis as part of the design approval process to the Project Manager for approval. The Contractor shall implement the protection measures required to mitigate the risks identified in the fire risk analysis.

3.4.3 Corrosion Protection

Plant and Materials are adequately protected from physical damage and corrosion during storage and erection

3.4.4 Testing and Commissioning

Testing and commissioning shall include as a minimum:

The services of skilled Engineers to supervise the testing and commissioning and making ready for the operation of the works as required for partial and full duty operation as

The Contractor shall provide a method for testing the integrity of the piping system for acceptance by the Project Manager. The Contractor shall make provision for any equipment required to perform the necessary testing 

The Contractor's preliminary trials and commissioning of the works shall be carried out by the Contractor's representatives, who shall remain in attendance until such time as the works are working to the Employer's satisfaction. A requirement of these trials is 2 hour test period to determine that all activities as laid down in the operating manuals are correct and are carried out in the correct sequence and to determine that all the plants have been provided as required in the scope of work.
The Contractor shall supply all data books with signed (Inspection and Testing Plan) ITPs and as built drawings of the works
Commissioning of the system shall be done by the Contractor’s staff with the Employer’s dedicated operations/commissioning staff

The Contractor shall submit a commissioning schedule and program for acceptance to the Project Manager by the contract date

Before plant and equipment is placed in service the Contractor shall certify that it is in a suitable and safe condition.

Prior to the time when commissioning is to commence, the Project Manager shall appoint a representative who shall co-ordinate the commissioning of all plant and equipment forming an integral part of the system being commissioned. The Contractor shall be responsible for the commissioning of all the plant and materials he/she shall supply to the requirements of this specification to the satisfaction of the Project Manager and the Employer's representatives. Where various components are already in place, or are supplied by the Employer to form an integrated system, the Contractor at the time of commissioning, shall carry the responsibility for the correct functioning of the whole system

In the event of incorrect functioning, the Contractor shall determine the cause and shall correct the defect if the defect is within plant and equipment of his/her own supply. The Contractor, at the time of commissioning, has the agreement, or alternatively, the attendance of the Project Manager involved in a particular phase, before proceeding with commissioning. Consequently , the Contractor shall assure himself/herself as to the safety of his/her own plant and equipment in respect of any particular commissioning test and in the event of damage accept responsibility for such plant and equipment 

The Contractor shall commission the works and ensures conformance to the Employer's performance requirements for the works. The Employer takes over sections of the system as required once the system performance requirements have been verified by the Contractor
3.5 Use of Contractor’s design

The completed design shall become property of the Employer
3.6 Design of Equipment
N/A
3.7 Equipment required to be included in the works
The Contractor shall prepare and submit a project ITP for the affected system and materials included in the scope. The project ITP shall detail all elements of the plant and shall itemise the required quality levels for each of these components.

The Contractor shall indicate in the project ITP which items are of a proprietary nature where the level of certification is limited to standard documentation and certificates of conformity. 

The Contractor shall use only ISO 9001 accredited suppliers for these products. Evidence of ISO 9001 certification shall be supplied with the delivery documentation. Failure to include this certification at the time of delivery shall result in rejection of the plant and materials by the Employer
3.8 As-built drawings, operating manuals and maintenance schedules

All as-built drawings shall be available to the Employer as soon as the plant is ready for commissioning. All drawings and reports compiled for the works are to become the property of the Employer on completion of the works.
The Contractor shall ensure the following:

· Makes use of a system compatible with the Employer's Microstation (Version 7/8 SE 2D) CAD for all drawings supplied to the Employer in electronic medium (e.g. disks) in addition to prints. Additionally, all drawings shall be supplied in Adobe PDF format.

· All drawings shall be originally created in the required format which is Microstation version 7/8 SE 2D, according to the specified drawing format and standards 36-945, 36-945, 36-946 available from DO on request . 

· No conversion from other format will be accepted. Accompanying the new drawings will be the item list with full component descriptions.

· Implements and maintains an updated drawing register, the format of which shall be submitted to the Project Manager for acceptance. Updates are submitted on a regular basis or when significant changes are made.

The Contractor shall submit detailed drawings of all the separate items of the works included in the specification for acceptance once the general arrangement drawings have been accepted. If works or materials are supplied before such acceptance has been given, the Contractor shall modify or replaces such works or material at his own expense if called upon by the Project Manager to do so.

Submit four prints of all "as built" drawings with approval signatures at completion by the ECSA registered professional engineer accountable for the design, backed up on the electronic medium, without delay on request by the Project Manager.
3.8.1 TECHNICAL, OPERATING AND MAINTENANCE MANUALS

The Contractor shall provide good quality operating and maintenance manuals prepared by suitably experienced personnel. The maintenance manuals shall state explicitly the maintenance requirements for each piece of equipment. Copies of the first draft manuals as well as all "as built" drawings are submitted to the Project Manager for review and acceptance. Manuals are in English and each manual is complete with the Power Station's name, contract number and index. The Contractor shall also provide an electronic copy of these documents.

The manuals should indicate the level of responsibility of the operating personnel for each action in the procedures. Included in these manuals are the following:

· Design data including descriptions of control philosophy with alarms, set-points, interlocks and logics clearly explained.

· Range, calibration factors, calibrations certificates, data sheets, etc., for all control and instrumentation equipment.

· General arrangement and installation drawings and instructions.

· Operating procedures and instructions for normal and emergency conditions, including flow diagrams.

· Maintenance procedures and instructions for specific plant and equipment.

· All drawings required for component location, dismantling and re-assembly for maintenance.

· Equipment details such as make, model, type, specifications, etc

· Detailed parts lists and ordering instructions pertaining to storage of spare parts or to their shelf life.

· Exploded view type drawings clearly detailing the part and uniquely identifying it, technical descriptions of the equipment and component parts.

· Catalogues, schedules and other product support documents.

· Troubleshooting and fault finding guide.

· Safety procedures and instructions.

· All special tools and equipment required for maintaining and operating the works.

The technical manuals shall include fully detailed descriptions, as-built drawings, diagrams, illustrations, schedules and data for use by Eskom  technical staff to evaluate performance, trace faults, adjust, maintain and fully understand the plant and to allow satisfactory training of junior staff in conjunction with the operating manuals.

The operating manuals shall be set out in simple terms in ordinal, tabular or pictorial form to provide factual and concise descriptions of:

· How to carry out start-up, shut-down, and service operation of the plants by automatic, semi­automatic and by manual control.

· What happens when the plants are operated, e.g. where does the water, etc. flow when a sequence is initiated or a valve is operated.

· What an alarm condition implies and how it is corrected.

· What problems can occur and how they are overcome.

· A routine visual plants inspection procedure.

The operating manuals are intended for daily use and therefore shall be separated from the technical and maintenance manuals. Bold print, diagrams, illustrations, etc. shall be used.

The maintenance instruction manuals shall include schedules to cover plant inspection procedures, fully detailed maintenance programs for plant and plant equipment services at daily, monthly, three monthly, six monthly, yearly and any other necessary intervals, and contain manufacturer's and supplier's detailed maintenance and lubrication instructions, diagrams, sectional drawings giving part numbers, descriptions etc. Where spare parts have been provided these should be coloured in, scheduled, and their filling procedure described. The manual shall also include minimum surveillance requirements for the plant.

Detailed maintenance procedures, covering removal, dismantling, replacement of parts, re-erection, checking, and reassembly and re-commissioning shall be included for all equipment. The re­commissioning shall be included for all equipment. The maintenance manual shall be fully comprehensive and cover all plant and materials installed. As the manuals shall be frequently used for training and maintenance, they shall be prepared similarly to those described for the operating instruction manuals for use by operating personnel.

4 Procurement

4.1 People
4.1.1 Minimum requirements of people employed on the Site

· The Contractor provides sufficient personnel with the required experience, expertise and skills to provide the Works.

· The Employer considers the provision of sufficient supervisory staff to be an essential part of the responsibilities of the Contractor and requires the Contractor to appoint a suitably qualified Site Supervisor who is also authorised as a Responsible Person (appointed in term of the Plant Safety Regulations), to permanently manage all aspects of the Contractor’s activities and responsibilities on site for the duration of the contract.

4.1.2 BBBEE and preferencing scheme

As per SDL & I requirements
4.1.3 Accelerated Shared Growth Initiative – South Africa (ASGI-SA) 

The Contractor complies with and fulfils the Contractor’s obligations in respect of the Accelerated and Shared Growth Initiative - South Africa in accordance with and as provided for in the Contractor’s ASGI-SA Compliance Schedule stated below

.

[Insert the agreed ASGI-SA Compliance Schedule here]

The Contractor shall keep accurate records and provide the Project Manager with reports on the Contractor’s actual delivery against the above stated ASGI-SA criteria.   [Elaborate on access to and format of records and frequency of submission etc.]
The Contractor’s failure to comply with his ASGI-SA obligations constitutes substantial failure on the part of the Contractor to comply with his obligations under this contract.
4.2 Subcontracting
4.2.1 Preferred subcontractors

Contractor submits conditions of subcontracting contract to the Project Manager for approval. 

4.2.2 Subcontract documentation, and assessment of subcontract tenders

The use of NEC document is compulsory. Specified constraints on how the Contractor prepares subcontract documentation and how subcontract tenders are to be issued, received, assessed (using joint report) and awarded.
4.2.3 Limitations on subcontracting

Contractor obtains approval from the Project Manager. Employer permits Contractor to subcontract other works, but not more than a specialised proportion of the whole contract. Contractor provides the majority of the works with own resources and all the necessary documentation for the works carried out by subcontracting is submitted to the Project Manager for approval

4.2.4 Attendance on subcontractors

The main Contractor is responsible for the management of the duties and performance of the Subcontractor.

4.3 Plant and Materials

4.3.1 Quality

The Employer places emphasis on the provision of a comprehensive Quality Management System (QMS) for all phases of the project in accordance with 240-1105658000 [37] Supplier Quality Management Specification. The QMS shall comply with the requirements of ISO 9001. 

The Contractor and all of the Contractors' suppliers shall hold a valid certificate of compliance for their QMS to the requirements of ISO 9001:2008. The Employer may at his sole discretion carry out an audit any supplier or sub-supplier QMS for compliance.

Documents shall be submitted for review and acceptance by the Project Manager prior to the commencement of work.

No work is allowed on Site unless the Employer accepts the Quality Control Plan.

The Contractor shall utilise the Employer's quality documentation forms for requesting access, erection checks etc. These request forms are to be submitted to the Supervisor at least one week prior to the requested activity. or as agreed to by the Project Manager.
Apart from any statutory data packages required, the Contractor shall also compile a data package of the relevant drawings, test certificates etc. for each section of work which is to be reviewed and signed off by the Supervisor at erection stage prior to the commencement of the commissioning phase.

4.3.2 Plant & Materials provided “free issue” by the Employer
No ''free issue" items shall be supplied. All Plant and Materials are to be provided by the Contractor.
4.3.3 Contractor’s procurement of Plant and Materials

The Contractor shall procure all Plant and Materials required for constructing, installing and commissioning the works.
The Contractor shall:
· Advise the Project Manager in advance of all major shipments of Plant and Material and co­ ordinates with the Employer the arrival, off-loading and release of such. The Contractor shall promptly unload shipments and promptly releases carrier equipment.

· Notifies the Project Manager of being unable to promptly unload any shipment not less than 5 (five) days prior to arrival. The Project Manager, at his/her option, off-loads or makes arrangements for others to off-load such shipments for the account and risk of the Contractor. Costs incurred in respect of off-loading shall be for the Contractor's account.

· Ensures that all the Plant and Materials are inspected. The Contractor shall notify the Project Manager who instructs designated Employer's representatives to inspect the Plant and Materials at the factory, or the Contractor's premises, before it is transported to the Site.

· Ensures that all relevant factory tests are witnessed and accepted by the designated Employer's representatives. Any deviations from accepted drawings, standards or specifications are noted and reported to the Contractor by the above mentioned representatives. A copy of the deviations is forwarded to the Project Manager for record keeping. The Project Manager follows up with the Contractor to ensure that deviations are successfully corrected.

4.3.4 Spares and consumables
The Contractor shall supply, on acceptance by the Project Manager, a set of spares considered to be essential as part of the works.
The Contractor shall submit, on completion of the design, a detailed listing of the recommended spares and prices for the Project Manager's acceptance to comply with the aforementioned requirement. The prices quoted shall include for packing, delivery to and off-loading at site, inspection and testing and adequate protection against corrosion, damage and weathering during transit and storage.

4.4 Tests and inspections before delivery

The Employer carries out quality inspections at his discretion.

All inspections and testing to be performed in accordance with the Quality Control Procedure developed by the Contractor.
The Employer shall be provided access to the Contractor's premises for the purpose of:

· Establishing compliance with the contractual requirements by means of inspections, surveillance and audits.

· Witnessing the performance of any tests.

The Contractor shall obtain clearance from the Employer or the Employer's agent before dispatching of the equipment. This factory release inspection does not release the Contractor of any of his obligations under the contract.

No Plant shall be released for dispatch without the AS MANUFACTURED documentation and drawings accompanying them.

4.5 Marking Plant and Materials outside the Working Areas

All equipment to be safely stored as per the OHS Act.

All plant and equipment to be removed from the designated area can only be removed with the permission of the Contractor and Project Manager.
4.6 Contractor’s Equipment (including temporary works).

The Contractor shall be liable for all plant and equipment in the designated area under his control.

The Employer shall not take any responsibility for any loss or damage to the equipment.
4.7 Cataloguing requirements by the Contractor
The Contractor to provide a list of all material and component used in the project with full description or specification.
5 Construction

5.1 Temporary works, Site services & construction constraints

5.1.1 Employer’s Site entry and security control, permits, and Site regulations
Employers Site entry and security control, permits, and Site regulations

All the Contractor's employees shall be required to attend a safety induction course before they shall be allowed to work on the Site. It shall be the responsibility of the Contractor to ensure that all employees have attended the safety induction. The Contractor shall compile his safety file for approval at the safety officer. The safety officer shall first approve this file, before the Contractor can attend the safety induction course.

A list of employees requiring safety induction shall be submitted at least 2 days in advance of arrival on site with the date and time of arrival so that safety induction can be arranged.

Site access control to HPS shall be arranged with the Project Manager after successfully completing the safety induction course.

Alcohol testing shall be conducted at any time on all employees entering the HPS premises. All staff that tested positive for alcohol abuse shall not be allowed on site.

All vehicles shall comply with the Road Traffic Act.

Vehicle inspections shall be conducted on a daily basis and check sheets shall be kept at the Contractor's
5.1.2 Restrictions to access on Site, roads, walkways and barricades

Restrictions to access on Site, roads, walkway and barricades shall be observed. 

5.1.3 People restrictions on Site; hours of work, conduct and records

Working hours at Employer are 07:00 -16:15 on Mondays to Thursdays and 07:00 -12:00pm on Fridays. Collection and delivery of any plant or equipment would be within working hours.

During the execution of the works, Contractor keeps records of signed registers or time sheets of the Contractor’s specific employees on site, including subcontractors. Contractor keeps the records, and avail it to the Project Manager upon request.
5.1.4 Health and safety facilities on Site 
The Medical Centre is used by all individuals on site for injuries and first aid related issues, however cost to perform Medical services is covered by the Contractor. The fire department is also available for fire and other related emergencies. Their respective contact details to be provided during induction. However, the Contractor must have their own medical facilities available and appointed safety supervisor.
5.1.5 Environmental controls, fauna & flora, dealing with objects of historical interest 

Contractor refers to section 4.2, of the issued Part C31 ECC3 Employer’s Work Information, for environmental compliance to be adhered to during execution of this contract.
5.1.6 Title to materials from demolition and excavation

Employer has the title deeds to the waste accumulated from conducting the works. Contractor complies with the following waste disposal requirements:

i. Construction rubble is disposed at the landfill site.

ii. Hazardous waste is disposed at a permitted landfill. Contractor submits disposal certificate to Project Manager for approval.
5.1.7 Cooperating with and obtaining acceptance of Others

Site access is granted by Project Manager. During contract period, Contractor works in parallel with other contractors.

The routing of all written communications is between the Project Manager and the Contractor only. Any agreement between the Contractor and any other person representing the Employer which has not been routed via the Project Manager is unacceptable and invalid.

Contractor takes charge of the work site and ensures no interference from other parties which may hinder the progress and completion of the works in the stipulated time frame. 

5.1.8 Publicity and progress photographs 

No pictures of anything on site are taken by the Contractor without prior approval by the Project Manager 
5.1.9 Contractor’s Equipment

The Contractor shall provide all Equipment that is required to complete the works.
The Contractor's Equipment shall not impair the operation or access to the plant.

The Contractor shall provide all or any temporary or expendable materials required for the storage of material.

Any Equipment, or appliances used by the Contractor shall conform to the applicable OHS Act safety standards and is maintained in a safe and proper working condition. The Project Manager has the right to stop the Contractor's use of any Equipment which, in the opinion of Project Manager, does not conform to the foregoing.

Off-loading and material handling Equipment such as cranes and fork lifts are available on Site (within the station's security fence) and shall be arranged with the Project Manager if required by the Contractor. Off-site requirements for cranes and fork lifts are not provided by the Employer and shall be arranged by the Contractor at his own expense.

The Contractor shall submit a list of all tools and equipment entering site. Equipment and tools not declared shall become the Employer's property.

On completion of the project, all tools and equipment shall be removed only with permission from the

Project Manager on the applicable approved Employer documents.

5.1.10 Equipment provided by the Employer
Employer provides scaffolding during the execution of the works. Contractor notifies Project Manager within 3 days for scaffolding requests.

5.1.11 Site services and facilities
	Item
	Date by which it will be provided

	Safety file review  
	Before commencement of the project

	Induction for Contractor’s Employer’s
	Before commencement of the project

	Power supply at the site-establishment area
	At commencement of the project

	Potable water 
	At commencement of the project

	Waste disposal area
	At commencement of the project


5.1.11.1 Supply of electricity

All points of supply requested by the Contractor are provided in terms of quantity and location at the discretion of the Project Manager.
There is no energy charge for electricity used for construction purposes.

No connection is made to the permanent installation at the Power Station without the prior approval by the Project Manager.
No guarantees of power supply quality are given and power supply breaks of some duration may occur without warning. Planned outages are also a possibility. The Contractor shall make arrangements at his own expense to improve continuity and quality of power where necessary for any reason and no claim of any nature relating to power failures is considered.

All electrical work shall have a valid Certificate of Compliance (COG).

5.1.12 Roads

Main access roads are surfaced and complete and may be used by the Contractor with the necessary care. The Employer maintains the Site roads, described above, to a fair condition. Any costs incurred by the Project Manager from damage caused to underground services, structures, etc. as a result of the Contractor not using the prescribed routes is recovered from the Contractor
5.1.13 .First Aid and Fire Fighting

The Contractor in cases of emergencies or accidents shall call upon the services of the first aid and firefighting resources at the HPS.

5.1.14 Sanitary Facilities

The Employer's sanitary facilities are used as directed by the Project Manager.
5.1.15 Facilities provided by the Contractor
Contractor provides:

i. All the necessary machinery/equipment and facilities to provide the Works. This includes machinery/equipment and facilities not issued by the Employer
ii. Their own resources to secure security of machinery and equipment that may be stored on site. Employer is not liable to account for any costs related to damages or theft of machinery and equipment.
Contractor keeps comprehensive records of the Contractor’s equipment bought on and removed from site. Contractor complies with the Employer’s site access procedures.
1.1.1 Lay Down Areas

No Plant, Material and Equipment lay down areas are permitted on the terrace. The Contractor shall deliver all Plant, Materials and Equipment to the point of erection as and when needed. Plant, Materials and Equipment not used within 14 days are removed from the terrace and stored in the site yard.

5.1.16 Security

The Contractor shall provide security necessary for the protection of the works at all times until the completion of the whole of the works.
The Contractor shall be informed of the access procedures through Site Regulations and note that such procedures may change depending on the prevailing security situation.

All persons entering the site pass through the control points at the main access gate and shall be required to have temporary permits that are issued to Contractor's staff on request. If it is necessary to bring Equipment onto site a list is submitted which is verified by security staff prior to Equipment entering the security area.

No firearms, weapons, alcohol, illegal substances and cameras (including cell phones with cameras) are permitted on Site.

The generator area and the other units are barricaded and out of bounds and only authorised persons are permitted. Areas outside the Site are out of bounds to the Contractor's staff.

5.1.17 Giving Notice of Work to be Covered Up

All intended activities shall be captured in the scope of work and also on the project schedule. The project schedule shall be reviewed and updated weekly.

5.1.18 Existing premises, inspection of adjoining properties and checking work of Others

Inspection with the owners of adjacent buildings and properties, before commencing with the works, are required that have the potential to damage surrounding buildings and property. Contractor inspects the work of Others to which he/she is required to connect but he/she inspects in the presence of Others.

5.1.19 Survey control and setting out of the works
Contractor provides all the necessary equipment and facilities to execute the works.
5.1.20 Excavations and associated water control

Contractor ensures all excavations are barricaded and sufficient signage placed around excavated areas
5.1.21 Underground services, other existing services, cable and pipe trenches and covers
The station has underground piping for fire system, potable range, sewage system and cables. For any excavation to be undertaken cable detection to be conducted prior. 
Any damage to these systems due to negligence shall be repair by the contractor at his or her cost.

Any challenges with regarding the existing system shall be communicated with the Project Manager. 
5.1.22 Control of noise, dust, water and waste 

Contractor disposes waste as per waste management procedure. Misuse of water is not tolerated. Usage of noisy machinery is tested by the Occupational Hygienist to assess if noise level is acceptable
5.1.23 Sequences of construction or installation

Contractor refers to

i. NEC ECC3 Employer’s Work Information.

ii. Sequence of executing the works and interfacing requirements is discussed during kick-off meeting.
5.1.24 Giving notice of work to be covered up
Contractor notifies Project Manager within 3 days of works to be covered up
5.1.25 Hook ups to existing works

Contractor complies with working at heights requirements, of hook up heights above or below 2m during the execution of the works.
5.2 Completion, testing, commissioning and correction of Defects

5.2.1 Work to be done by the Completion Date

The entire works shall be completed by the agreed upon completion date including commissioning and testing. 

5.2.2 Use of the works before Completion has been certified

Take-over is after Completion through QIP/QCP assessment and authorization of every task, final approval and authorization of reports.
5.2.3 Materials facilities and samples for tests and inspections 
The Contractor to provide material facilities and samples for tests as stipulated  in the scope of work. 
5.2.4 Commissioning
Take-over and/or commissioning is after Completion through QIP/QCP assessment and authorization of every task, final approval and authorization of reports.
5.2.5 Start-up procedures required to put the works into operation
The plant shall be put in operation after safety clearance of certain parts of the plant and systems

Sign off shall be scheduled as per the project schedule on completion of each activity
5.2.6 Take over procedures

Take-over or hand over shall be scheduled as per completion
5.2.7 Access given by the Employer for correction of Defects

The defects period is 52 weeks from completion of the entire works. Any defects shall be rectified within this period at the expense of the Contractor and at the convenience of the Project Manager.
5.2.8 Performance tests after Completion

Acceptance tests shall be carried out to prove all the plant guarantee figures provided by the Contractor in the technical schedules. The Contractor shall provide his own testing equipment.

· Pipework shall be fully flushed to ensure no debris is left inside the pipework.

· Newly installed pipework shall be hydraulically tested in accordance with NFPA 15 [29].

· If any fault, such as permanent distortion, rupture or leakage, is disclosed by the hydraulic test, the fault shall be corrected and the test shall be repeated.

· A spray test is to be performed to test the functioning of the valves and high velocity nozzles.

· This test shall be conducted in accordance with NFPA 15 [29].

· All equipment which is sensitive to water damage is to be covered when performing spray tests.

· A commissioning certificate is to be issued to Eskom for acceptance once the commissioning of a system is completed.

· The contractor is to supply commissioning procedure, pipe flush and pressure test procedure for acceptance when QCPs are submitted.

Where the results of the performance tests performed don't correlate with expected results (flow rates, pressures etc.) and/or the control functions as per the operating philosophy do not meet the specifications guaranteed, then the Contractor, at his own expense, shall carry out all necessary adjustments and modifications to the works required to obtain the stated tolerances. Fully detailed proposals are submitted in writing to the Project Manager for acceptance before any adjustments and modifications are made and work in this respect is carried out when convenient to the Project Manager. All adjustments and modifications are subject to inspection and approval by the Project Manager.

When adjustments and modifications are completed, the Contractor shall advise the Project Manager in writing to this effect and applies for a further acceptance test. From the results obtained, and provided that the Employer is satisfied that it shall be lasting, the works shall be finally accepted by Project Manager.
5.2.9 Training and technology transfer

The Contractor shall provide training to the operating, maintenance and engineering departments of the Employer. All Operating and Maintenance requirements must be included in the training manuals
5.2.10 Operational maintenance after Completion

The contractor shall provide Eskom with the maintenance and operating procedure for the fire protection systems. The procedure shall include the recommended maintenance intervals and maintenance to be carried out on the fire system and components, test procedure and list of recommended spares to ensure reliable operation of the fire protection system.

6 Plant and Materials standards and workmanship

6.1 Investigation, survey and Site clearance

Contractor refers to NEC ECC3 Employer’s Work Information.

Contractor site de-establishes once take-over is completed through QIP/QCP assessment and sign off, final approval and authorization of reports. Project Manager approves Contractor’s site de-establishment.
6.2 Building works
The Contractor shall be responsible for the design, erection, maintenance and removal of all temporary bracing or propping required for the execution of the works.
The Contractor shall adhere to the Eskom Standards and should these be unavailable, the relevant SANS standard shall apply.

The Contractor shall provide all relevant welding procedures for acceptance to the Project Manager. The Contractor's welding procedures shall comply with Eskom Standard 240- 106628253 [15] (Standard for Welding Requirements on Eskom Plant) and Eskom Standard for Quality 240-1105658000 [37].

6.3 Civil engineering and structural works

All works shall be performed in accordance with the Contractor's accepted Quality Control Plan. All construction and erection work conducted on the site shall be subject to inspection by the Supervisor.

The construction and erection of the works shall be performed under the supervision of the Supervisor. An acceptance/test schedule shall be compiled by the Contractor and approved by the Supervisor.

All equipment required for the erection and completion of the works shall be supplied by the Contractor. This Equipment shall be in good condition and subject to the Employer's safety requirements.

The Contractor shall supply all Plant and Materials where new Plant and Materials are required for the completion of the works.
All Plant and Materials used shall comply with the requirements regarding quality, method of manufacturing, testing and performance specification as given in the relevant SASS/SANS specification, or where such a specification does not exist, the requirements of the relevant British or ISO standard. All plant and materials shall be suitable for use or operation under the operating conditions applicable to the system.

6.4 Restricted Working Conditions

The erection of any temporary works such as formwork is subject to acceptance of the Supervisor. The Contractor shall take all necessary precautions to ensure that no damage to any existing plant and equipment takes place during the works. The Contractor shall supply all equipment necessary for the construction of the works. The Contractor shall take cognizance of existing plant and equipment as well as safety and housekeeping constraints. It is the Contractor's responsibility to overcome any issues that may arise due to space constraints with prior consent from the Project Manager and no extra payment or claim of any kind shall be allowed on account of difficulties of access to the works.
6.5 Electrical & mechanical engineering works

Contractor refers to NEC ECC3 Employer’s Work Information.

6.6 Process control and IT works
N/A
1.2 DOCUMENTATION AND CONFIGURATION MANAGEMENT

6.6.1 Document Management

All documents supplied by the Contractor shall be subject to Eskom's .approval. The language of all documentation shall be in English. The Contractor shall include the Employer's drawing number in the drawing title block. This requirement only applies to design drawings developed by the Contractor and his Sub-contractors. Drawing numbers will be assigned by the Employer as drawings are developed. All documentation shall be controlled and managed in accordance with Document and Records Management Procedure (32-6).

6.6.2 Document Identification

The Contractor is required to submit the Vendor Document Submission Schedule (VDSS) as per agreed dates to the delegated Eskom Representative. Eskom will pre-allocate document numbers on the VDSS and send back to the Contractor through the delegated Eskom Representative. The VDSS is revisable and changes· must be discussed and agreed upon by.all parties. Changes in the VDSS can be additional documentation to be submitted, changes in submission dates or corrections in documentation descriptions, document numbers, etc. The Contractor's VDSS shall indicate the format of documents to be submitted.

6.6.3 Document Submission

All project documents must be submitted to the delegated Eskom Representative with transmittal note according to Project I Plant Specific Technical Documents and Records Management Work Instruction (240-76992014 [38]). In order to portray a consistent image it is important that all documents used within the project follow the same standards of layout, style and formatting as described in the Work Instruction. The Contractor is required to submit documents as electronic and hard copies and both copies must be delivered to the Eskom Representative with a transmittal note.

In addition, the Contractor shall be provided with the following standards which must be adhered to:

· Documentation Management Review and Handover Procedure for Gx Coal Projects 240-66920003 [35].

· Project Documentation Deliverable Requirement Specification 240-65459834 [30].

· Technical Documentation Classification and Designation Standard 240-54179170 [31].

· Project/ Plant Specific Technical Documents and Records Management Work Instruction 240-76992014 [38].

6.6.4 Email Subject

The Contractor shall submit all documentation to the Eskom Representative as well as the Project's Documentation Centre in the following media:

Electronic copies shall be submitted to Eskom Representative through the email that will be specified. The email subject shall as a minimum have the following: (Project Name, Discipline and Subject). Electronic copies that are too large for email will be delivered on CD/DVD, large file transfer protocol and/or hard drives to the Project Documentation Centre. A notification email, with the transmittal note attached, shall be sent to the Eskom Representative. Hard copies shall be submitted to the Eskom Representative accompanied by the Transmittal Note.

6.6.5 Engineering Change Management

All Design change management shall be performed in accordance to the latest revision of the Eskom Engineering Change Management Procedure 240-53114002 [32] and the Employer shall ensure that Contractor is provided with latest revisions of this procedure. Any uncertainty regarding this procedure should be clarified with the Employer. All design reviews will be conducted according to the Design Review Procedure 240-53113685 [33].
1.3 Drawings Format and Layout

The creation, issuing and control of all Engineering Drawings will be in accordance to the latest revision of Engineering Drawing Standard 240-86973501 [27]. Drawings issued to Eskom will be a minimum of one hardcopy and an electronic copy that is editable. All Contractors are required to submit electronic drawings in Micro Station (DGN) format, and scanned drawings in "PDF" format. No drawings in TIFF, AUTOCAD or any other electronic format will be accepted. Drawings issued to Eskom may not be "Right Protected" or encrypted. The Employer reserves the right to use these drawings to meet other contractual obligations.
1.4 CONFIGURATION MANAGEMENT

6.6.6 General Requirement

The Contractor includes the Employer's drawing number in the drawing title block. This requirement only applies to design drawings developed by the Contractor and his Subcontractors. It does not apply to drawings developed by manufacturers for equipment and material such as valves, instruments, etc. Drawing numbers will be assigned by the Employer as drawings are developed.

The project name shall be listed on all drawings, including manufacturers' drawings.  Tag numbers and equipment names shall be listed on all manufacturers' drawings. A separate sheet may be attached to the submittal if needed to adequately list all tag .numbers associated with the drawings such as valves which may have numerous tag numbers associated with it.

The language of all documentation shall be in the English language. The units of measure shall be metric.

The Contractor retains project design calculations and information for the entire life cycle of the plant and provides these to the Employer on prior written notice at any time notwithstanding the expiry or termination of the contract.

6.6.7 Configuration Management

The Contractor supplies a comprehensive configuration management program according to ISO 10007 (2nd Edition) to ensure that plant structures, components and computer software conform to approved design requirements. However a project specific Configuration Management Plan document will be developed which will be aligned to ISO 10007. In addition, the Works as-built physical and functional characteristics shall be accurately reflected in selected documents and databases, including those for design, procurement, construction, operation, testing and training. The configuration program shall · be applicable for use throughout all phases of the project life cycle, including management of spare parts, replacement parts and product upgrades , and shall form part of deliverables for hand-over to the Employer for use during the operation and maintenance phases of the plant.

6.6.8 Change Management

All Design change management shall be performed in in line with the Eskom Project Change Management Procedure 240-53114002 [32] and the Employer ensures that Contractor is provided with latest revisions of this procedure. Any uncertainty regarding this procedure should be clarified with the Employer and clarification updates should be reflected in updated versions of this procedure.

6.6.9 Design Review Documentation

The Contractor conducts design reviews as per the Contractors official design review procedure. Contractor further takes note of the Employers Design Review Procedure 240-53113685 [33] and participates in all design reviews as specified by the Employer. The Employer may "Accepted"; "Accept with Comments" or "Rejected". If required, the Contractor makes the necessary revisions on the documentation and ensures acceptance is obtained from Employer. The Contractor includes these design reviews as part of the schedule and suggests appropriate timing for such reviews
7 Normative/Informative References
Parties using this document shall apply the most recent edition of the documents listed in the following paragraphs.

7.1 Normative
[1] ISO 9001 Quality Management Systems

[2] 240-54937450 Fire Protection and Life Safety Design Standard

[3] 240-55714363 Coal Fired Power Stations Lighting and Small Power Installation Standard
[4] 240-56227443 Requirements for Control and Power Cables for Power Stations Standard
[5] 240-56355754 Field Instrument Installation Standard
[6] 240-56355815 Field Instrument Installation Standard: Junction Boxes and Cable Termination

[7] 240-56356396 Earthing and Lighting Protection Standard 
[8] 240-56364545 Structural Design and Engineering Standard 

[9] 240-107981296 Constructability Assessment Guidelines

[10] 240-57617975 Procurement of Power Station Low Voltage Electric Motors Specification Standard
[11] SANS 10142 The Wiring of Premises Part 1: Low-voltage Installations

[12] SANS 10114-1 Interior Lighting Part 1: Artificial Lighting of Interiors 

[13] 240-105020315 Standard for Low Pressure Valves.

[14] 240-123801640 Standard for Low Pressure Pipelines

[15] 240-106628253 Standard for Welding Requirement on Eskom

[16] 240-106365693 Standard for External Corrosion Protection of Plant, Equipment and Associated Piping with Coatings.

[17] 240-101712128 Standard for the Internal Corrosion Protection of Water Systems, Chemical Tanks and Vessels And Associated Piping With Linings

[18] 240-85549846 Standard for Design Drainage and Sewerage Infrastructure

[19] 240-56356376 On-Site Commission for Low Pressure Systems Standard

[20] SANS 10100-2 The Structural Use of Concrete

[21] 25.1523521 Hendrina Power Station Common Plant Fire Water System P&ID (Sheet2)

[22] OTSU8C2-25 Hendrina Power Station Operating Technical Specifications – Normal Plant Operating Conditions – Fire Fighting System

[23] SANS 121 Hot Dip Galvanized Coatings on Fabricated Iron and Steel Articles - Specifications and Test Methods
[24] SANS 62 Steel Pipes
[25] SANS 719 Electric Welded Low Carbon Steel Pipes For Aqueous Fluids (Large Bore) Bore)
[26] SANS 10287 Automatic Sprinkler Installations For Fire-Fighting Purposes
[27] 240-86973501 Engineering Drawing Standard – Common Requirement
[28] SANS 1476 Fabricated Flanged Steel Pipework
[29] NFPA 15 Standard for Water Spray Fixed Systems for Fire Protection
[30] 240-65459834 Project Documentation Deliverable Requirement Specification
[31] 240-54179170 Technical Documentation Classification and Designation Standard
[32] 240-53114002 Engineering Change Management Procedure
[33] 240-53113685 Design Review Procedure
[34] 240-56227516 
LV Switchgear and Control Gear Assemblies and Associated Equipment For Voltage Up To and Including 1 000V AC and 1 500V AC
7.2 Informative

[35] SANS 10140 Identification Colour Marking: Identification of Hazards and Equipment In Work Situations

[36] 240-71432150 Plant Labelling Standard

[37] 240-105658000 Supplier Quality Management Specification
[38] 240-76992014 Project Plant Specific Technical Documents and Records Management Work Instruction
7.3 List of drawings 

7.3.1 Drawings issued by the Employer
This is the list of drawings issued by the Employer at or before the Contract Date and which apply to this contract.

Note:  Some drawings may contain both Works Information and Site Information.

	Drawing  number
	Revision
	Title

	N/a
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	


C3.2
Contractor’s Works Information

	This section of the Works Information will always be contract specific depending on the nature of the works.

It is most likely to be required for design and construct contracts where the tendering contractor will have proposed specifications and schedules for items of Plant and Materials and workmanship, which once accepted by the Employer prior to award of contract now become obligations of the Contractor per core clause 20.1.
Typical sub headings could be

a) 
Contractor’s design

b)
Plant and Materials specifications and schedules

c)
Other




This section could also be compiled as a separate file.




Part C3: Scope of Work
1
C3 ecc3 Cover page


