- TECHNICAL SPECIFICATION FOR PROTECTION RELAYS (preferable: P122, micom overcurrent and earth fault protection relays or similar)

- Power Supply Nominal auxiliary voltage:

- 48-250Vdc, or

- 48-240Vac

The protection relay must have the following functions;

| PROTECTION FUNCTIONS | ANSI CODE |
| --- | --- |
| Phase under/over voltage (AND & OR mode) | 27/59 |
| Directional Power (Under/Over act./react. power) | 32 |
| Wattmetric Earth Fault | 32N/67W |
| Undercurrent / Loss of load | 37 |
| Negative phase sequence overcurrent | 46 |
| Broken conductor | 46BC |
| Negative sequence overvoltage | 47 |
| Thermal overload | 49 |
| Earth overcurrent / Sensitive earth fault | 50N/51N |
| 3 Phase overcurrent | 50/51 |
| Circuit breaker failure | 50BF |
| Voltage controlled overcurrent | 51V |
| Residual over voltage / Derived Vo sequence overvoltage | 59N |
| Restricted earthfault | 64 |
| Earth fault directional overcurrent | 67N |
| 3 phase directional overcurrent | 67P |
| Wattmetric earthfault | 67W/32N |
| Autoreclose | 79 |
| Under/over frequency | 81O/U |
| Rate of change of Frequency (df/dt+t) | 81R |
| Output relay latching | 86 |
| CB command (local Open / Close) |  |
| Current transformer supervision | CTS |
| Switch on to fault | SOTF |
| Trip Circuit Supervision | TCS |
| Voltage transformer supervision | VTS/60 |
| Circuit breaker monitoring |  |
| Cold load pick-up | CLPU |
| Inrush blocking |  |

Table 1: protection relay functions

- TECHNICAL SPECIFICATION FOR ALARM ANNUNCIATOR:

Part Number:		             MOD93-170

Supply Voltage:		24V-35V DC

Inputs Voltage:		24V-35V DC

Outputs:			Relay, Potential Free.

Switches:			Test, Accept, Reset.

Terminal: 			1 (Left) t0 21 (Right)

- Description:

The alarm annunciator has 12 positive voltage triggered alarm inputs. Should any input triggered the alarm, its corresponding indicator will flash and a buzzer will sound the alarm. While the input voltage remains applied to the input, the indicator will flash fast. When the input voltage is removed, the indicator will flash slowly. All inputs are latched and will continue to be indicated even after a power failure.

Any input will activate the trigger relay and a Normally Open contact will close. This relay contact can be utilized by the user to his discretion.

Pressing the ‘Test’ button will apply the Power Supply Voltage to all inputs, Triggering them.

To shut up the buzzer, the ‘REMOTE RESET’ sequence can also be applied via two 24V remote inputs. The sequence and result is the same as when following the push-button sequence.

As long as ‘RESET’ or ‘REMOTE RESET’ is activated, a Reset Acknowledge relay will activate. Its Normally Open contact will close. This relay contact can be utilized by the user to his discretion.

- Terminal Description:

1 to 12:   Input 1 to Input 12.

13:           Remote Accept Input.

14:    	   Remote Rest Input

15:	   +24V Power Supply

16.17:     GND.

18.19:     Reset Relay Potential free contact.

20.21:     Trigger Relay Potential free contact.

# Bill of Quantities

| Area or Location | Bill of QUANTITY FOR BELLVILLE TRANSFORMER REPAIRS |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Description of Works | Quantity | Unit | Unit Price | Amount (excl. vat) |
| Prasa Western Cape | Supply and deliever | all | each |  |  |
|  | Protection Relays | 8 | each |  |  |
|  | Alarm annunciator | 2 | each |  |  |
| Total Cost (Excluding Vat) |  |  |  |  |  |
| Value Added Tax (Vat = 15%) |  |  |  |  |  |
| Total Cost (Including Vat) |  |  |  |  |  |

Table 2: Bill of Quantity