NEC3 Term Service Contract (TSC3)

| Between | NTCSA SOC Ltd (Reg No. 2021/539129/30) |  |
| --- | --- | --- |
| and | [Insert at award stage] (Reg No. ___________ ) |  |
| for | PROVISION OF HEATING, VENTILATION AND AIR CONDITIONING (HVAC) MAINTENANCE SERVICES FOR TRANSMISSION REAL ESTATE, NORTH EAST GRID (MPUMALANGA) ON AN AS AN WHEN REQUIRED BASIS |  |
| Contents: |  | No of pages |
| Part C1 | Agreements & Contract Data | [●] |
| Part C2 | Pricing Data | [●] |
| Part C3 | Scope of Work | [●] |
| CONTRACT No. | [Insert at award stage] |  |

PART C1:	AGREEMENTS & CONTRACT DATA

| Contents: |  | No of pages |
| --- | --- | --- |
| C1.1 | Form of Offer and Acceptance | [●] |
| C1.2a | Contract Data provided by the Employer | [●] |
| C1.2b | Contract Data provided by the Contractor ] | [●] |
| C1.3 | Proforma Guarantees | [●] |

C1.1 Form of Offer & Acceptance

## Offer

The Employer, identified in the Acceptance signature block, has solicited offers to enter into a contract for the procurement of:

Provision of Heating, Ventilation and Air Conditioning (HVAC) Maintenance services for Transmission Real Estate, North East Grid (Mpumalanga) for a period of 36 months

The tenderer, identified in the Offer signature block, has examined the documents listed in the Tender Data and addenda thereto and by submitting this Offer has accepted the Conditions of Tender.

By the representative of the tenderer, deemed to be duly authorised, signing this part of this Form of Offer and Acceptance the tenderer offers to perform all of the obligations and liabilities of the Contractor under the contract including compliance with all its terms and conditions according to their true intent and meaning for an amount to be determined in accordance with the conditions of contract identified in the Contract Data.

| Options A | The offered total of the Prices exclusive of VAT is | Rates based contract |
| --- | --- | --- |
|  | Value Added Tax @ 15% is | Rates based contract |
|  | The offered total of the amount due inclusive of VAT is | Rates based contract |
|  | (in words) Rates based contract |  |

This Offer may be accepted by the Employer by signing the Acceptance part of this Form of Offer and Acceptance and returning one copy of this document including the Schedule of Deviations (if any) to the tenderer before the end of the period of validity stated in the Tender Data, or other period as agreed, whereupon the tenderer becomes the party named as the Contractor in the conditions of contract identified in the Contract Data.

| Signature(s) |  |  |  |  |
| --- | --- | --- | --- | --- |
| Name(s) |  |  |  |  |
| Capacity |  |  |  |  |
| For the tenderer: |  |  |  |  |
| Name & signature of witness | (Insert name and address of organisation) |  | Date |  |
| Tenderer’s CIDB registration number: |  |  |  |  |

## Acceptance

By signing this part of this Form of Offer and Acceptance, the Employer identified below accepts the tenderer’s Offer.  In consideration thereof, the Employer shall pay the Contractor the amount due in accordance with the conditions of contract identified in the Contract Data.  Acceptance of the tenderer’s Offer shall form an agreement between the Employer and the tenderer upon the terms and conditions contained in this agreement and in the contract that is the subject of this agreement.

The terms of the contract, are contained in:

Part C1		Agreements and Contract Data, (which includes this Form of Offer and Acceptance)

Part C2		Pricing Data

Part C3		Scope of Work: Service Information

and drawings and documents (or parts thereof), which may be incorporated by reference into the above listed Parts.

Deviations from and amendments to the documents listed in the Tender Data and any addenda thereto listed in the Returnable Schedules as well as any changes to the terms of the Offer agreed by the tenderer and the Employer during this process of offer and acceptance, are contained in the Schedule of Deviations attached to and forming part of this Form of Offer and Acceptance.  No amendments to or deviations from said documents are valid unless contained in this Schedule.

The tenderer shall within two weeks of receiving a completed copy of this agreement, including the Schedule of Deviations (if any), contact the Employer’s agent (whose details are given in the Contract Data) to arrange the delivery of any securities, bonds, guarantees, proof of insurance and any other documentation to be provided in terms of the conditions of contract identified in the Contract Data at, or just after, the date this agreement comes into effect.  Failure to fulfil any of these obligations in accordance with those terms shall constitute a repudiation of this agreement.

Notwithstanding anything contained herein, this agreement comes into effect on the date when the tenderer receives one fully completed and signed original copy of this document, including the Schedule of Deviations (if any).

| Signature(s) |  |  |  |  |
| --- | --- | --- | --- | --- |
| Name(s) |  |  |  |  |
| Capacity |  |  |  |  |
| for the Employer |  |  |  |  |
| Name & signature of witness | (Insert name and address of organisation) |  | Date |  |

Note: If a tenderer wishes to submit alternative tenders, use another copy of this Form of Offer and Acceptance.

## Schedule of Deviations to be completed by the Employer prior to contract award

| No. | Subject | Details |
| --- | --- | --- |
| 1 | Not Applicable |  |
| 2 |  |  |
| 3 |  |  |
| 4 |  |  |
| 5 |  |  |
| 6 |  |  |
| 7 |  |  |

By the duly authorised representatives signing this Schedule of Deviations below, the Employer and the tenderer agree to and accept this Schedule of Deviations as the only deviations from and amendments to the documents listed in the Tender Data and any addenda thereto listed in the Tender Schedules, as well as any confirmation, clarification or changes to the terms of the Offer agreed by the tenderer and the Employer during this process of Offer and Acceptance.

It is expressly agreed that no other matter whether in writing, oral communication or implied during the period between the issue of the tender documents and the receipt by the tenderer of a completed signed copy of this Form shall have any meaning or effect in the contract between the parties arising from this Agreement.

|  | #### For the tenderer: |  | #### For the Employer |
| --- | --- | --- | --- |
| Signature |  |  |  |
| Name |  |  |  |
| Capacity |  |  |  |
| On behalf of | (Insert name and address of organisation) |  | (Insert name and address of organisation) |
| Name & signature of witness |  |  |  |
| Date |  |  |  |

C1.2 TSC3 Contract Data

# Part one - Data provided by the Employer

Completion of this data in full, according to the Options chosen, is essential to create a complete contract.

| Clause |  |  | ## Statement |  | ## Data |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 |  |  | ## General |  |  |  |  |  |  |
|  |  |  | The conditions of contract are the core clauses and the clauses for main Option: |  |  |  |  |  |  |
|  |  |  |  |  | A: Priced contract with price list |  |  |  |  |
|  |  |  | dispute resolution Option |  | W1: Dispute resolution procedure |  |  |  |  |
|  |  |  | and secondary Options |  |  |  |  |  |  |
|  |  |  |  |  | X1: Price adjustment for inflation X2: Changes in the law |  |  |  |  |
|  |  |  |  |  | X17: Low service damages |  |  |  |  |
|  |  |  |  |  | X18: Limitation of liability |  |  |  |  |
|  |  |  |  |  | X19: Task Order |  |  |  |  |
|  |  |  |  |  | Z: Additional conditions of contract |  |  |  |  |
|  |  |  | of the NEC3 Term Service Contract April 2013 (TSC3) |  | If 2005 Edition is to be used delete “April 2013” and replace with “June 2005 with amendments June 2006”. Always delete this note before finalising this Data |  |  |  |  |
| 10.1 |  |  | The Employer is (name): |  | NTCSA SOC Ltd (reg no: 2021/539129/30), a state owned company incorporated in terms of the company laws of the Republic of South Africa |  |  |  |  |
|  |  |  | Address |  | Registered office at Megawatt Park, Maxwell Drive, Sandton, Johannesburg |  |  |  |  |
| 10.1 |  |  | The Service Manager is (name): |  | TBC |  |  |  |  |
|  |  |  | Address |  | TBC |  |  |  |  |
|  |  |  | Tel |  | TBC |  |  |  |  |
|  |  |  | e-mail |  | TBC |  |  |  |  |
| 11.2(2) |  |  | The Affected Property is |  | Commercial buildings, depos and substations in various locations within the North East Grid in Mpumalanga |  |  |  |  |
| 11.2(13) |  |  | The service is |  | Provision of Heating, Ventilation and Air Conditioning (HVAC) Maintenance services for Transmission Real Estate, North East Grid (Mpumalanga), on an as and when required basis |  |  |  |  |
| 11.2(14) |  |  | The following matters will be included in the Risk Register |  | The risk register will be completed at each service interval and the Service Manager, and the Contractor will identify all possible risks. |  |  |  |  |
| 11.2(15) |  |  | The Service Information is in |  | Part 3: Scope of Work and all documents and drawings to which it makes reference. |  |  |  |  |
| 12.2 |  |  | The law of the contract is the law of |  | the Republic of South Africa |  |  |  |  |
| 13.1 |  |  | The language of this contract is |  | English |  |  |  |  |
| 13.3 |  |  | The period for reply is |  | One (1) week |  |  |  |  |
| ## 2 |  |  | ## The Contractor’s main responsibilities |  | Data required by this section of the core clauses is also provided by the Contractor in Part 2 and terms in italics used in this section are identified elsewhere in this Contract Data |  |  |  |  |
| 21.1 |  |  | The Contractor submits a first plan for acceptance within |  | Two (2) weeks of the Contract Date |  |  |  |  |
| ## 3 |  |  | ## Time |  |  |  |  |  |  |
| 30.1 |  |  | The starting date is. |  | TBC |  |  |  |  |
| 30.1 |  |  | The service period is |  | 36 Months |  |  |  |  |
| ## 4 |  |  | ## Testing and defects |  | ## There is no reference to Contract Data in this section of the core clauses and terms in italics used in this section are identified elsewhere in this Contract Data |  |  |  |  |
| ## 5 |  |  | ## Payment |  |  |  |  |  |  |
| 50.1 |  |  | The assessment interval is |  | between the 25th day of each successive month. |  |  |  |  |
| 51.1 |  |  | The currency of this contract is the |  | South African Rand |  |  |  |  |
| 51.2 |  |  | The period within which payments are made is |  | Four (4) weeks. |  |  |  |  |
| 51.4 |  |  | The interest rate is |  | the publicly quoted prime rate of interest (calculated on a 365 day year) charged by from time to time by the Standard Bank of South Africa Limited (as certified, in the event of any dispute, by any manager of such bank, whose appointment it shall not be necessary to prove) for amounts due in Rands and (ii) the LIBOR rate applicable at the time for amounts due in other currencies. LIBOR is the 6 month London Interbank Offered Rate quoted under the caption “Money Rates” in The Wall Street Journal for the applicable currency or if no rate is quoted for the currency in question then the rate for United States Dollars, and if no such rate appears in The Wall Street Journal then the rate as quoted by the Reuters Monitor Money Rates Service (or such service as may replace the Reuters Monitor Money Rates Service) on the due date for the payment in question, adjusted mutatis mutandis every 6 months thereafter (and as certified, in the event of any dispute, by any manager employed in the foreign exchange department of The Standard Bank of South Africa Limited, whose appointment it shall not be necessary to prove. |  |  |  |  |
| ## 6 |  |  | ## Compensation events |  | There is no reference to Contract Data in this section of the core clauses and terms in italics used in this section are identified elsewhere in this Contract Data |  |  |  |  |
| ## 7 |  |  | ## Use of Equipment Plant and Materials |  | ## No provision made on the contract to provide equipment plant and material to the Contractor. |  |  |  |  |
| ## 8 |  |  | ## Risks and insurance |  |  |  |  |  |  |
| 80.1 |  |  | These are additional Employer's risks |  | None |  |  |  |  |
| ## 9 |  |  | ## Termination |  | A termination process provided in Sub-clause 90.2 of the NEC document sets out the rights of the terminating Party, Employer or Contractor for the various reasons given; the procedure to be followed; and the amount due after termination if there is any and as per Z10 of Z Clauses below |  |  |  |  |
| ## 10 |  |  | ## Data for main Option clause |  |  |  |  |  |  |
| A |  |  | Priced contract with price list |  |  |  |  |  |  |
| 20.5 |  |  | The Contractor prepares forecasts of the final total of the Prices for the whole of the service at intervals no longer than |  | Four (4) weeks. |  |  |  |  |
| ## 11 |  |  | ## Data for Option W1 |  |  |  |  |  |  |
| W1.1 |  |  | The Adjudicator |  | the person selected from the ICE-SA Division (or its successor body) of the South African Institution of Civil Engineering Panel of Adjudicators by the Party intending to refer a dispute to him. (see www.ice-sa.org.za). If the Parties do not agree on an Adjudicator the Adjudicator will be appointed by the Arbitration Foundation of Southern Africa (AFSA). |  |  |  |  |
| W1.2(3) |  |  | The Adjudicator nominating body is: |  | the Chairman of ICE-SA a joint Division of the South African Institution of Civil Engineering and the Institution of Civil Engineers (London) (see www.ice-sa.org.za ) or its successor body. |  |  |  |  |
| W1.4(2) |  |  | The tribunal is: |  | arbitration |  |  |  |  |
| W1.4(5) |  |  | The arbitration procedure is |  | the latest edition of Rules for the Conduct of Arbitrations published by The Association of Arbitrators (Southern Africa) or its successor body. |  |  |  |  |
|  |  |  | The place where arbitration is to be held is |  | Johannesburg South Africa |  |  |  |  |
|  |  |  | The person or organisation who will choose an arbitrator - if the Parties cannot agree a choice or - if the arbitration procedure does not state who selects an arbitrator, is |  | the Chairman for the time being or his nominee of the Association of Arbitrators (Southern Africa) or its successor body. |  |  |  |  |
| ## 12 |  |  | ## Data for secondary Option clauses |  |  |  |  |  |  |
| X1 |  |  | Price adjustment for inflation |  |  |  |  |  |  |
| X1.1 |  |  | The base date for indices is |  | The rates will be fixed and firm for 12 months from start date, thereafter CPA escalation will apply annually for second and third year |  |  |  |  |
|  |  |  | The proportions used to calculate the Price Adjustment Factor are: |  | proportion | linked to index for | Index prepared by |  |  |
|  |  |  | *(Tenderer to propose the elements and proportion) |  | 0.00 | CPI |  |  |  |
|  |  |  |  |  | 0.00 | non-adjustable |  |  |  |
|  |  |  |  |  | 1.00 |  |  |  |  |
| X2 |  |  | Changes in the law |  | There is no reference to Contract Data in this Option and terms in italics are identified elsewhere in this Contract Data. |  |  |  |  |
| X17 |  |  | Low service damages |  |  |  |  |  |  |
| X17.1 |  |  | The service level table is in |  | Annexure A in the Service Information |  |  |  |  |
| X18 |  |  | Limitation of liability |  |  |  |  |  |  |
| X18.1 |  |  | The Contractor’s liability to the Employer for indirect or consequential loss is limited to |  | R0.0 (zero Rand) |  |  |  |  |
| X18.2 |  |  | For any one event, the Contractor’s liability to the Employer for loss of or damage to the Employer’s property is limited to |  | the amount of the deductibles relevant to the event |  |  |  |  |
| X18.3 |  |  | The Contractor’s liability for Defects due to his design of an item of Equipment is limited to |  | The greater of - the total of the Prices at the Contract Date and - the amounts excluded and unrecoverable from the Employer’s insurance (other than the resulting physical damage to the Employer’s property which is not excluded) plus the applicable deductibles |  |  |  |  |
| X18.4 |  |  | The Contractor’s total liability to the Employer, for all matters arising under or in connection with this contract, other than the excluded matters, is limited to |  | the total of the Prices other than for the additional excluded matters. The Contractor’s total liability for the additional excluded matters is not limited. The additional excluded matters are amounts for which the Contractor is liable under this contract for - Defects due to his design, plan and specification, - Defects due to manufacture and fabrication outside the Affected Property, - loss of or damage to property (other than the Employer’s property, Plant and Materials), - death of or injury to a person and - infringement of an intellectual property right. |  |  |  |  |
| X18.5 |  |  | The end of liability date is |  | Six (6) months after the end of the service period. |  |  |  |  |
| X19 |  |  | Task Order |  |  |  |  |  |  |
| X19.5 |  |  | The Contractor submits a Task Order programme to the Service Manager within |  | 2 – 3 days of receiving the Task Order |  |  |  |  |
| Z |  |  | The additional conditions of contract are |  | Z1 to Z14 always apply. |  |  |  |  |
| Z1 |  | Cession delegation and assignment |  |  |  |  |  |  |  |
| Z1.1 |  | The Contractor does not cede, delegate or assign any of its rights or obligations to any person without the written consent of the Employer. |  |  |  |  |  |  |  |
| Z1.2 |  | Notwithstanding the above, the Employer may on written notice to the Contractor cede and delegate its rights and obligations under this contract to any of its subsidiaries or any of its present divisions or operations which may be converted into separate legal entities as a result of the restructuring of the Electricity Supply Industry. |  |  |  |  |  |  |  |
| Z2 |  | Joint ventures |  |  |  |  |  |  |  |
| Z2.1 |  | If the Contractor constitutes a joint venture, consortium or other unincorporated grouping of two or more persons or organisations then these persons or organisations are deemed to be jointly and severally liable to the Employer for the performance of this contract. |  |  |  |  |  |  |  |
| Z2.2 |  | Unless already notified to the Employer, the persons or organisations notify the Service Manager within two weeks of the Contract Date of the key person who has the authority to bind the Contractor on their behalf. |  |  |  |  |  |  |  |
| Z2.3 |  | The Contractor does not alter the composition of the joint venture, consortium or other unincorporated grouping of two or more persons without the consent of the Employer having been given to the Contractor in writing. |  |  |  |  |  |  |  |
| Z3 |  |  | Change of Broad Based Black Economic Empowerment (B-BBEE) status |  |  |  |  |  |  |
| Z3.1 |  |  | Where a change in the Contractor’s legal status, ownership or any other change to his business composition or business dealings results in a change to the Contractor’s B-BBEE status, the Contractor notifies the Employer within seven days of the change. |  |  |  |  |  |  |
| Z3.2 |  |  | The Contractor is required to submit an updated verification certificate and necessary supporting documentation confirming the change in his B-BBEE status to the Service Manager within thirty days of the notification or as otherwise instructed by the Service Manager. |  |  |  |  |  |  |
| Z3.3 |  |  | Where, as a result, the Contractor’s B-BBEE status has decreased since the Contract Date the Employer may either re-negotiate this contract or alternatively, terminate the Contractor’s obligation to Provide the Service. |  |  |  |  |  |  |
| Z3.4 |  |  | Failure by the Contractor to notify the Employer of a change in its B-BBEE status may constitute a reason for termination. If the Employer terminates in terms of this clause, the procedures on termination are P1, P2 and P4 as stated in clause 92, and the amount due is A1 and A3 as stated in clause 93. |  |  |  |  |  |  |
| Z4 |  | Confidentiality |  |  |  |  |  |  |  |
| Z4.1 |  | The Contractor does not disclose or make any information arising from or in connection with this contract available to Others. This undertaking does not, however, apply to information which at the time of disclosure or thereafter, without default on the part of the Contractor, enters the public domain or to information which was already in the possession of the Contractor at the time of disclosure (evidenced by written records in existence at that time). Should the Contractor disclose information to Others in terms of clause 25.1, the Contractor ensures that the provisions of this clause are complied with by the recipient. |  |  |  |  |  |  |  |
| Z4.2 |  | If the Contractor is uncertain about whether any such information is confidential, it is to be regarded as such until notified otherwise by the Service Manager. |  |  |  |  |  |  |  |
| Z4.3 |  | In the event that the Contractor is, at any time, required by law to disclose any such information which is required to be kept confidential, the Contractor, to the extent permitted by law prior to disclosure, notifies the Employer so that an appropriate protection order and/or any other action can be taken if possible, prior to any disclosure. In the event that such protective order is not, or cannot, be obtained, then the Contractor may disclose that portion of the information which it is required to be disclosed by law and uses reasonable efforts to obtain assurances that confidential treatment will be afforded to the information so disclosed. |  |  |  |  |  |  |  |
| Z4.4 |  | The taking of images (whether photographs, video footage or otherwise) of the Affected Property or any portion thereof, in the course of Providing the Service and after the end of the service period, requires the prior written consent of the Service Manager. All rights in and to all such images vests exclusively in the Employer. |  |  |  |  |  |  |  |
| Z4.5 |  | The Contractor ensures that all his subcontractors abide by the undertakings in this clause. |  |  |  |  |  |  |  |
| Z5 |  | Waiver and estoppel: Add to core clause 12.3: |  |  |  |  |  |  |  |
| Z5.1 |  | Any extension, concession, waiver or relaxation of any action stated in this contract by the Parties, the Service Manager or the Adjudicator does not constitute a waiver of rights, and does not give rise to an estoppel unless the Parties agree otherwise and confirm such agreement in writing. |  |  |  |  |  |  |  |
| Z6 |  |  | Health, safety and the environment: Add to core clause 27.4 |  |  |  |  |  |  |
| Z6.1 |  |  | The Contractor undertakes to take all reasonable precautions to maintain the health and safety of persons in and about the execution of the service. Without limitation the Contractor: - accepts that the Employer may appoint him as the “Principal Contractor” (as defined and provided for under the Construction Regulations 2014 (promulgated under the Occupational Health & Safety Act 85 of 1993) (“the Construction Regulations”) for the Affected Property; - warrants that the total of the Prices as at the Contract Date includes a sufficient amount for proper compliance with the Construction Regulations, all applicable health & safety laws and regulations and the health and safety rules, guidelines and procedures provided for in this contract and generally for the proper maintenance of health & safety in and about the execution of the service; and - undertakes, in and about the execution of the service, to comply with the Construction Regulations and with all applicable health & safety laws and regulations and rules, guidelines and procedures otherwise provided for under this contract and ensures that his Subcontractors, employees and others under the Contractor’s direction and control, likewise observe and comply with the foregoing. |  |  |  |  |  |  |
| Z6.2 |  |  | The Contractor, in and about the execution of the service, complies with all applicable environmental laws and regulations and rules, guidelines and procedures otherwise provided for under this contract and ensures that his Subcontractors, employees and others under the Contractor’s direction and control, likewise observe and comply with the foregoing. |  |  |  |  |  |  |
| Z7 |  | Provision of a Tax Invoice and interest. Add to core clause 51 |  |  |  |  |  |  |  |
| Z7.1 |  | Within one week of receiving a payment certificate from the Service Manager in terms of core clause 51.1, the Contractor provides the Employer with a tax invoice in accordance with the Employer's procedures stated in the Service Information, showing the amount due for payment equal to that stated in the payment certificate. |  |  |  |  |  |  |  |
| Z7.2 |  | If the Contractor does not provide a tax invoice in the form and by the time required by this contract, the time by when the Employer is to make a payment is extended by a period equal in time to the delayed submission of the correct tax invoice. Interest due by the Employer in terms of core clause 51.2 is then calculated from the delayed date by when payment is to be made. |  |  |  |  |  |  |  |
| Z7.3 |  | The Contractor (if registered in South Africa in terms of the companies Act) is required to comply with the requirements of the Value Added Tax Act, no 89 of 1991 (as amended) and to include the Employer’s VAT number 4710303126 on each invoice he submits for payment. |  |  |  |  |  |  |  |
| Z8 |  | Notifying compensation events |  |  |  |  |  |  |  |
| Z8.1 |  | Delete the last paragraph of core clause 61.3 and replace with: If the Contractor does not notify a compensation event within eight weeks of becoming aware of the event, he is not entitled to a change in the Prices. |  |  |  |  |  |  |  |
| Z9 |  | Employer’s limitation of liability |  |  |  |  |  |  |  |
| Z9.1 |  | The Employer’s liability to the Contractor for the Contractor’s indirect or consequential loss is limited to R0.00 (zero Rand) |  |  |  |  |  |  |  |
| Z9.2 |  | The Contractor’s entitlement under the indemnity in 82.1 is provided for in 60.1(12) and the Employer’s liability under the indemnity is limited to compensation as provided for in core clause 63 and X19.11 if Option X19 Task Order applies to this contract. |  |  |  |  |  |  |  |
| Z10 |  | Termination: Add to core clause 91.1, at the second main bullet point, fourth sub-bullet point, after the words "against it": |  |  |  |  |  |  |  |
| Z10.1 |  | or had a business rescue order granted against it. |  |  |  |  |  |  |  |
| Z11 | Ethics |  |  |  |  |  |  |  |  |
| For the purposes of this Z-clause, the following definitions apply: |  |  |  |  |  |  |  |  |  |
| Affected Party |  |  |  | means, as the context requires, any party, irrespective of whether it is the Contractor or a third party, such party’s employees, agents, or Subcontractors or Subcontractor’s employees, or any one or more of all of these parties’ relatives or friends, |  |  |  |  |  |
| Coercive Action |  |  |  | means to harm or threaten to harm, directly or indirectly, an Affected Party or the property of an Affected Party, or to otherwise influence or attempt to influence an Affected Party to act unlawfully or illegally, |  |  |  |  |  |
| Collusive Action |  |  |  | means where two or more parties co-operate to achieve an unlawful or illegal purpose, including to influence an Affected Party to act unlawfully or illegally, |  |  |  |  |  |
| Committing Party |  |  |  | means, as the context requires, the Contractor, or any member thereof in the case of a joint venture, or its employees, agents, or Subcontractors or the Subcontractor’s employees, |  |  |  |  |  |
| Corrupt Action |  |  |  | means the offering, giving, taking, or soliciting, directly or indirectly, of a good or service to unlawfully or illegally influence the actions of an Affected Party, |  |  |  |  |  |
| Fraudulent Action |  |  |  | means any unlawfully or illegally intentional act or omission that misleads, or attempts to mislead, an Affected Party, in order to obtain a financial or other benefit or to avoid an obligation or incurring an obligation, |  |  |  |  |  |
| Obstructive Action |  |  |  | means a Committing Party unlawfully or illegally destroying, falsifying, altering or concealing information or making false statements to materially impede an investigation into allegations of Prohibited Action, and |  |  |  |  |  |
| Prohibited Action |  |  |  | means any one or more of a Coercive Action, Collusive Action Corrupt Action, Fraudulent Action or Obstructive Action. |  |  |  |  |  |
| Z11.1 | A Committing Party may not take any Prohibited Action during the course of the procurement of this contract or in execution thereof. |  |  |  |  |  |  |  |  |
| Z11.2 | The Employer may terminate the Contractor’s obligation to Provide the Services if a Committing Party has taken such Prohibited Action and the Contractor did not take timely and appropriate action to prevent or remedy the situation, without limiting any other rights or remedies the Employer has. It is not required that the Committing Party had to have been found guilty, in court or in any other similar process, of such Prohibited Action before the Employer can terminate the Contractor’s obligation to Provide the Services for this reason. |  |  |  |  |  |  |  |  |
| Z11.3 | If the Employer terminates the Contractor’s obligation to Provide the Services for this reason, the amounts due on termination are those intended in core clauses 92.1 and 92.2. |  |  |  |  |  |  |  |  |
| Z11.4 | A Committing Party co-operates fully with any investigation pursuant to alleged Prohibited Action. Where the Employer does not have a contractual bond with the Committing Party, the Contractor ensures that the Committing Party co-operates fully with an investigation. |  |  |  |  |  |  |  |  |

Z12		Insurance

Z _12_.1	Replace core clause 83 with the following:

| Insurance cover | 83 |  |
| --- | --- | --- |
|  | 83.1 | When requested by a Party, the other Party provides certificates from his insurer or broker stating that the insurances required by this contract are in force. |
|  | 83.2 | The Contractor provides the insurances stated in the Insurance Table A from the starting date until the earlier of Completion and the date of the termination certificate. INSURANCE TABLE A Insurance against; Minimum amount of cover or minimum limit of indemnity. Loss of or damage caused by the Contractor to the Employer’s property; The replacement cost where not covered by the Employer’s insurance. The Employer’s policy deductible as at Contract Date, where covered by the Employer’s insurance.. Loss of or damage to Plant and Materials; The replacement cost where not covered by the Employer’s insurance. The Employer’s policy deductible as at Contract Date, where covered by the Employer’s insurance.. Loss of or damage to Equipment; The replacement cost where not covered by the Employer’s insurance. The Employer’s policy deductible as at Contract Date, where covered by the Employer’s insurance.. The Contractor’s liability for loss of or damage to property (except the Employer’s property, Plant and Materials and Equipment) and liability for bodily injury to or death of a person (not an employee of the Contractor) arising from or in connection with the Contractor’s Providing the Service; Loss of or damage to property The replacement cost Bodily injury to or death of a person The amount required by the applicable law.. Liability for death of or bodily injury to employees of the Contractor arising out of and in the course of their employment in connection with this contract; The amount required by the applicable law.. |

Z __12.2	Replace core clause 86 with the following:

| Insurance by the Employer | 86 |  |
| --- | --- | --- |
|  | 86.1 | The Employer provides the insurances stated in the Insurance Table B |
|  |  | INSURANCE TABLE B Insurance against or name of policy; Minimum amount of cover or minimum limit of indemnity. Assets All Risk; Per the insurance policy document. Contract Works insurance; Per the insurance policy document. Environmental Liability; Per the insurance policy document. General and Public Liability; Per the insurance policy document. Transportation (Marine); Per the insurance policy document. Motor Fleet and Mobile Plant; Per the insurance policy document. Terrorism; Per the insurance policy document. Cyber Liability; Per the insurance policy document. Nuclear Material Damage and Business Interruption; Per the insurance policy document. Nuclear Material Damage Terrorism; Per the insurance policy document. |

| Z13 | Nuclear Liability |  |
| --- | --- | --- |
| Z13.1 | The Employer is the operator of the Koeberg Nuclear Power Station (KNPS), a nuclear installation, as designated by the National Nuclear Regulator of the Republic of South Africa, and is the holder of a nuclear licence in respect of the KNPS. |  |
| Z13.2 | The Employer is solely responsible for and indemnifies the Contractor or any other person against any and all liabilities which the Contractor or any person may incur arising out of or resulting from nuclear damage, as defined in Act 47 of 1999, save to the extent that any liabilities are incurred due to the unlawful intent of the Contractor or any other person or the presence of the Contractor or that person or any property of the Contractor or such person at or in the KNPS or on the KNPS site, without the permission of the Employer or of a person acting on behalf of the Employer. |  |
| Z13.3 | Subject to clause Z13.4 below, the Employer waives all rights of recourse, arising from the aforesaid, save to the extent that any claims arise or liability is incurred due or attributable to the unlawful intent of the Contractor or any other person, or the presence of the Contractor or that person or any property of the Contractor or such person at or in the KNPS or on the KNPS site, without the permission of the Employer or of a person acting on behalf of the Employer. |  |
| Z13.4 | The Employer does not waive its rights provided for in section 30 (7) of Act 47 of 1999, or any replacement section dealing with the same subject matter. |  |
| Z13.5 | The protection afforded by the provisions hereof shall be in effect until the KNPS is decommissioned. |  |
| Z14 | Asbestos |  |
| For the purposes of this Z-clause, the following definitions apply: |  |  |
| AAIA |  | means approved asbestos inspection authority. |
| ACM |  | means asbestos containing materials. |
| AL |  | means action level, i.e. a level of 50% of the OEL, i.e. 0.1 regulated asbestos fibres per ml of air measured over a 4 hour period. The value at which proactive actions is required in order to control asbestos exposure to prevent exceeding the OEL. |
| Ambient Air |  | means breathable air in area of work with specific reference to breathing zone, which is defined to be a virtual area within a radius of approximately 30cm from the nose inlet. |
| Compliance Monitoring |  | means compliance sampling used to assess whether or not the personal exposure of workers to regulated asbestos fibres is in compliance with the Standard’s requirements for safe processing, handling, storing, disposal and phase-out of asbestos and asbestos containing material, equipment and articles. |
| OEL |  | means occupational exposure limit. |
| Parallel Measurements |  | means measurements performed in parallel, yet separately, to existing measurements to verify validity of results. |
| Safe Levels |  | means airborne asbestos exposure levels conforming to the Standard’s requirements for safe processing, handling, storing, disposal and phase-out of asbestos and asbestos containing material, equipment and articles. |
| Standard |  | means the Employer’s Asbestos Standard 32-303: Requirements for Safe Processing, Handling, Storing, Disposal and Phase-out of Asbestos and Asbestos Containing Material, Equipment and Articles. |
| SANAS |  | means the South African National Accreditation System. |
| TWA |  | means the average exposure, within a given workplace, to airborne asbestos fibres, normalised to the baseline of a 4 hour continuous period, also applicable to short term exposures, i.e. 10-minute TWA. |
| Z14.1 | The Employer ensures that the Ambient Air in the area where the Contractor will Provide the Services conforms to the acceptable prescribed South African standard for asbestos, as per the regulations published in GNR 155 of 10 February 2002, under the Occupational Health and Safety Act, 1993 (Act 85 of 1993) (“Asbestos Regulations”). The OEL for asbestos is 0.2 regulated asbestos fibres per millilitre of air as a 4-hour TWA, averaged over any continuous period of four hours, and the short term exposure limit of 0.6 regulated asbestos fibres per millilitre of air as a 10-minute TWA, averaged over any 10 minutes, measured in accordance with HSG248 and monitored according to HSG173 and OESSM. |  |
| Z14.2 | Upon written request by the Contractor, the Employer certifies that these conditions prevail. All measurements and reporting are effected by an independent, competent, and certified occupational hygiene inspection body, i.e. a SANAS accredited and Department of Employment and Labour approved AAIA. The Contractor may perform Parallel Measurements and related control measures at the Contractor’s expense. For the purposes of compliance the results generated from Parallel Measurements are evaluated only against South African statutory limits as detailed in clause Z14.1. Control measures conform to the requirements stipulated in the AAIA-approved asbestos work plan. |  |
| Z14.3 | The Employer manages asbestos and ACM according to the Standard. |  |
| Z14.4 | In the event that any asbestos is identified while Providing the Services, a risk assessment is conducted and if so required, with reference to possible exposure to an airborne concentration of above the AL for asbestos, immediate control measures are implemented and relevant air monitoring conducted in order to declare the area safe. |  |
| Z14.5 | The Contractor’s personnel are entitled to stop working and leave the contaminated area forthwith until such time that the area of concern is declared safe by either Compliance Monitoring or an AAIA approved control measure intervention, for example, per the emergency asbestos work plan, if applicable. |  |
| Z14.6 | The Contractor continues to Provide the Services, without additional control measures presented, on presentation of Safe Levels. The contractually agreed dates to Provide the Services, including the Completion Date, are adjusted accordingly. The contractually agreed dates are extended by the notification periods required by regulations 3 and 21 of the Asbestos Regulations, 2001. |  |
| Z14.7 | Any removal and disposal of asbestos, asbestos containing materials and waste, is done by a registered asbestos contractor, instructed by the Employer at the Employer’s expense, and conducted in line with South African legislation. |  |

C1.2 Contract Data

# Part two - Data provided by the Contractor

Completion of the data in full, according to Options chosen, is essential to create a complete contract.

| ## Clause | ## Statement | ## Data |
| --- | --- | --- |
| 10.1 | The Contractor is (Name): |  |
|  | Address |  |
|  | Tel No. |  |
|  | Fax No. |  |
| 11.2(8) | The direct fee percentage is |  |
|  | The subcontracted fee percentage is |  |
| 11.2(14) | The following matters will be included in the Risk Register |  |
| 11.2(15) | The Service Information for the Contractor’s plan is in: |  |
| 21.1 | The plan identified in the Contract Data is contained in: |  |
| 24.1 | The key people are: |  |
|  | 1 Name: |  |
|  | Job: |  |
|  | Responsibilities: |  |
|  | Qualifications: |  |
|  | Experience: |  |
|  | 2 Name: |  |
|  | Job |  |
|  | Responsibilities: |  |
|  | Qualifications: |  |
|  | Experience: |  |
|  |  | CV's (and further key person's data including CVs) are in |
| A | Priced contract with price list |  |
| 11.2(12) | The price list is in | C2.2 |
| 11.2(19) | The tendered total of the Prices is | Rates based contract |

Part 2: Pricing Data

TSC3 Option A

| Document reference | Title | No of pages |
| --- | --- | --- |
| C2.1 | Pricing assumptions: Option A | 2 |
| C2.2 | The price list | 1 |

C2.1 Pricing assumptions: Option A

# How work is priced and assessed for payment

Clause 11 in NEC3 Term Service Contract (TSC3) core clauses and Option A states:

| Identified and defined terms | 11 11.2 | (12) The Price List is the price list unless later changed in accordance with this contract. |
| --- | --- | --- |
|  |  | (17) The Price for Services Provided to Date is the total of - the Price for each lump sum item in the Price List which the Contractor has completed and - where a quantity is stated for an item in the Price List, an amount calculated by multiplying the quantity which the Contractor has completed by the rate. |
|  |  | (19) The Prices are the amounts stated in the Price column of the Price List. Where a quantity is stated for an item in the Price List, the Price is calculated by multiplying the quantity by the rate. |

This confirms that Option A is a priced contract where the Prices are derived from a list of items of service which can be priced as lump sums or as expected quantities of service multiplied by a rate or a mix of both.

# Function of the Price List

Clause 54.1 in Option A states: “Information in the Price List is not Service Information”.  This confirms that instructions to do work or how it is to be done are not included in the Price List but in the Service Information.  This is further confirmed by Clause 20.1 which states, “The Contractor Provides the Service in accordance with the Service Information”. Hence the Contractor does not Provide the Service in accordance with the Price List.   The Price List is only a pricing document.

# Link to the Contractor’s plan

Clause 21.4 states “The Contractor provides information which shows how each item description on the Price List relates to the operations on each plan which he submits for acceptance”.  Hence when compiling the price list, the tendering contractor needs to develop his first clause 21.2 plan in such a way that operations shown on it can be priced in the price list  and result in a satisfactory cash flow in terms of clause 11.2(17).

# Preparing the price list

Before preparing the price list, both the Employer and tendering contractors should read the TSC3 Guidance Notes pages 14 and 15.  In an Option A contract, either Party may have entered items into the price list either as a process of offer and acceptance (tendering) or by negotiation depending on the nature of the service to be provided.  Alternatively the Employer, in his Instructions to Tenderers or in a Tender Schedule, may have listed some items that he requires the Contractor to include in the price list to be prepared and priced by him.

It is assumed that in preparing or finalising the price list the Contractor:

- Has taken account of the guidance given in the TSC3 Guidance Notes relevant to Option A;

- Understands the function of the Price List and how work is priced and paid for;

- Is aware of the need to link operations shown in his plan to items shown in the Price List;

- Has listed and priced items in the price list which are inclusive of everything necessary and incidental to Providing the Service in accordance with the Service Information, as it was at the time of tender, as well as correct any Defects not caused by an Employer’s risk;

- Has priced work he decides not to show as a separate item within the Prices or rates of other listed items in order to fulfil the obligation to complete the service for the tendered total of the Prices.

- Understands there is no adjustment to items priced as lump sums if the amount, or quantity, of work within that item later turns out to be different to that which the Contractor estimated at time of tender. The only basis for a change to the (lump sum) Prices is as a result of a compensation event.

## Format of the price list

(From the example given in an Appendix within the TSC3 Guidance Notes)

Entries in the first four columns in the price list in section C2.2 are made either by the Employer or the tendering contractor.

If the Contractor is to be paid an amount for the item which is not adjusted if the quantity of work in the item changes, the tendering contractor enters the amount in the Price column only, the Unit, Expected Quantity and Rate columns being left blank.

If the Contractor is to be paid an amount for an item of work which is the rate for the work multiplied by the quantity completed, the tendering contractor enters the rate which is then multiplied by the Expected Quantity to produce the Price, which is also entered.

If the Contractor is to be paid a Price for an item proportional to the length of time for which a service is provided, a unit of time is stated in the Unit column and the expected length of time (as a quantity of the stated units of time) is stated in the Expected Quantity column.

C2.2 the price list

| Item no. | Bill Description | Unit | Rate |
| --- | --- | --- | --- |
| SECTION NO. 1 |  |  |  |
| SHE Schedule |  |  |  |
| 1. | SHE Requirements and Compliance |  |  |
| SECTION NO. 2 |  |  |  |
| 1. Work to be done from Monday to Friday between 7:30am and 4pm: |  |  |  |
| 1.1 | Project coordinator/ Senior supervisor | Hour |  |
| 1.2 | Mechanical Artisan | Hour |  |
| 1.3 | Semi-skilled worker | Hour |  |
| 2. Work to be done from Monday to Friday after 4pm: |  |  |  |
| 2.1 | Project coordinator/ Senior supervisor | Hour |  |
| 2.2 | Mechanical Artisan | Hour |  |
| 2.3 | Semi-skilled worker | Hour |  |
| 3. Work to be done on Saturdays between 7:30am and 4pm: |  |  |  |
| 3.1 | Project coordinator/ Senior supervisor | Hour |  |
| 3.2 | Mechanical Artisan | Hour |  |
| 3.3 | Semi-skilled worker | Hour |  |
| 4. Work to be done on Sunday and public holidays between 7:30am and 4pm: |  |  |  |
| 4.1 | Project coordinator/ Senior supervisor | Hour |  |
| 4.2 | Mechanical Artisan | Hour |  |
| 4.3 | Semi-skilled worker | Hour |  |
| 5. Materials |  |  |  |
| 5.1 | Provisional sum for the supply of required material according to PM's instruction of compressors, pc boards, fan motors, filters, contactors, overloads, circuit breakers, isolators, relays, copper piping, insulation, pump couplings, oil (compressors or pumps), fan belts, bearings, fuses, controllers, timers, PLC, plumbing fittings, humidifiers bottles, drain pumps and refrigerants and etc. | Sum |  |
| 5.2 | Mark up fee percentage | % | % |
| 6. Transport |  |  |  |
| Payment for transport/traveling will be paid in excess of 50Km from the CLN office/depo that the site falls under (see list of sites and applicable CLNs). |  |  |  |
| 6.1 | Cost of transport/ travelling | KM | R |

Part 3: Scope of Work

| Document reference | Title | No of pages |
| --- | --- | --- |
|  | This cover page | 1 |
| C3.1 | Employer’s Service Information | 20 |
|  | Total number of pages | 21 |

C3.1: Employer’s service Information

Contents

Part 3: Scope of Work	1

C3.1: Employer’s service Information	2

1	Description of the service	4

1.1	Executive overview	4

1.2	Employer’s requirements for the service	4

1.4	Interpretation and terminology	9

2	Management strategy and start up.	10

2.1	The Contractor’s plan for the service	10

2.2	Management meetings	10

2.3	Contractor’s management, supervision and key people	11

2.4	Provision of bonds and guarantees.	11

2.5	Documentation control	11

2.6	Invoicing and payment	12

2.7	Contract change management.	13

2.8	Records of Defined Cost to be kept by the Contractor	13

2.9	Insurance provided by the Employer	13

2.10	Training workshops and technology transfer	13

2.11	Design and supply of Equipment	13

2.12	Things provided at the end of the service period for the Employer’s use	14

2.12.1	Equipment	14

2.12.2	Information and other things	14

2.13	Management of work done by Task Order	14

3	Health and safety, the environment and quality assurance	14

3.1	Health and safety risk management	14

3.2	Environmental constraints and management	15

3.3	Quality assurance requirements	15

4	Procurement	15

4.1	People	15

4.1.1	Minimum requirements of people employed.	15

4.1.2	BBBEE and preferencing scheme	15

4.2	Subcontracting	16

4.2.1	Preferred subcontractors	16

4.2.2	Subcontract documentation, and assessment of subcontract tenders	16

4.2.3	Limitations on subcontracting	16

4.2.4	Attendance on subcontractors	16

4.3	Plant and Materials	16

4.3.1	Specifications	16

4.3.2	Correction of defects	17

4.3.3	Contractor’s procurement of Plant and Materials	17

4.3.4	Tests and inspections before delivery	17

4.3.5	Plant & Materials provided “free issue” by the Employer	17

4.3.6	Cataloguing requirements by the Contractor	17

5	Working on the Affected Property	17

5.1	Employer’s site entry and security control, permits, and site regulations	17

5.2	People restrictions, hours of work, conduct and records	17

5.3	Health and safety facilities on the Affected Property	18

5.4	Environmental controls, fauna & flora	18

5.5	Records of Contractor’s Equipment	18

5.6	Equipment provided by the Employer	18

5.7	Site services and facilities	18

5.7.1	Provided by the Employer.	18

5.7.2	Provided by the Contractor	18

5.8	Control of noise, dust, water and waste	19

5.9	Hook ups to existing works	19

5.10	Tests and inspections	19

5.10.1	Description of tests and inspections	19

5.10.2	Materials facilities and samples for tests and inspections	19

6	List of drawings	20

6.1	Drawings issued by the Employer	20

7	Low Service Damages – Annexure A	20

# Description of the service

## Executive overview

The purpose of this contract is to appoint a suitable qualified Contractor for the Provision of heating, ventilation and air conditioning (HVAC) maintenance service, goods and material supply contract and will render a service to the Transmission Real Estate property portfolio which includes the North East Grid regional office, 22 substations and 4 depos (CLNs), within the Mpumalanga Province for a period of 36 months on an as and when required basis.

This will include provision of labour, supervision and management, staff uniform/PPE, equipment and its maintenance, transport and services during the critical operation of NTCSA. This document outlines the roles and responsibilities, what the scope of work will entail as well as the technical evaluation criteria to be used during tender evaluations.

## Employer’s requirements for the service

The scope includes the provision of the following HVAC services:

- Diagnostics of defects,

- Minor adjustments of controls and minor repairs,

- Major repairs such as dismantling of components, opening of systems, the evaluation and re-charging of same etc.

- Replacement of defective equipment

The Contractor shall provide all labour, supervision, administration and management, transport, equipment, tools, supplies and material required to perform the facilities management services specified herein.

In addition to the listed sites, NTCSA may request the Contractor to execute works on other NTCSA sites in the region on an as and when required basis.

Closure of site

In the event that a site or building closes down then the service at that site must come to a stop, no compensation will be paid to the contractor when a site is closed down.

NTCSA reserves the right to instruct the Contractor to change working times based on business requirements.

1.3 Detailed description of the service

| Item | Description | Frequency |
| --- | --- | --- |
| 4.1. | Inspection of air conditioning filters and filter frames - Remove all filters from one air handling unit at a time. - Inspect filters for defects. - Inspect and clean filter frame properly before re-installing filters | As and when required |
| 4.2. | Replacement of air-conditioning filters - All the air-conditioning filters shall be supplied and replaced by the Contractor on request. - Remove existing old filter (as and when required). - Inspect all framework and clips for damage, rust and fair wear and tear. - Clean framework. | As and when required |
| 4.3. | Fit new filter in position - The Contractor shall remove all the redundant filters from the Site and dispose of these redundant filters only at a registered dump site. It is the responsibility of the Contractor to obtain written proof from the registered dump site that the waste was disposed of in a safe manner. A copy of this document shall be placed on record in the Contractor’s Health, Safety & Environmental File. | As and when required |
| 4.4. | Filter cleaning | As and when required |
| 4.5. | Service of air Handling units - Check Fan in Operation - Check Fan and Motor Bearings - Lubricate Fan Bearings - Check Condition of Fan Belts. Realign Drives if Adjustment is Required. Check Condition of Pulleys - Check Base Mounting Springs - Inspect Flexible Duct Collar - Ensure Coupling Guard is Secure - Check Motor and Terminal Connections - Check for Excessive Vibration - Cleaning Humidifier bottles and check operation | As and when required |
| 4.6. | Service of exhaust Fans and Extraction Fans (toilets, battery rooms) - Check Fan in Operation - Check Motor Bearings - Clean Air Screen - Check Motor and Terminal Connections - Check for Excessive Vibration - Check and clean speed drives | As and when required |
| 4.7. | Servicing of split Air-Conditioning Units - Check Operation of Unit - Clean Air Filters - Check Condenser Fan Motor Bearings - Clean Cooling Coil Surfaces(Brush) - Check System Gas Charge (If and when required) - Check Operating Pressures and Record Suction & Discharge Pressure - Leak Test Refrigeration System - Check and Tighten All Terminal Connections - Check Operation of Reverse Cycle - Check unit Voltage and Amperages - Check Operation of Heaters - Ensure that Condensing Unit Coils are Clean - Check drain is not blocked - Clean unit Fill out report and hand copy to the Employer’s Representative | As and when required |
| 4.8. | Air-Conditioning VRV’s Service of external units - Check operation of each unit - Wash down coils on all exterior condensing units - Fill out report and hand copy to the Employer’s Representative - Visually inspect units for any defects and/or damage. - Inspect all wiring and check all electrical connections. - Check all filters and clean as required or replace. - Check all refrigerant pressures and record readings. - Check compressor to ensure that it is suspended freely, that all bushes are in good condition that, that the compressor is operating correctly and that it does not overheat in normal operating conditions Service of internal Units - Check condensate drains and clear if necessary to prevent internal water leaks. - Clean equipment generally and observe its operation in all its functions. - Check amperage readings on cooling, heating and fan only operation and compare to name plate ratings. - Check air filters and clean where necessary. Should the filter be damaged or torn it will be necessary to provide a new filter at the client's cost. - Check condition of evaporator coil and clean. Straighten fins with a fin comb where necessary. - Check condensate drip trays and treat for corrosion if necessary. Ensure unobstructed gravity flow. - Check condensate drains and clear if necessary to prevent internal water leaks. - Check fans to ensure that they are secured to fan shafts. - Check fan motor(s) to ensure that it (they) is (are) running freely and true and that the bearings show no sign of wear. Oil where applicable. Ensure that the baffle plates are secured between in and outlet air. - Check thermostats, switches, contactors, and the wiring thereof to ensure that all electrical connections are secure and clean. - Check refrigerant system for leaks and repair where necessary. - Ensure that all copper tubing is clear of other components. - Clean equipment generally and observe its operation in all its functions. - Check amperage readings on cooling, heating and fan only operation and compare to name plate readings. - Clean outside of unit, particularly return air grill and discharge vanes. - Rust proof where necessary. - Check and tighten where necessary all refrigerant pipe fittings. - Check head and suction pressures to ensure that these are in accordance with specifications. If not adjust gas volume to required head. - Where conditions change due to excavations, construction, dusty areas or any kind of extraordinary exercises, the cycle of service may be adjusted to maintain healthy performance co-efficient - Check operation of BS selector box | As and when required |
| 4.9. | Servicing of Diffusers - Clean diffusers - Clean return air grills | Bi annual |
| 4.10. | Plant Distribution Boards and Control Equipment (service) - The Contractor shall be responsible for the cleaning, service, maintenance and repairs to all Air-conditioning related Plant Electrical Distribution Boards and Control Equipment. - The distribution boards will include the following: o The Main Air-conditioning Distribution Board o All distribution boards within the site that relates to HVAC | Bi-annual |
| 4.11. | Gauges and Thermometers (service) - Check for accuracy. - Check for leaks. | Bi-annual |
| 4.12. | Refrigeration Equipment (including bar fridges) (service) - Check Operation of Unit - Clean Condenser Coil - Check System Gas Charge - Leak Test Refrigerant System - Check Compressor Oil Levels - Check Operating Pressures. Record Discharge and Suction - Check Safety Cut-Outs. Record Discharge, Suction & O/P/S - Record Time Delay of Oil Pressure Safety Switch - Check for Signs of Oil Leaks - Check for Signs of Vibrations - Clean Condenser Coils (Hose) - Clean water strainer | As and when required |
| 4.13. | Heat Pump Service - Heat pump base: - Clean base outside and inside. - Ensure drainage holes are clear. - Check for rust and treat as required Electronics - Look for signs of corrosion on PCB controller. - Ensure all electrics are dry and clean - Ensure all connections are good. Piping - Check all piping and fittings for leaks. - Check lagging. - Clean the inline strainer. - Check circulation pump. Heat Exchanger - Reverse water flush system under pressure for =- three minutes. | As and when required |

This scope shall be applicable to all sites listed below:

| CLN | Site Name | Address | Purpose |
| --- | --- | --- | --- |
| South CLN | Alpha | -26.808408460211826, 29.39979533917009 | Substation |
| South CLN | Camden | -26.620510429080063, 30.089471479974222 | Sub Station |
| South CLN | Grootvlei | -26.768932159890927, 28.49225591703365 | Sub Station |
| South CLN | Majuba | -27.091641966956935, 29.887537595937648 | Sub Station |
| South CLN | Normandie | -27.142187777551182, 31.023094035896147 | Sub Station |
| South CLN | Sol | -26.53888071162474, 29.11754312566423 | Depo/Substation |
| South CLN | Tutuka | -26.775942833261574, 29.35176108615823 | Sub Station |
| South CLN | Zeus | -26.698737378102887, 29.09178946615079 | Sub Station |
| Witbank | Kriel | -26.25215663203415, 29.17707576140124 | Sub Station |
| Witbank | Kruispunt | -26.209952666442447, 29.092479457501227 | Sub Station |
| Witbank | Kusile | -25.917887030105575, 28.916972866113873 | Sub Station |
| Witbank | Kendal | -26.089728113930306, 28.96734358701323 | Sub Station |
| Witbank | Matla | -26.281554438539718, 29.14136413305024 | Sub Station |
| Witbank | Vulcan | -25.828199007117597, 29.109676033278106 | Sub Station |
| Witbank | Regional Office | Eskom Park, Witbank | Office building |
| Middleburg | Rockdale | -25.810907507805016, 29.50869359679409 | Depo/Substation |
| Middleburg | Arnot | -25.948812688142432, 29.78913349871135 | Sub Station |
| Middleburg | Duvha | -25.960782034611306, 29.338812482578266 | Sub Station |
| Middleburg | Komati | -26.090268901485782, 29.471813399799245 | Sub Station |
| Middleburg | Hendrina | -26.025936967261632, 29.59919205689115 | Sub Station |
| Middleburg | Ermelo | 2 Laai street | Offices |
| Lowveld | Marathon | -25.405600777691653, 30.920333859199843 | Depo/Offices/Substation |
| Lowveld | Khanyazwe | -25.500693204993794, 31.527448869793695 | Sub Station |
| Lowveld | Barberton | -25.753177929660733, 31.024878379599212 | Sub Station |
| Lowveld | Simplon | -25.72056821444972, 31.0321354767602 | Sub Station |
| Lowveld | Prairie | -25.715285504630522, 30.229943270106812 | Sub Station |
| Lowveld | Gumeni | -25.750484462983657, 30.23124709864096 | Sub Station |
| Lowveld | Komatipoort | -25.434171530992266, 31.945964252598444 | Sub Station |

KM to be calculated from Marathon, Witbank, Sol and Rockdale sites as per applicable CLN.

## Interpretation and terminology

The following abbreviations are used in this Service Information:

| Abbreviation | Meaning for Abbreviation |
| --- | --- |
| TRE | Transmission Real Estate |
| NTCSA | National Transmission Company South Africa |
| Tx | Transmission |
| Sat. | Saturday |
| Sun. | Sunday |
| PPE | Personal Protective Equipment |
| SOC | State Owned Company |
| NEC | New Engineering Contract |
| PDF | Portable Document Format |
| FAS | Fall Arrest System |
| SHEQ | Safety Health Environment Quality |
| NEG | North East Grid |
| CLN | Customer Load Network |

# Management strategy and start up.

## The Contractor’s plan for the service

The service provided must detail in writing its plan to deliver the excellent service for NTCSA throughout the entire period for the contract. The below items must form part of the site management plan:

- Health and safety management

- Time management

- Communication management

- Environmental management

- Quality management

- Emergency response

- Supplier management

- Stakeholder management

- Cost management

- Material management

- Access arrangement

- Criminal management

- Schedules arrangement and management

- UIF and COID Payment

- Subcontractor management (if applicable)

- Housekeeping management

- Delivery management or arrangements

- Permit arrangements

- Site inspection and supervision

## Management meetings

Monthly Meetings’ shall take place on site (face-to-face) to discuss all issues or plans for all perimeters for the contract or project (time, cost, quality, environment and health and safety). Monthly Meetings preferred at the start of each month for the good planning of activities on site. The Employer can request the ‘Emergency Meeting’ at any given time if there are serious issues or risks that can affect the service delivery for the project / contract. All meetings shall be chaired by the service manager. Ms Teams can be used as alternative platform due to unforeseen and other circumstances or very urgent issues e.g., Emergency Meeting, etc.

All meetings shall be recorded in the form of minutes or a register prepared and circulated by a person who convened the meetings. The minutes or register shall not be used for the purpose of confirming actions or instructions under the contract as these shall be done separately by the person identified in the condition of contract to carry out such actions or instructions.

Regular meetings of a general nature may be convened and chaired by the Service Manager as follows:

| Title and purpose | Approximate interval | Location | Attendance by: |
| --- | --- | --- | --- |
| Kick of meeting | Minimum within 1 week after start date |  | Service Manager, Contractor and Supervisor |
| Overall contract progress and feedback in terms of contract obligations | Monthly intervals or when deemed required by the Service Manager |  | Employer, Service Manager, Relevant NTCSA representatives and appointed Contractor/Sub-contractor |
| Safety, health, environmental and quality meeting | Monthly |  | Employer and Contractor |
| Contractor Forums | As and when deemed necessary |  | Employer, Service Manager, Relevant NTCSA representatives and appointed Contractor/Sub-contractor |
| Daily safety Toolbox Talks | Daily before work starts on site with signed attendance registers by the Contractor’s employees an signed off minutes by the Contractor’s site Agent or manager |  | Contractor and his/her employees |

## Contractor’s management, supervision and key people

The Contractor is required to hire experienced supervisors with a proven track record in HVAC field environments. These specialized supervisors must possess a minimum of five years of experience in supervising maintenance. Prior to deployment on-site to oversee activities, the qualifications, training records, and curriculum vitae of supervisors must be submitted to the Service Manager for approval..

The Contractor is responsible for maintaining an updated organogram on-site, detailing all supervision and management both on-site and off-site for the management of this contract. Additionally, the Contractor must always maintain daily attendance registers and make them available to the Service Manager upon request.

2.3.4 Contractor’s Responsibility

- The Contractor shall conform with Eskom Distribution Standard “Occupational Health Contractors Reference ESKASAAP4.

- The Contractor must comply with the Occupational Health and Safety Act, all applicable regulations and Compensation of Occupational Injuries and Diseases Act.

- Health and safety and Environmental induction is compulsory prior the start of work for each site.

- Workers shall have valid medical certificate of fitness from the occupational health practitioner.

- The Contractor shall ensure the submission of man hours at specified time to the Employer.

2.3.5 Uniforms and Protective Clothing, and Equipment

- The Contractor shall supply all his employees on site with its uniform colour and style.

- The Contractor shall supply its employees with the two sets of overalls and uniforms.

- The Contractor shall supply one pair of safety shoes – steel toe safety boots.

- All employees shall receive two jerseys warmer jackets and raincoat for rain and winter season.

- All personal protecting clothing and equipment shall be replaced as and when required – this does not mean only at the beginning of the year or financial year.

- All operators shall be equipped with safety helmets, eye and ear protection and the safety boots where required.

- Contractor shall ensure that its employees are wearing the relevant personal protecting equipment for the task at all the times.

- Contractor shall ensure that there’s no PPE shortage on workers on site at any time.

## Provision of bonds and guarantees.

Not applicable

## Documentation control

All Contractual Documents must have relevant Contract Number and Purchase Order Number as reference per the NTCSA Standards. All correspondence shall be dated and sequency numbered and distributed in accordance with a procedure as agreed and accepted by the service manager. The use of SMS, WhatsApp, and Ms Teams do not override the use of applicable and relevant NEC standards templates, forms, and NTCSA procedures. All invoices and service delivery notes must be in PDF format.

## Invoicing and payment

Within one week of receiving a payment certificate from the Service Manager in terms of core clause 51.1, the Contractor provides the Employer with a tax invoice showing the amount due for payment equal to that stated in the Service Manager’s payment certificate.

The Contractor shall address the tax invoice to include on each invoice the following information:

- Name and address of the Contractor and the Service Manager.

- The contract number and title.

- Contractor’s VAT registration number.

- The Employer’s VAT registration number 4710303126.

- Description of service provided for each item invoiced based on the Price List.

- Total amount invoiced excluding VAT, the VAT and the invoiced amount including VAT.

- Electronic submission of invoices via email

- Signed service delivery note(s) must accompany the required invoice(s) for payment.

Invoices and Additional Information

- NTCSA order number must be clearly indicated on the invoice with the line number on the order for billing.

- Only PDF invoices must be submitted.

- Each PDF file should contain one invoice, one debit, and credit note only as NTCSA’s SAP system does not support more than one PDF being linked into workflow at a time.

- Only one PDF file per email (one invoice or debit note or credit note).

- Send all invoices in PDF straight from your system to an NTCSA email address (see the email address below).

- When it comes to foreign invoices, suppliers will be required to physical deliver the hard copies of original documents to the respective documentation management centers – though invoices emailed. NTSCA is still seeking clarity from the South African Reserve Bank for foreign invoices and currency. Current requirements are that these manual invoices should be submitted. Invoice copy can be sent to the email address indicated below.

- All submitted invoices electronically must comply with the Tax Requirements.

- If there is a Cost Price Adjustment on the invoice, NTCSA recommends separate invoice for CPA to avoid delays on payment, if there are issues for the CPA.

- Introduction of electronic invoicing does not guarantee payment but will ensure visibility of all invoices and ensure that no invoices get lost. If the goods receipt is not done, the invoice will be parked, and the system will automatically send an email to the end user to do good receipt. This is also tracked by NTCSA through the park invoice report.

- The Contractor can request a park invoice report from the Finance Shared Services (FSS) contact centre which can then be followed up and corrected.

- The Contractor is welcome to forward the details of invoices corrected to the FSS contact centre.

- All invoices for payment must be submitted Invoicesntcsalocal@ntcsa.co.za

Follow-up with Finance Shared Services (FSS):

All queries and follow-up on invoice payments should be made by contacting the FSS Contact Centre at +27 11 800 5060 or email fss@eskom.co.za

Introducing electronic invoicing does not guarantee payment, but will ensure visibility of all invoices as well as ensure that no invoices are lost. If the Goods Receipt (GR) is not done, the invoice will be parked and the system will automatically send an email to the end user to do the GR. This is also tracked by NTCSA through the parked invoice report.

## Contract change management.

Changes to the contract will be notified and addressed as per the NEC3 – TSC3 and as per NTCSA’s internal Governance Processes for approval. Modifications to work/service can only resume once NTCSA approval is obtained and as instructed by the NTCSA Representative (Service Manager).

## Records of Defined Cost to be kept by the Contractor

As a control measure, it is required for the Contractor to maintain record keeping of all defined cost items for the purpose of compensation event management. A schedule of these cost components may not be listed in the contract price list should be provided when required.

## Insurance provided by the Employer

Refer to Z12 in Data by Employer document.

## Training workshops and technology transfer

- OHS supervisor training or Supervisory training

- Hazardous chemical substance training certificate

- HIRA certificate

- Incident Investigation Certificate

- Fire Fighting Certificate

- 1st Aid Certificate Level 2

- Health and Safety Representative Certificate

- Legal liability training

- Working at height

- Oil Spillage Training

- Fall arrest system (FAS)

- Fall protection plan developer.

## Design and supply of Equipment

The Contractor bears responsibility for providing all necessary equipment on-site. All equipment supplied by the Contractor must meet the SABS standard and be of good quality. No payment will be made for the standing time of equipment on-site. Faulty equipment or machinery must not remain on-site for more than seven working days. The Contractor is prohibited from storing or retaining any irrelevant equipment or tools at the service site. Any breakdowns of plant and equipment must be promptly reported to the Employer (Service Manager). Furthermore, the light-duty vehicle assigned to the site shall not be older than five years.

## Things provided at the end of the service period for the Employer’s use

### Equipment

At the end of the contract, all the equipment purchased through the contract by the Employer must be handed over to the Service Manager

### Information and other things

At the end of service contract, the Contractor must provide the following information.

•	Consolidated health and safety file

•	Employers’ investigation reports and all supporting documents

•	All contracts reports in relation to this service contract

•	All historical invoicing and the signed delivery notes for the service

•	All defined cost documents

## Management of work done by Task Order

- The Contractor shall receive the task order prior the start of work on site.

- Other than emergency work requests, no works shall proceed without an approved task order.

- An approved task order shall bear the signature of Contractor representative and NTCSA Representative (Service Manager).

- Discretion of the Contractor and Supervisor shall apply in determining and interpreting emergency requests to ratify works done without an approved task order.

The Contractor will not be compensated for works that proceed without an approved task order unless the task order is ratified at the discretion of the Service Manager and Supervisor. Reasons shall be in writing to the Contractor to request ratification for compensation events with any works done without the approved task order.

# Health and safety, the environment and quality assurance

## Health and safety risk management

The Contractor shall conform and comply with the following standards and legislation below:

- Issued Health and Safety and Environment Specification

- Basic Condition of Employment Act No. 75 of 1997

- Occupational Health and Safety Act and Regulations No. 85 of 1993

- 32 – 37 Eskom Substance Abuse Procedure

- 240-62196227 Life- Saving Rules

- 32-95 Occupational Health and Safety Incident Management

- 32-727 SHEQ Policy

- 32- 418 Working at Heights Procedure

- ISO 9001: Quality management system

- ISO 45001: Occupational Health and Safety Management System

- Eskom’s Covid-19 Health and Safety Policy statement

- National Road Traffic Management Act.

- Eskom Risk Assessment Procedure 32-520

- Employees Right of Refusal to Work in an Unsafe Situation Procedure 240-43843827

## Environmental constraints and management

The Contractor shall conform and comply with the following standards and legislation below:

- Issued Health and Safety and Environment Specification

- National Environmental Management Act 107 of 1998.

- National Environmental Management Waste Act 59 of 2008.

- Environmental Incident Management Procedure 240-133087117

- Waste Management Standard 32-245

- 32-727 SHEQ Policy

- ISO 14001: Environmental Management System

The Contractor to clean up hazardous material spillages (and oil spillages)

## Quality assurance requirements

The Contractor shall conform with the following standards and documents below:

- Quality Management Specification

- ISO 9001 Quality Management Systems – Requirements

- 32-727: Safety, Health, Environment, and Quality (SHEQ) Policy

- 240-12248652 Supplier Quality Management: List of Tender Returnables

# Procurement

## People

### Minimum requirements of people employed.

•	The Contractor shall conduct criminal and site clearance checks of its employees (before offer of employment).

•	The Contractor shall conduct training, testing and verifying key personnel qualifications and competence including certification for operation of machinery and equipment in relation to OSHACT.

### BBBEE and preferencing scheme

All tenderers must at a minimum maintain their B-BBEE status throughout the contract period.

Supplier Development Localisation and Industrialisation (SDL&I)

SDL&I contractual obligations

Contract skills development goals:

- HVAC Artisans:

- Apprentices:

Job Opportunities:

- Jobs to be created:

- Jobs to be retained:

Designated sector:

Local content percentage: 100%

SDL&I Penalty and Performance Security

- NTCSA will apply a penalty of 2.5% of the invoice amount for failure to meet SDL&I obligations. As security for the fulfilment of all SDL&I obligations, NTCSA will apply a penalty of 2.5% of every invoice amount (excluding VAT) for failure to submit SDL&I performance reports every quarter; or failure to meet the SDL&I obligations in a contract.

Reporting and Monitoring

- The suppliers shall on a monthly/quarterly basis submit a report to NTCSA in accordance with Data Collection Template on their compliance with the SDL&I obligations described above.

- NTCSA shall review the SDL&I reports submitted by the suppliers within 60 (sixty) days of receipt of the reports and notify the suppliers in writing if their SDL&I obligations have not been met.

- Upon notification by NTCSA that the suppliers have not met their SDL&I obligations, the suppliers shall be required to implement corrective measures to meet those SDL&I obligations before the commencement of the following report, failing which Retention clauses shall be invoked.

- Every contract shall be accompanied by the SDL&I Implementation Schedule which must be completed by the suppliers and returned to SDL&I representative for acceptance 28 days after contract award.

The Contractor shall keep accurate records and provide the Service Manager with reports on the Contractor’s actual delivery against the above stated SDL&I criteria.

The Contractor’s failure to comply with his SDL&I obligations constitutes substantial failure on the part of the Contractor to comply with his obligations under this contract.

## Subcontracting

### Preferred subcontractors

Not applicable

### Subcontract documentation, and assessment of subcontract tenders

Not applicable

### Limitations on subcontracting

The use of Sub Contractors by the Contractor must be approved in writing by the Service Manager before commencement on site.

### Attendance on subcontractors

It is the sole responsibility of the Contractor. The Contractor is to ensure that the Contractor fulfils any upfront payments or deposits required by the subcontractor such that the subcontractor executes the service timeously.

## Plant and Materials

### Specifications

The price list state the list of required plant and equipment for the service required as per the scope of work. The Contractor can engage fairly and in bona fide in works execution by assisting the Employer with advice and recommendations on changes in technologies and industry best practices that may affect the Employer’s ability to perform works as per the contract stipulation. The Contractor shall take reasonable care to acquire and maintain equipment that meets minimum legal requirements.

### Correction of defects

The repairs for plant or equipment shall be performed by accredited or competent person or Contractor as per manufacturers manual. The repairs shall not interfere with or hinder the employers’ work operation on site. All the maintenance or repairs records shall be kept safely and be available at any time when employer is looking for the records.

All defects identified to be corrected immediately or not more than 2 days if the work requires special equipment

### Contractor’s procurement of Plant and Materials

The Contractor must purchase the plant and materials in good faith, and for mutual benefit for both parties. The Contractor shall purchase all materials and plant from the accredited Supplier. The Contractor shall remain the sole responsibility to procure plant and materials for the reasonable and acceptable quality. The Employer can request at any time the data sheet and proof of purchase for the equipment purchased and supplied on site for usage. Guarantees and warrantees certificate may also be required for any plant and material supplied by Contractor to the Employer.

### Tests and inspections before delivery

The Service Manager may request inspection during the equipment and materials arrival on site. All equipment and materials must be inspected by the Contractor together with Employer (Service Manager) during arrival before use on site. The records of inspection must be available at any request by the Service Manager.

### Plant & Materials provided “free issue” by the Employer

Not applicable

### Cataloguing requirements by the Contractor

Not applicable

# Working on the Affected Property

## Employer’s site entry and security control, permits, and site regulations

NTCSA reserves the right to subject all employees for the Contractor to a vetting and security clearance process in line with NTCSA’s security requirements for the site. Any person entering (Including NTCSA’s employees) the site of NTCSA is subject to random alcohol testing to gain access to the site. All employees and vehicles that are entering or exiting the site shall be subjected to be searched by security personnel at gates or checkpoints.

The Contractor shall do criminal checks, and submit the ID copy, physical address and contact details for its employees to NTCSA before deploying any employee for work activities on NTCSA’ site. The contractor shall inform the Service Manager prior any removal of its employees on site. The Contractor shall ensure that all equipment and material brought on site are signed in the approved NTCSA security register at the security gate. The Contractor shall not remove any equipment or materials on site, prior informing the Service Manager or Supervisor.

## People restrictions, hours of work, conduct and records

Normal working hours for the sites access is between 07h00 and 16h00 from Mondays to Fridays. The Contractor shall keep timesheet records for its employees and submit the man hours on agreed dates. Health and safety facilities on the Affected Property. The contract might be called upon to attend to defects after working hours.

The Contractor shall conform with all standards and procedures for operation at the NTCSA’ site, e.g., Life Saving Rules, and comply with all applicable legislations on site for the OHSA Act 85 of 1993.

## Health and safety facilities on the Affected Property

The Contractor shall conform with all standards and procedures for operation at the NTCSA site and comply with all applicable legislations on site for the NEMA and NEMWA.

## Environmental controls, fauna & flora

As per clause 25.1 of this contract (Core Clauses).

## Records of Contractor’s Equipment

The Contractor must report to the Service Manager and Supervisor prior or during arrival of any equipment (owned or hired equipment) on site.  The Contractor shall inform the Service Manager and Supervisor prior removal any equipment (owned or hired equipment) on site. The Contractor shall keep the updated list of all the equipment. All equipment must be inspected as per all applicable legislations, and the records shall be made available at any given time required by the Service Manager or the inspector from the Department of Employment and Labour. The Contractor shall not keep on site any unused equipment.

Any electrical equipment or appliances used by the Contractor must comply with all relevant safety regulations and requirements and be maintained in safe and proper working condition.

The Employer has the right to stop the Contractor's use of any electrical equipment or appliance, which in the Employer’s opinion does not conform to the foregoing.

## Equipment provided by the Employer

All the equipment and tools purchased through the contract belongs to the Employer, and the Contractor shall hand over all that equipment to the Service Manager at the end of the service contract.

The Contractor shall not leave the site with the equipment or tools purchased through the contract. In case of service or maintenance required for equipment to be conducted outside site, the Contractor shall agree with the Service Manager or Supervisor on timelines and provide backup equipment.

## Site services and facilities

### Provided by the Employer.

- Water

- Electricity

- Stores

- Changing rooms where possible

- Ablution facilities

- Shower facilities where possible

### Provided by the Contractor

- The Contractor shall supply all plant required for operation.

- Relevant tools including ladders, scaffolding, instrumentation for air conditioning discipline.

## Control of noise, dust, water and waste

The Contractor shall conform with NTCSA’s requirements and comply with all applicable legislations for environment management on site.

The Contractor shall take appropriate measures to minimise the generation of dust as a result of his works, operations and activities to the satisfaction of the Service Manager.

## Hook ups to existing works

The Contractor shall conform with the requirements for Eskom’s Life Saving Rules., Eskom working at Heights Procedure, The performance of works which affects the employer’s operations, or the system of other contractors shall be scheduled to be performed only at times approved by the Employer). The procedure for carrying out work which of necessity interrupts the employer’s operation, or the system of other contractors, or imposes abnormal operating conditions of their systems, is subject to approval of the service manager.

- No scaffolding and platforms will be used without it having been safety cleared and the required documentation completed as per SANS 10085-1:2004 or recent version.

- Scaffolding should be done by trained personnel and certified as safe thereafter

- All working at heights apparel should be certified and inspected daily before use.

## Tests and inspections

### Description of tests and inspections

The Contractor shall be responsible for providing the quality inspections as per the scope requirements and rectifies all defects within the agreed time. The Contractor to provide test and inspection records on approved templates by the Employer (Service Manager). The inspections and records shall comply and conform with all applicable legislative and Employer’s requirements.

### Materials facilities and samples for tests and inspections

All deliveries for material shall be inspected by the Service Manager or Supervisor before usage on site.

# List of drawings

## Drawings issued by the Employer

Not applicable

# Low Service Damages – Annexure A

| Low service damages table 2 |  |  |
| --- | --- | --- |
| Service Levels |  |  |
| Item | Low service | Damages |
| 1 | Penalty for late completion of task orders | R 2,000.00 per task order. |
| 2 | Failure to supply 2 overalls, and 2uniforms, one pair safety boots and 2 warmer jacket prior the start of employees on site. | R 2000.00 per incident |
| 3 | Workers on site without mandatory PPE | R5 000.00 per incident |
| 4 | Non-payment to subcontractors causing disruption of service to NTCSA | R 3000.00 per infringement |
| 5 | Equipment and tools shortage on site | R 2000 per incident |
| 6 | Failure to maintain defect free period through poor workmanship on corrective or preventative maintenance tasks | R 2000.00 per infringement |
| 7 | Where a repair is delayed by 5 calendar day or more due to the unavailability of a spare part without the approval of the Service Manager or his/her duly authorised representative | R 2,500.00 per task |
| 8 | Leaving a breakdown /emergency unattended or incomplete for another day without the approval of the Service Manager or his/her duly authorised representative | R 2,500.00 per infringement |
| 9 | Failure to perform 100% of all required preventative maintenance tasks per month | R 3,000.00 per task |

This total is required by the Employer for budgeting purposes only.  Actual amounts due will be assessed in terms of the conditions of contract.

Available from Engineering Contract Strategies Tel 011 803 3008 Fax 086 539 1902 www.ecs.co.za