{"text_format":"3","workbook":"xls","n_sheets":4,"sheets":["Notes for completing schedules","Technical A&B Schedule","Deviation Schedule","Technical Schedule C"],"not_rendered":{"images":1,"external_links":1,"defined_names":72},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Notes for completing schedules","index":0,"n_rows":19,"n_cols":3,"rows_kept":19,"merged":[[0,1,0,2],[6,1,6,2],[7,1,7,2],[8,1,8,2],[9,1,9,2],[10,1,10,2],[11,1,11,2],[12,1,12,2],[13,1,13,2],[14,1,14,2],[15,1,15,2],[16,1,16,2],[18,1,18,2],[19,1,19,2],[265,9,266,9],[326,1,326,4]],"flags":["formulas_cached_only"]}
["A","DESCRIPTION OF SCHEDULES"]
[]
[null,"SCHEDULE A:  ","PARTICULARS OF EMPLOYER’S REQUIREMENTS"]
[]
[null,"SCHEDULE B:","GUARANTEES AND TECHNICAL PARTICULARS OF PLANT AND MATERIAL OFFERED"]
[]
["B","GUIDE FOR FILLING THE SCHEDULES"]
[]
[1,"Values and parameters entered in Schedule A are considered to be the minimum requirements. Where the Contractor does not fully comply with the Employer's  requirement, any deviations must be clearly indicated in Schedule B and listed in the Deviation Schedule."]
[]
[2,"Where there is a need to substantiate or further describe an item in Schedule B, especially in instances of non-compliance with Schedule A, particulars are furnished on a separate sheet clearly marked with the notation of the Schedule A item referred to."]
[]
[3,"If a blank space is left in Schedule B next to certain requirement specified in Schedule A, this constitutes a confirmation that the tenderer does not comply with that specific requirement."]
[]
[4,"Where ‘xxx’ is indicated for an item in Schedule A, the Contractor is required to fill in the appropriate information in Schedule B, for the equipment offered."]
[]
[5,"Where ‘***’ is indicated in the Schedule A column, Eskom engineering practitioner shall provide information before enquiry is issued to the market."]
[]
[6,"Separate schedules are completed for each rating of switchgear as per the requirements of the switchgear schedules. The same applied for the circuit breakers. Further, separate schedules should be provided for the equipment of different types, if offered for the same ratings."]

{"sheet":"Technical A&B Schedule","index":1,"n_rows":452,"n_cols":6,"rows_kept":452,"merged":[[0,0,5,1],[0,2,5,2],[0,3,0,4],[1,3,1,4],[2,3,2,4],[3,3,3,4],[4,3,4,4],[5,3,5,5]],"flags":["formulas_cached_only"]}
[null,null,"TECHNICAL A&B SCHEDULE FOR  GENERATION AIR-INSULATED WITHDRAWABLE METAL-ENCLOSED SWITCHGEAR AND CONTROLGEAR FOR RATED VOLTAGES ABOVE 1KV UPTO AND INCLUDING 52KV","Template Unique Identifier:","Template Unique Identifier:","240-93576770 (Rev 2)"]
[{"$nulls":3},"Switchgear Standard number:","Switchgear Standard number:","240-56227573"]
[{"$nulls":3},"Document Unique Identifier:","Document Unique Identifier:","xxx-xxxxxxxx"]
[{"$nulls":3},"Revision No:","Revision No:","<x.x>"]
[{"$nulls":3},"Effective Date","Effective Date","2020-07-01"]
[{"$nulls":3},"GENERATION ASSET MANAGEMENT"]
["Item no.","Clause of 240-56227573","Item Description","Units","Schedule A","Schedule B"]
[]
[1,3.1,"RATNGS AND OPERATING CONDITIONS"]
[]
[1.1,"3.1.1","Panel Ratings"]
[1.2,null,"System nominal voltage","kV","per switchgear schedule"]
[1.3,null,"System voltage range","%","per switchgear schedule"]
[1.4,null,"Rated voltage","kV","per switchgear schedule"]
[1.5,null,"Number of phases",null,3]
[1.6,null,"System neutral earthing",null,"***"]
[1.7,null,"Rated Short-Duration Power Frequency Withstand Voltage ","kV rms","per switchgear schedule"]
[1.8,null,"Rated Lightning Impulse Withstand Voltage  ","kV peak","per switchgear schedule"]
[1.9,null,"Rated Frequency ","Hz",50]
[{"v":1.1,"d":"1.10"},null,"Rated Normal Current at 40 degrees Celsius","A","per switchgear schedule"]
[1.11,null,"Rated Short-Time Withstand Current ","kA","per switchgear schedule"]
[1.12,null,"Rated Peak Withstand Current ","kA","per switchgear schedule"]
[1.13,null,"Rated Duration of Short Circuit ","s","per switchgear schedule"]
[1.14,null,"Rated Supply Voltage of Closing and Opening Devices and of Auxiliary and Control Circuits",null,"***"]
[]
[2,"3.1.2","Ratings for Switching Devices\nNote: Individual ratings of circuit breakers shall be stipulated on Switchgear Schedule Template"]
[2.1,"d)","Circuit-breakers' Electrical endurance classification",null,"E2"]
[2.2,"e)","Circuit-breakers' Mechanical endurance classification",null,"M2"]
[2.3,"f)","Earthng Devices Electrical endurance classification",null,"E2"]
[2.4,null,"Fault making curent rating",null,"kA"]
[2.5,null,"Fault withstand current rating",null,"kA"]
[2.6,null,"Durantion of short circuit withsatnd current",null,"s"]
[2.7,null,"Current rating of connection between device abd earth bar",null,"kA"]
[2.8,"g)","Earthing Devices Mechanical endurance classification",null,"M1"]
[]
[3,"3.1.3","System Characteristics and Operating Conditions"]
[3.1,"a)","Main power system normal power supply ",null,"± 5% "]
[3.2,"b)","Circuit-breaker auxiliary coils:"]
[3.3,null,"Shunt closing release",null,"85% - 110%"]
[3.4,null,"Shunt opening release",null,"85% - 110%"]
[3.5,null,"Under-voltage release",null,"below 35%"]
[3.6,"c)","Total Harmonic Distortion (THD) ",null,"up to 5%"]
[]
[4,3.2,"PANEL DESIGN AND CONTRUCTION"]
[]
[4.1,"3.2.1","Service Conditions"]
[4.2,null,"Installation","Indoor/Outdoor","Indoor"]
[4.3,"a)","Ambient temperature","OC","-5 to 40"]
[4.4,"b)","Altitude","metres","xxx"]
[]
[5,"3.2.2","General Requirements"]
[5.1,null,"Manufacturer",null,"xxx"]
[5.2,null,"Technology type",null,"xxx"]
[5.3,null,"Model/Type",null,"xxx"]
[5.4,null,"Power cable access","Rear/Front","yyy"]
[5.5,null,"Control cable entry","Top/Bottom","yyy"]
[]
[5.6,null,"Switchboards physical dimesions"]
[5.7,null,"Minimum overall length                        ","mm","xxx"]
[5.8,null,"Maximum overall height                   ","mm","xxx"]
[5.9,null,"Maximum overall depth                     ","mm","xxx"]
[{"v":5.1,"d":"5.10"},null,"Circuit breaker compartment depth","mm","xxx"]
[5.11,null,"Low voltage compartment depth          ","mm","xxx"]
[5.12,null,"Base frame height  ","mm","xxx"]
[5.13,null,"Power cable opening/slot  (Length x Width)   ","mm x mm","xxx"]
[5.14,null,"Overall mass of complete switchboard ","kg","xxx"]
[]
[5.15,"b)","Internal Arc Classification",null,"AFLR for 1 sec"]
[5.16,null,"Fault current rating","kA","xxx"]
[5.17,"c)","The switchgear and controlgear shall be of behind-closed-door operation i.e circuit-breaker compartment door shall not be part of the circuit-breaker",null,"Yes"]
[5.18,"d)","The switchboards shall be of modular designs that allow for the subsequent addition of identical panels",null,"Yes"]
[]
[6,"3.2.4","Segregation of Compartments"]
[]
[6.1,"3.2.4.1","General"]
[6.2,null,"Separate circuit breaker compartment",null,"Yes"]
[6.3,null,"Separate busbar compartment",null,"Yes"]
[6.4,null,"Separate control and protection cable termination compartment",null,"Yes"]
[6.5,null,"Separate power cable termination compartment \n(including cable earth switch)",null,"Yes"]
[6.6,null,"Separate busbar earthing device compartment",null,"Yes"]
[6.7,null,"Separate busbar VT compartment",null,"Yes"]
[]
[6.8,"3.2.4.3","Power Cable Compartment"]
[6.9,"c)","Power cable compartment shall comply with SANS 876",null,"Yes"]
[{"v":6.1,"d":"6.10"},null,"Power cable terminations type for single core and three core",null,"Type 2 (shrouded/covered)"]
[]
[6.11,"3.2.4.5","Circuit-breaker Compartment"]
[6.12,"1)","Integral motorised racking mechanism",null,"Yes"]
[]
[6.13,"3.2.4.6","Busbar Earthing Device Compartment"]
[6.14,"b)","The busbar earthing device compartment shall be on the same panel as the VT compartment",null,"Yes"]
[6.15,"d)","Fixed type busbar earthing device",null,"Yes"]
[]
[6.16,"3.2.4.7","VT Compartment"]
[6.17,"d)","Withdrwable type VT",null,"Yes"]
[]
[7,"3.2.5","Service Continuity Classification"]
[7.1,null,"Loss of service continuity category",null,"LSC2B"]
[]
[8,"3.2.6","Partition Class and Shutters"]
[8.1,"a)","Partiton class",null,"PM"]
[8.2,null,"Number of mechanical operating cycles",null,1000]
[]
[9,"3.2.8","Degree of Protection"]
[9.1,"a) 1)","Protection againsnt live part inside LV compartment",null,"IPXXB"]
[9.2,"     2)","Cable  boxes",null,"IP3X"]
[9.3,"               b)","Switchboards",null,"IP4X"]
[]
[9.4,"3.2.9.1","Padlocking Facilities"]
[9.5,"c)","Diameter for all padlocking facilities ",null,"Min 10 mm"]
[9.6,null,"Dimensions of padlock",null,"Figure 1 of 240-56227574"]
[]
[10,"3.2.10","Corrosion Protection "]
[10.1,"a)","Corrosion protection",null,"Yes"]
[]
[10.2,"3.2.11.2","Colour Coding of Switchboards"]
[10.3,null,"Panel exterior colour coding",null,"xxx"]
[]
[11,"3.2.12","Busbars and Connections"]
[11.1,null,"Main busbars current rating","A","xxx"]
[11.2,null,"Number of busbars","number per phase","xxx"]
[11.3,null,"Busbar insulating medium",null,"Air"]
[11.4,null,"Busbar connections",null,"Bolt, nut and washer"]
[11.5,null,"Busbar material",null,"HD copper"]
[11.6,null,"Method of busbar identification",null,"Colour coding"]
[]
[12,"3.2.14","Insulating Materials"]
[12.1,"a)","Insulating material name",null,"xxx"]
[12.2,null,"Type and manufacturer of phase to phase barriers",null,"xxx"]
[12.3,null,"Type and manufacturer of phase to earth barriers",null,"xxx"]
[12.4,null,"Type and manufacturer of connection joints insulation",null,"xxx"]
[]
[13,"3.2.15","Auxiliary Circuit Wiring and Identification"]
[13.1,null,"Control cable type ",null,"PVC, PVC, SWA"]
[13.2,null,"Insulation voltage rating            ","V","600/1000"]
[13.3,null,"VT and CT circuits conductor sizes   ","mm2",2.5]
[13.4,null,"Control circuits conductor sizes           ","mm2",1.5]
[13.5,null,"Alarm circuits                         ","mm2",1.5]
[13.6,"d)","Control wire sheath colour:"]
[13.7,"1)","AC circuits",null,"Black"]
[13.8,"2)","DC circuits",null,"Grey"]
[13.9,"3)","Earthing",null,"Green and yellow"]
[{"v":13.1,"d":"13.10"},"4)","CT and VT wiring as per the phase",null,"red,white, blue and black(neutral)"]
[]
[13.11,"3.2.16.1","Power Cable Termination"]
[13.12,"b)","Clearance between cable termination points and and adjacent structures (SANS 876)","mm","xxx"]
[13.13,null,"Power cable entry",null,"Bottom"]
[13.14,null,"Power cable type ",null,"per switchgear schedule"]
[13.15,null,"Conductor size",null,"per switchgear schedule"]
[13.16,null,"Number of cables",null,"per switchgear schedule"]
[]
[13.17,"3.2.16.3","Cable Entry Arrangements"]
[13.18,null,"Distance from terminal(bushing) centre line to the gland plate or cable clamp (SANS 876)","mm","Min 800 mm"]
[]
[13.19,"3.2.16.4","Vermin and Fire Proofing of Cable Compartment and LV Compartment"]
[{"v":13.2,"d":"13.20"},"a)","Minimum fire rating","hrs",2]
[13.21,null,"Type of material used",null,"xxx"]
[]
[14,"3.2.17","Earthing"]
[14.1,"c)","Earth bar cross sectional area (25 mm wide)","mm2","xxx"]
[14.2,null,"Earth conductor position",null,"Rear of the panel"]
[14.3,null,"Earth conductor material",null,"Copper"]
[14.4,null,"Earth conductor type",null,"Earth bar"]
[14.5,null,"Earth conductor size (calculated as per switchboard specification)                  ","mm2","200 minimum"]
[14.6,null,"Short-time current withstand for earth conductor between earth switch and earth bar (for three seconds)               ","kA","xxx (equal to board rating)"]
[14.7,null,"Earth conductor screened earth bar required","Yes/No","No"]
[]
[15,3.3,"Special Consideration for Internal Arc proof design "]
[15.1,"c)","Each compartment shall contain the arc without spreading it to other compartments",null,"Yes"]
[15.2,"d)","Each functional unit (panel) shall contain the arc without spreading it to any other functional unit/s.  ",null,"Yes"]
[15.3,"h) ","Switchboard fitted with the exhaust duct shall not have common duct with the next switchboard",null,"Yes"]
[15.4,"j)","IAC requirements shall be upheld while working in the low voltage compartment. Hence, the channels or conduits between the power compartments and the low voltage compartments should be sealed accordingly and type tested with the LV compartment door removed. ",null,"Yes"]
[]
[16,3.4,"CIRCUIT-BREAKERS"]
[]
[16.1,"3.4.1","General"]
[16.2,null,"Manufacturer",null,"xxx"]
[16.3,null,"Model",null,"xxx"]
[16.4,null,"Number of poles",null,3]
[16.5,null,"Total auxiliaries contacts",null,"xxx"]
[16.6,null,"Type of circuit-breaker operation",null,"Trip-free"]
[16.7,"a)","Circuit-breakers in accorance with SANS 62271-100",null,"Yes"]
[16.8,"b)","Triple pole withdrawable type",null,"Yes"]
[16.9,"d)","Withdrawable circuit-breakers are housed in a circuit-breaker compartment of the “behind close door” design",null,"Yes"]
[{"v":16.1,"d":"16.10"},"i)","Arc-interrupting medium",null,"Vacuum"]
[16.11,null,"Vacuum interupter name",null,"xxx"]
[]
[17,"3.4.4","Mechanisms and Closing Devices"]
[17.1,null,"Spring Mechanism"]
[17.2,null,"Manual recharge","Yes/No","Yes"]
[17.3,null,"Motor recharge","Yes/No","Yes"]
[17.4,null,"Motor voltage rating","V DC",220]
[17.5,null,"Motor power rating","W","xxx"]
[17.6,null,"Motor starting current ","A","xxx"]
[17.7,null,"Motor steady-state current rating","A","xxx"]
[17.8,null,"Mechanism recharging time at 80% control voltage                         ","s","xxx"]
[17.9,null,"Mechanism recharging time at 100% control voltage                                             ","s","xxx"]
[{"v":17.1,"d":"17.10"},null,"Number of spare spring-device limit switch contacts per mechanism provided  - Normally open (when closing spring is discharged)",null,1]
[17.11,null,"Number of spare spring-device limit switch contacts per mechanism\nprovided  - Normally closed (when closing spring is discharged)",null,1]
[17.12,null,"Number of open/close operations before recharge",null,"xxx"]
[17.13,"b)","Electrically-operated devices including charging motors operating voltage tolerance",null,"85% - 110%"]
[]
[17.14,null,"Closing Coils"]
[17.15,null,"Nominal voltage ","V DC",220]
[17.16,null,"Maximum operating voltage                    ","%",10]
[17.17,null,"Minimum operating voltage ","%",-15]
[17.18,null,"Maximum power drawn by closing coil at nominal voltage ","W","xxx"]
[17.19,null,"Maximum operating current at nominal voltage","A","xxx"]
[{"v":17.2,"d":"17.20"},null,"Nominal operating current at nominal voltage","A","xxx"]
[17.21,null,"Number of open/close operations stored",null,"xxx"]
[17.22,"d)","closing coil power per circuit-breaker",null,"Max 1200VA"]
[]
[18,"3.4.5","Tripping Devices"]
[18.1,null,"Main Tripping Coil"]
[18.2,null,"Nominal voltage ","V DC",220]
[18.3,"a)","Maximum operating voltage                    ","%",110]
[18.4,null,"Minimum operating voltage ","%",85]
[18.5,null,"Maximum power drawn by tripping coil at nominal voltage ","W","xxx"]
[18.6,null,"Maximum operating current at nominal voltage","A","xxx"]
[18.7,null,"Steady-state operating current at nominal voltage","A","xxx"]
[]
[18.8,null,"Second Tripping Coil"]
[18.9,"c)","Provision fo the intallation of second tripping coil",null,"Yes"]
[{"v":18.1,"d":"18.10"},null,"Nominal voltage ","V DC",220]
[18.11,null,"Maximum operating voltage                    ","%",110]
[18.12,null,"Minimum operating voltage ","%",85]
[18.13,null,"Maximum power drawn by tripping coil at nominal voltage ","W","xxx"]
[18.14,null,"Maximum operating current at nominal voltage","A","xxx"]
[18.15,null,"Steady-state operating current at nominal voltage","A","xxx"]
[]
[18.16,null,"Under Voltage Release Coil"]
[18.17,null,"Nominal voltage ","V AC or DC","***"]
[18.18,"e)","Release voltage ","%","xxx"]
[18.19,null,"Maximum power drawn by closing coil at nominal voltage ","W","xxx"]
[{"v":18.2,"d":"18.20"},null,"Maximum operating current at nominal voltage","A","xxx"]
[18.21,null,"Steady-state operating current at nominal voltage","A","xxx"]
[]
[19,"3.4.6","Indicating Devices"]
[19.1,"a) 1)","Circuit-breaker close: ON or I – white lettering on a red background",null,"Yes"]
[19.2,"    2)","Circuit-breaker open (Trip): OFF or O – white lettering on green background",null,"Yes"]
[19.2,"              b)","Lettering size",null,"Min 10 mm"]
[]
[20,"3.4.7","Auxiliary Contacts"]
[20.1,null,"Manufacturer",null,"xxx"]
[20.2,null,"Type ",null,"xxx"]
[20.3,"b)","Number of spare normally-open contacts",null,2]
[20.4,"b)","Number of spare normally-closed contacts",null,2]
[20.5,null,"Current rating at 220V DC \n(utilizing category AC14 or DC13 to IEC 60947-5-1)","A","xxx"]
[20.6,null,"Current rating at 220V AC\n(utilizing category AC14 or DC13 to IEC 60947-5-1)","A","xxx"]
[20.7,null,"Anti-pumping facilities provided",null,"Yes"]
[]
[21,"3.4.9","Insulation Level"]
[21.1,null,"Manufacturer",null,"xxx"]
[21.2,null,"Type of material used"]
[21.3,null,"Thickness","mm","xxx"]
[21.4,null,"Insulation withstand ","V/mm","xxx"]
[21.5,"a)","Internal insulation and clearances in air in accordance with SANS 876 unless proven by type testing to the required insulation levels",null,"xxx"]
[]
[22,3.5,"DISCONNECTORS"]
[]
[22.1,"a)","Disconnectors shall be in accordance with SANS 62271-102",null,"Yes"]
[22.2,"b)","Air-break, triple-pole and gang-operated type",null,"Yes"]
[]
[23,3.6,"EARTHING DEVICES"]
[]
[23.1,null,"Type",null,"xxx"]
[23.2,null,"Manufacturer",null,"xxx"]
[23.3,null,"Designation (e.g. busbar earth switch, cable earth switch)",null,"Where Required"]
[23.4,null,"Number of operations",null,2000]
[23.5,"a)","Earthing devices shall be in accordance with SANS 62271–102",null,"Yes"]
[23.6,"d)","Motorising mechamism for earth switch",null,"Yes"]
[]
[23.7,null,"Auxiliary Contacts"]
[23.8,null,"Manufacturer",null,"xxx"]
[23.9,null,"Type ",null,"xxx"]
[{"v":23.1,"d":"23.10"},null,"Number of spare normally-open contacts",null,2]
[23.11,null,"Number of spare normally-closed contacts",null,2]
[23.12,null,"Current rating at 220V DC \n(utilizing category AC14 or DC13 to IEC 60947-5-1)","A","xxx"]
[23.13,null,"Current rating at 220V AC\n(utilizing category AC14 or DC13 to IEC 60947-5-1)","A","xxx"]
[]
[24,3.8,"ACCESSORIES"]
[]
[24.1,"3.8.1","Current Transformers"]
[24.2,"a)","CTs complies to SANS 61869 part 1 and 2",null,"Yes"]
[24.3,"c)","CTs short-time withstand current rating not less than associated Circuit-breaker rating",null,"Yes"]
[24.4,"e)","CTs shall be air-cooled design with natural flow of air",null,"Yes"]
[]
[24.5,null,"Circuit Protection and Measurement"]
[24.6,null,"Manufacturer",null,"xxx"]
[24.7,null,"Type ","Ring/Bar","Bar"]
[24.8,null,"Model",null,"xxx"]
[24.9,null,"Grouping",null,"Block"]
[]
[{"v":24.1,"d":"24.10"},null,"Core Balance"]
[24.11,null,"Manufacturer",null,"xxx"]
[24.12,null,"Type ",null,"xxx"]
[24.13,null,"Model",null,"xxx"]
[]
[24.14,null,"Current Sensing Device"]
[24.15,null,"Manufacturer",null,"xxx"]
[24.16,null,"Type",null,"xxx"]
[24.17,null,"Model",null,"xxx"]
[]
[25,"3.8.2","Voltage Transformers"]
[25.1,"a)","VTs complies to SANS 61869 part 1 and 3",null,"Yes"]
[25.2,"b)","VT s shall be resin encapsulated type and air cooled design. And cooling shall be through natural flow of air",null,"Yes"]
[25.3,"c)","VTs shall be single phase design",null,"Yes"]
[25.4,"d)","Withdrawable type",null,"Yes"]
[]
[25.5,null,"Busbar Connected Voltage Transformer "]
[25.6,null,"Manufacturer",null,"xxx"]
[25.7,null,"Type",null,"xxx"]
[25.8,null,"Model",null,"xxx"]
[25.9,null,"Nominal voltage","kV","15 and 6.6"]
[{"v":25.1,"d":"25.10"},null,"Insulation of primary winding",null,"per switchgear schedule"]
[25.11,null,"Primary connection",null,"Star-unearthed"]
[25.12,null,"Secondary connection",null,"Star-earthed"]
[25.13,null,"Rated primary voltage ","kV","per switchgear schedule"]
[25.14,null,"Rated secondary voltage ","V",110]
[25.15,null,"Accuracy class",null,"per switchgear schedule"]
[25.16,null,"Voltage factor ",null,1.9]
[25.17,null,"Rated time at maximum operating voltage                                                ",null,"Continuous"]
[25.18,null,"Magnetising current on secondary winding basis at 100% rated voltage ","A","xxx"]
[25.19,null,"Continuous power rating of the secondary winding ","VA",50]
[{"v":25.2,"d":"25.20"},null,"Primary protection",null,"HRC fuse"]
[25.21,null,"Secondary protection",null,"mcb"]
[]
[25.22,null,"Cable Voltage Transformer"]
[25.23,null,"Manufacturer",null,"xxx"]
[25.24,null,"Type",null,"Single phase"]
[25.25,null,"Model",null,"xxx"]
[25.26,null,"Nominal voltage ","kV","per switchgear schedule"]
[25.27,null,"Insulation of primary winding",null,"xxx"]
[25.28,null,"Primary connection",null,"Star-unearthed"]
[25.29,null,"Secondary connection",null,"Star-earthed"]
[{"v":25.3,"d":"25.30"},null,"Rated primary voltage ","kV","per switchgear schedule"]
[25.31,null,"Rated secondary voltage ","V",110]
[25.32,null,"Accuracy class",null,"per switchgear schedule"]
[25.33,null,"Voltage factor",null,1.9]
[25.34,null,"Rated time at maximum operating voltage                                                ",null,"Continuous"]
[25.35,null,"Magnetising current on secondary winding basis at 100% rated voltage ","A","xxx"]
[25.36,null,"Continuous power rating of the secondary winding ","VA",50]
[25.37,null,"Primary protection",null,"HRC fuse"]
[25.38,null,"Secondary protection",null,"mcb"]
[]
[25.39,null,"Running Hour Meters"]
[{"v":25.4,"d":"25.40"},null,"Functionality incorporated in IED","Yes/No","xxx"]
[25.41,null,"Manufacturer",null,"xxx"]
[25.42,null,"Type",null,"Flush electromechanical"]
[25.43,null,"Model",null,"xxx"]
[25.44,null,"Number of display running hours (minimum)","hrs","100 000"]
[25.45,null,"Number of operation counter display digits",null,6]
[25.46,null,"Supply voltage","V DC",220]
[25.47,null,"Reset",null,"No"]
[]
[26,"3.8.4","Cable and Busbar Live Indicators"]
[26.1,null,"Manufacturer",null,"xxx"]
[26.2,null,"Type",null,"xxx"]
[26.3,null,"Model",null,"xxx"]
[]
[27,"3.8.5","Wiring and Cable Lugs"]
[27.1,"a) ","Control wiring lugs",null,"0.00-10341"]
[27.2,"b)","Crimping on of power lugs shall be in accordance with   SANS 61238-1",null,"Yes"]
[]
[28,"3.8.6","Nameplates and Labels"]
[28.1,null,"Designation of equipment",null,"Yes"]
[28.2,null,"Main labels",null,"Yes"]
[28.3,null,"Circuit description labels",null,"Yes"]
[28.4,null,"Component labels",null,"Yes"]
[28.5,null,"Operating Labels",null,"Yes"]
[]
[29,3.9,"SWITCHGEAR AND INTERLOCKS SYSTEMS"]
[]
[29.1,null,"All interlocks as stipulated in 240-56227573",null,"Yes"]
[]
[30,{"v":3.1,"d":"3.10"},"TESTING"]
[]
[30.1,"3.10.1","Type Testing"]
[30.2,null,"Schedule C completed fully (on Appendix C of 240-56227573)",null,"Yes"]
[30.3,null,"All relevant reports available",null,"Yes"]
[30.4,null,"Reports available in accordance with IEC standards",null,"Yes"]
[30.5,null,"Reports in English",null,"Yes"]
[30.6,"g)","Testing authority of a laboratory accredited by a full member (MRA signatory) of ILAC (International Laboratory Accreditation Cooperation)",null,"Yes"]
[]
[31,"3.10.2","Routine Testing"]
[]
[31.1,null,"Provision made for Factory Acceptance Testing (FAT)",null,"Yes"]
[31.2,null,"Location where FAT will be performed",null,"Yes"]
[31.3,null,"Provision made for Site Acceptance Testing",null,"Yes"]
[]
[32,"3.10.3","Special Test – Open door LV compartment"]
[]
[32.1,null,"Type tests performed with LV compartment door open or removed",null,"Yes"]
[32.2,null,"Duration of the test with LV compartment door open","s",1]
[32.3,"a) 1)","The internal arc test shall be carried out in accordance with SANS 62271-200"]
[32.4,"   2)","The test shall be carried out on compartments that are adjacent to the LV compartment"]
[32.5,"b)","Type test laboratory used to perform special test shall be accredited as a full member (MRA signatory) of ILAC (International Laboratory Accreditation Cooperation)"]
[]
[33,3.11,"OPERATING AND MAINTENANCE"]
[]
[33.1,null,"Number of toolboxes for operating",null,"2 sets per substation"]
[33.2,null,"Number of toolboxes for maintenance",null,"2 sets per substation"]
[33.3,null,"Number of trolleys and associated lifting equipment required (cradle type switchgear)",null,"2 per substation per breaker type"]
[33.4,null,"Access Ladders",null,"2 per substation"]
[]
[34,3.12,"TRAINING"]
[34.1,null,"240-56065202 for the switchgear training requirements from original equipment manufacturers",null,"Yes"]
[]
[35,3.13,"DOCUMENTATION"]
[]
[36,"3.13.1","Language"]
[36.1,"a)","All documentation shall be in English Language",null,"Yes"]
[]
[37,"3.13.3","Manuals and Drawings"]
[37.1,"a)","The technical, training, maintenance and operating manuals shall be provided for each type (e.g. for different ratings, voltage levels etc.) of a functional unit",null,"Yes"]
[37.2,"d)","Drawings shall comply with 240-86973501 and 240-54690969",null,"Yes"]
[]
[37.3,null,"Drawings"]
[37.4,null,"Software format (Microstation)",null,"Microstation"]
[37.5,null,"Software copies","No. of drawings",2]
[37.6,null,"Hard copies","No. of drawings",5]
[]
[37.7,null,"Technical Manual"]
[37.8,null,"Equipment catalogue","Copies per type",5]
[37.9,null,"Equipment functional description manual","Copies per type",5]
[]
[{"v":37.1,"d":"37.10"},null,"Operating and Maintenance Manuals"]
[37.11,null,"Operating manual","Copies",5]
[37.12,null,"Maintenance manual","Copies",5]
[37.13,null,"Training manual","Copies",5]
[37.14,null,"Maintenance video/DVD","Copies",5]
[37.15,null,"Operating video/DVD","Copies",5]
[]
[38,3.14,"PACKAGE, TRANSPORTATION AND HANDLING"]
[]
[38.1,null,"Transportation"]
[38.2,null,"Dimensions of largest transport section:"]
[38.3,null,"Width","mm","xxx"]
[38.4,null,"Depth ","mm","xxx"]
[38.5,null,"Height ","mm","xxx"]
[]
[39,3.15,"SPARES"]
[]
[39.1,"3.15.1","Availability of Spares"]
[39.2,"a)","Availability of spare parts required for maintenance from the date of discontinuation of the switchgear and controlgear",null,"More than 25 years"]
[39.3,"b)","Spares required under emergency breakdown conditions shall be readily available with a maximum lead time of 96 hours from date of purchase order",null,"xxx"]
[39.4,"c)","The following spares shall be readily available locally (in South Africa) within 96 hours:"]
[39.5,null,"Trip coils",null,"xxx"]
[39.6,null,"Closing coils",null,"xxx"]
[39.7,null,"Under voltage release coils",null,"xxx"]
[39.8,null,"Spring charging motors",null,"xxx"]
[39.9,null,"Racking motors",null,"xxx"]

{"sheet":"Deviation Schedule","index":2,"n_rows":14,"n_cols":3,"rows_kept":14,"merged":[[0,0,0,2],[3,0,3,2],[4,0,4,2],[5,0,5,2],[6,0,6,2],[7,0,7,2],[8,0,8,2],[10,0,10,2],[12,0,12,2]],"flags":["formulas_cached_only"]}
[" EXCLUSIONS, ADDITIONS AND DEVIATIONS"]
[]
[]
[]
["NOTES:"]
[]
["1. Any deviations/modifications/alternatives offered to specification are listed below with reasons for the departure."]
[]
["2. No deviations/modifications/alternatives offered to the specification are recognised unless listed on this Schedule."]
[]
["3. If no deviations/modifications/alternatives are offered, this Schedule are marked N/A"]
[]
[]
["Schedule Item no.","Item Description","Proposed deviation/ Modification/Alternative"]

{"sheet":"Technical Schedule C","index":3,"n_rows":90,"n_cols":13,"rows_kept":90,"merged":[[1,1,1,4],[5,1,5,2],[5,3,5,5],[5,6,5,7],[5,8,5,9],[5,10,5,11],[5,12,5,13],[6,1,6,2],[6,3,6,5],[6,6,6,7],[6,8,6,9],[6,10,6,11],[6,12,6,13],[7,1,7,2],[7,3,7,5],[7,6,7,7],[7,8,7,9],[7,10,7,11],[7,12,7,13],[8,1,8,2],[8,3,8,5],[8,6,8,7],[8,8,8,9],[8,10,8,11],[8,12,8,13],[9,1,9,2],[9,3,9,5],[9,6,9,7],[9,8,9,9],[9,10,9,11],[9,12,9,13],[10,1,10,2],[10,3,10,5],[10,6,10,7],[10,8,10,9],[10,10,10,11],[10,12,10,13],[11,1,11,2],[11,3,11,5],[11,6,11,7],[11,8,11,9],[11,10,11,11],[11,12,11,13],[12,1,12,2],[12,3,12,5],[12,6,12,7],[12,8,12,9],[12,10,12,11],[12,12,12,13],[13,1,13,2],[13,3,13,5],[13,6,13,7],[13,8,13,9],[13,10,13,11],[13,12,13,13],[14,1,14,2],[14,3,14,5],[14,6,14,7],[14,8,14,9],[14,10,14,11],[14,12,14,13],[15,1,15,2],[15,3,15,5],[15,6,15,7],[15,8,15,9],[15,10,15,11],[15,12,15,13],[16,1,16,2],[16,3,16,5],[16,6,16,7],[16,8,16,9],[16,10,16,11],[16,12,16,13],[17,1,17,2],[17,3,17,5],[17,6,17,7],[17,8,17,9],[17,10,17,11],[17,12,17,13],[18,1,18,2],[18,3,18,5],[18,6,18,7],[18,8,18,9],[18,10,18,11],[18,12,18,13],[19,1,19,2],[19,3,19,5],[19,6,19,7],[19,8,19,9],[19,10,19,11],[19,12,19,13],[20,1,20,2],[20,3,20,5],[20,6,20,7],[20,8,20,9],[20,10,20,11],[20,12,20,13],[21,1,21,2],[21,3,21,5],[21,6,21,7],[21,8,21,9],[21,10,21,11],[21,12,21,13],[22,1,22,2],[22,3,22,5],[22,6,22,7],[22,8,22,9],[22,10,22,11],[22,12,22,13],[23,1,23,2],[23,3,23,5],[23,6,23,7],[23,8,23,9],[23,10,23,11],[23,12,23,13],[24,1,24,2],[24,3,24,5],[24,6,24,7],[24,8,24,9],[24,10,24,11],[24,12,24,13],[25,1,25,2],[25,3,25,5],[25,6,25,7],[25,8,25,9],[25,10,25,11],[25,12,25,13],[26,1,26,2],[26,3,26,5],[26,6,26,7],[26,8,26,9],[26,10,26,11],[26,12,26,13],[32,1,32,7],[34,1,34,2],[34,3,34,5],[34,6,34,7],[34,8,34,9],[34,10,34,11],[34,12,34,13],[35,1,35,2],[35,3,35,5],[35,6,35,7],[35,8,35,9],[35,10,35,11],[35,12,35,13],[36,1,36,2],[36,3,36,5],[36,6,36,7],[36,8,36,9],[36,10,36,11],[36,12,36,13],[37,1,37,2],[37,3,37,5],[37,6,37,7],[37,8,37,9],[37,10,37,11],[37,12,37,13],[38,1,38,2],[38,3,38,5],[38,6,38,7],[38,8,38,9],[38,10,38,11],[38,12,38,13],[39,1,39,2],[39,3,39,5],[39,6,39,7],[39,8,39,9],[39,10,39,11],[39,12,39,13],[40,1,40,2],[40,3,40,5],[40,6,40,7],[40,8,40,9],[40,10,40,11],[40,12,40,13],[41,1,41,2],[41,3,41,5],[41,6,41,7],[41,8,41,9],[41,10,41,11],[41,12,41,13],[42,1,42,2],[42,3,42,5],[42,6,42,7],[42,8,42,9],[42,10,42,11],[42,12,42,13],[43,1,43,2],[43,3,43,5],[43,6,43,7],[43,8,43,9],[43,10,43,11],[43,12,43,13],[44,1,44,2],[44,3,44,5],[44,6,44,7],[44,8,44,9],[44,10,44,11],[44,12,44,13],[45,1,45,2],[45,3,45,5],[45,6,45,7],[45,8,45,9],[45,10,45,11],[45,12,45,13],[46,1,46,2],[46,3,46,5],[46,6,46,7],[46,8,46,9],[46,10,46,11],[46,12,46,13],[47,1,47,2],[47,3,47,5],[47,6,47,7],[47,8,47,9],[47,10,47,11],[47,12,47,13],[48,1,48,2],[48,3,48,5],[48,6,48,7],[48,8,48,9],[48,10,48,11],[48,12,48,13],[49,1,49,2],[49,3,49,5],[49,6,49,7],[49,8,49,9],[49,10,49,11],[49,12,49,13],[50,1,50,2],[50,3,50,5],[50,6,50,7],[50,8,50,9],[50,10,50,11],[50,12,50,13],[51,1,51,2],[51,3,51,5],[51,6,51,7],[51,8,51,9],[51,10,51,11],[51,12,51,13],[52,1,52,2],[52,3,52,5],[52,6,52,7],[52,8,52,9],[52,10,52,11],[52,12,52,13],[53,1,53,2],[53,3,53,5],[53,6,53,7],[53,8,53,9],[53,10,53,11],[53,12,53,13],[54,1,54,2],[54,3,54,5],[54,6,54,7],[54,8,54,9],[54,10,54,11],[54,12,54,13],[55,1,55,2],[55,3,55,5],[55,6,55,7],[55,8,55,9],[55,10,55,11],[55,12,55,13],[60,1,60,7],[62,1,62,2],[62,3,62,5],[62,6,62,7],[62,8,62,9],[62,10,62,11],[62,12,62,13],[63,1,63,2],[63,3,63,5],[63,6,63,7],[63,8,63,9],[63,10,63,11],[63,12,63,13],[64,1,64,2],[64,3,64,5],[64,6,64,7],[64,8,64,9],[64,10,64,11],[64,12,64,13],[65,1,65,2],[65,3,65,5],[65,6,65,7],[65,8,65,9],[65,10,65,11],[65,12,65,13],[66,1,66,2],[66,3,66,5],[66,6,66,7],[66,8,66,9],[66,10,66,11],[66,12,66,13],[67,1,67,2],[67,3,67,5],[67,6,67,7],[67,8,67,9],[67,10,67,11],[67,12,67,13],[68,1,68,2],[68,3,68,5],[68,6,68,7],[68,8,68,9],[68,10,68,11],[68,12,68,13],[69,1,69,2],[69,3,69,5],[69,6,69,7],[69,8,69,9],[69,10,69,11],[69,12,69,13],[70,1,70,2],[70,3,70,5],[70,6,70,7],[70,8,70,9],[70,10,70,11],[70,12,70,13],[71,1,71,2],[71,3,71,5],[71,6,71,7],[71,8,71,9],[71,10,71,11],[71,12,71,13],[72,1,72,2],[72,3,72,5],[72,6,72,7],[72,8,72,9],[72,10,72,11],[72,12,72,13],[73,1,73,2],[73,3,73,5],[73,6,73,7],[73,8,73,9],[73,10,73,11],[73,12,73,13],[74,1,74,2],[74,3,74,5],[74,6,74,7],[74,8,74,9],[74,10,74,11],[74,12,74,13],[75,1,75,2],[75,3,75,5],[75,6,75,7],[75,8,75,9],[75,10,75,11],[75,12,75,13],[76,1,76,2],[76,3,76,5],[76,6,76,7],[76,8,76,9],[76,10,76,11],[76,12,76,13],[77,1,77,2],[77,3,77,5],[77,6,77,7],[77,8,77,9],[77,10,77,11],[77,12,77,13],[78,1,78,2],[78,3,78,5],[78,6,78,7],[78,8,78,9],[78,10,78,11],[78,12,78,13],[79,1,79,2],[79,3,79,5],[79,6,79,7],[79,8,79,9],[79,10,79,11],[79,12,79,13],[80,1,80,2],[80,3,80,5],[80,6,80,7],[80,8,80,9],[80,10,80,11],[80,12,80,13],[81,1,81,2],[81,3,81,5],[81,6,81,7],[81,8,81,9],[81,10,81,11],[81,12,81,13],[82,1,82,2],[82,3,82,5],[82,6,82,7],[82,8,82,9],[82,10,82,11],[82,12,82,13],[83,1,83,2],[83,3,83,5],[83,6,83,7],[83,8,83,9],[83,10,83,11],[83,12,83,13],[87,1,87,7],[89,1,89,2],[89,3,89,5],[89,6,89,7],[89,8,89,9],[89,10,89,11],[89,12,89,13],[90,1,90,2],[90,3,90,5],[90,6,90,7],[90,8,90,9],[90,10,90,11],[90,12,90,13],[91,1,91,2],[91,3,91,5],[91,6,91,7],[91,8,91,9],[91,10,91,11],[91,12,91,13],[92,1,92,2],[92,3,92,5],[92,6,92,7],[92,8,92,9],[92,10,92,11],[92,12,92,13],[93,1,93,2],[93,3,93,5],[93,6,93,7],[93,8,93,9],[93,10,93,11],[93,12,93,13],[94,1,94,2],[94,3,94,5],[94,6,94,7],[94,8,94,9],[94,10,94,11],[94,12,94,13],[95,1,95,2],[95,3,95,5],[95,6,95,7],[95,8,95,9],[95,10,95,11],[95,12,95,13],[96,1,96,2],[96,3,96,5],[96,6,96,7],[96,8,96,9],[96,10,96,11],[96,12,96,13],[97,1,97,2],[97,3,97,5],[97,6,97,7],[97,8,97,9],[97,10,97,11],[97,12,97,13],[98,1,98,2],[98,3,98,5],[98,6,98,7],[98,8,98,9],[98,10,98,11],[98,12,98,13],[99,1,99,2],[99,3,99,5],[99,6,99,7],[99,8,99,9],[99,10,99,11],[99,12,99,13],[100,1,100,2],[100,3,100,5],[100,6,100,7],[100,8,100,9],[100,10,100,11],[100,12,100,13],[101,1,101,2],[101,3,101,5],[101,6,101,7],[101,8,101,9],[101,10,101,11],[101,12,101,13],[102,1,102,2],[102,3,102,5],[102,6,102,7],[102,8,102,9],[102,10,102,11],[102,12,102,13],[103,1,103,2],[103,3,103,5],[103,6,103,7],[103,8,103,9],[103,10,103,11],[103,12,103,13],[104,1,104,2],[104,3,104,5],[104,6,104,7],[104,8,104,9],[104,10,104,11],[104,12,104,13],[105,1,105,2],[105,3,105,5],[105,6,105,7],[105,8,105,9],[105,10,105,11],[105,12,105,13],[106,1,106,2],[106,3,106,5],[106,6,106,7],[106,8,106,9],[106,10,106,11],[106,12,106,13],[107,1,107,2],[107,3,107,5],[107,6,107,7],[107,8,107,9],[107,10,107,11],[107,12,107,13],[108,1,108,2],[108,3,108,5],[108,6,108,7],[108,8,108,9],[108,10,108,11],[108,12,108,13],[109,1,109,2],[109,3,109,5],[109,6,109,7],[109,8,109,9],[109,10,109,11],[109,12,109,13],[110,1,110,2],[110,3,110,5],[110,6,110,7],[110,8,110,9],[110,10,110,11],[110,12,110,13]],"flags":["formulas_cached_only"]}
[]
[null,"Schedule C: Type Testing Requirements"]
[]
[null,"Schedule C1: Switchgear and Controlgear (Switchboards) - Functional Units  SANS 62271-1 and SANS 62271-200"]
[]
[null,"Applicable  Clauses for SANS 62271-1 and SANS 62271-200",null,"Type Test ",null,null,"Equipment to which Applicable",null,"Panel type and Rating",null,"Report/Certificate Number",null,"Testing Authority"]
{"$rows_empty":26}
[null,"Schedule C2: Switchgear and Controlgear (Switchboards) - Circuit-breakers  SANS 62271-100"]
[]
[null,"Applicable  Clause for SANS 62271-1 and SANS 62271-100",null,"Type Test ",null,null,"Equipment to which Applicable",null,"Panel type and Rating",null,"Report/Certificate Number",null,"Testing Authority"]
{"$rows_empty":25}
[null,"Schedule C3: Switchgear and Controlgear (Switchboards) - Earthing Switches  SANS 62271-102"]
[]
[null,"Applicable  Clause for SANS 62271-1 and SANS 62271-102",null,"Type Test ",null,null,"Equipment to which Applicable",null,"Panel type and Rating",null,"Report/Certificate Number",null,"Testing Authority"]
{"$rows_empty":24}
[null,"Schedule C4: Switchgear associated Components - Current Transformers and Voltage Transformers"]
[]
[null,"Applicable  Clause for SANS 61869-1, SANS 61869-2 and SANS 61869-3",null,"Type Test ",null,null,"Equipment to which Applicable",null,"Panel type and Rating",null,"Report/Certificate Number",null,"Testing Authority"]