# Sentech Content Media Operations IP Managed Switched Outlet PDU

# Project Overview:

Sentech  Content Media Operations requires Smart PDUs that are IP Managed, IP Switched Power Outlets and with Power Socket level Proactive Overload Protection.

# Specifications:

The following are the specifications for the PDUs that will be installed:

- Power Distribution Units (PDUs): 4  x units of IP Managed Switched Outlet PDUs, with minimum of 20 Switched Power Outlets(IEC) per PDU.

- Proactive Overload Protection means that each of the IEC Power outlet should switch off when overloading, this is different to bank level overload protection.

Note: Each PDU should be Managed by Web Browser or Application and terminate on 32A 2P plus earth Industrial Plug.

# Scope of Work:

The scope of work for this project includes several key activities:

- Installation of PDUs supplied.

- On-Site Demonstration of how the PDUs IP Address is configured

- On-Site Demonstration of how the PDUs power outlets are switched individually remotely(Web Browser)

- Demonstrate Proactive Overload Protection per power socket outlet

- Provide full documentation of the PDUs, Datasheets and Manuals as PDFs

- Perform User Acceptance Tests that will demonstrate all the Mandatory Criteria Items.

Administrative Compliance Before Site Handover:

- Completion of OHS/Safety file spec & sect 37 agreement to be provided

- National Key Point Security Clearance of the person(s) for on-site for installations, this includes screening interviews.