{"text_format":"3","workbook":"xls","n_sheets":7,"sheets":["1 P& G","Summary","Bill 2 - MV OHL","Bill 3 - Pole Mounted Tfrf","Bill 4 - LV Retic","Bill 5 -  Service Connections","Bill 6 - Dismantling"],"not_rendered":{"external_links":3,"defined_names":31},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"1 P& G","index":0,"n_rows":43,"n_cols":7,"rows_kept":43,"merged":[[2,5,2,6],[3,1,4,2],[3,5,3,6]],"flags":["formulas_cached_only"]}
[]
[null,"BILL NO 1 - PRELIMINARY AND GENERAL"]
[]
[{"$nulls":5},"PRICE (EXCL VAT)"]
[]
[null,1.1,"Provision for compliance with all the General Conditions of Contract, Special Conditions of Contract, All necessary insurances required to adequately cover the works, Workmans Compensation, Travelling, Out-of-Town Allowance, Maintenance and Guarantee ","Sum",1,null,0]
[null,1.2,"Establish facilities on site. The Contractor shall provide a fenced space with fence at least 1.8m high with a lockable gate for a temporary Site Office and Stores where all drawings and Specifications will be kept, as well as the provision of safe and secure staorage - The length of the fence shall be 300m","Sum",1,null,0]
[null,1.3,"Facilities for Contractor :",{"$nulls":3},0]
[null,null,"a)  Offices & storage sheds","Sum",1,null,0]
[null,null,"b)  Establishment of staff accommodation, office accommodation on site for site meetings and a Clerk of Works including office furniture and telephone / telefax as specified and facilities.","Sum",1,null,0]
[null,null,"c)  Ablution & latrine facilities","Sum",1,null,0]
[null,null,"e)  Water supplies, electric power & communications","Sum",1,null,0]
[null,1.4,"Removal of all items indicated above upon completion of construction and making good and restoring of the Site to the satisfaction of the Project Manager.","Sum",1,null,0]
[null,1.5,"Provision of \"As Built\" drawings.","Sum",1,null,0]
[null,1.6,"The Contractor shall make an order for one project signboard bearing the name of the project, the name and logo of the Client, and the Contractor.","Sum",1,null,0]
[null,1.7,"Provision for Legal and Contractual Compliance.","Sum",1,null,0]
[null,1.8,"Provision of personal protective equipment and clothing for all the contractor's staff, including sub-contractors.","Sum",1,null,0]
[null,1.9,"Provision of safety measures, e.g.. Fall arrest systems, shoring for safety purposes etc.","Sum",1,null,0]
[null,{"v":1.1,"d":"1.10"},"Compliance with OH&S Act & Construction Regulations.","Sum",1,null,0]
[null,1.11,"Compliance with the Requirements for the Expanded Public Works Programme (incl. monthly reports).","Sum",1,null,0]
[null,1.12,"The Contractor shall make allowance to receive, transport to site, offload and stack the materials supplied to the contract. The rate shall also include the implementation and maintenance of a Materials Management System for the duration of the contract.","Sum",1,null,0]
[null,1.13,"On Completion of the project, all dismantled materials (transformers, mini-subs etc.) shall be reconciled and quantified. Once authorised by the Consultant/Project Manager, this materials shall be transported to Client stores using the correct material return forms.","Sum",1,null,0]
[null,1.14,"Operate and Maintain Facilities on Site(Time Related Items)"]
[null,null,"Facilities for Contractor:"]
[null,null,"a)  Offices & storage sheds","Month",4,null,0]
[null,null,"b)  Ablution & latrine facilities","Month",4,null,0]
[null,null,"d)  Water supplies, electric power & communications","Month",4,null,0]
[null,1.15,"Provision of office accommodation on site for site meetings and a Clerk of Works including office furniture and telephone / telefax as specified.","Month",4,null,0]
[null,1.16,"Contract management and full time supervision of the works","Month",4,null,0]
[null,1.17,"Outage Management ","Month",4,null,0]
[null,1.18,"Community Liaison Officer conversant in Xhosa and local cultural norms","Month",4,{"v":5000,"d":"R 5,000.00"},{"v":20000,"d":"R 20,000.00"}]
[null,1.19,"Provision for a trainee in electrical Engineering - Client to appoint Student ","Month",4,0,0]
[null,{"v":1.2,"d":"1.20"},"Social Facilitation Fees (Service Provider directly accountable to Client to ISD Services)","Month",4,{"v":5000,"d":"R 5,000.00"},{"v":20000,"d":"R 20,000.00"}]
[null,1.21,"Contractor to make a provision for a project Sample line to Eskom standard as per latest revision. This is available at Eskom T & Q department in ECOU","Sum",1,null,0]
[null,1.22,"Contractor shall provide security guard/s to ensure the construction site including offices, storage sheds and all material are protected from theft or any damage. The Contractor needs to ensure that the above mentioned is guarded 24hrs a day.","Month",3,{"v":7000,"d":"R 7,000.00"},{"v":21000,"d":"R 21,000.00"}]
[null,1.23,"Special Services - All special services, service provider to be appointed by Consultant"]
[null,null,"Detailed Land Suvery which include re-pegging and profiling for As-Builts that will be submitted to Eskom for Memos and Commissioning stage ","Sum",1,{"v":50000,"d":"R 50,000.00"},{"v":50000,"d":"R 50,000.00"}]
[null,"1.23.1","Allow for compliance with the WMM Local Municipality Environmental Specification on MV/LV Environmental studies application & DAFF tree cutting licence ","Sum",1,{"v":5000,"d":"R 5,000.00"},{"v":5000,"d":"R 5,000.00"}]
[null,"1.23.2","Provision for Detailed Marketing Service by the accredited sub-contractor appointed by Consulting Engineer .","Sum",1,{"v":5000,"d":"R 5,000.00"},{"v":5000,"d":"R 5,000.00"}]
[null,"1.23.3","Provision for Clerk of Works Services to ensure the quality of the project and to ensure that the contractor purchases Eskom approved material from approved suppliers.","Sum",1,{"v":5000,"d":"R 5,000.00"},{"v":5000,"d":"R 5,000.00"}]
[null,1.25,"Social Facilitation Fees (Service Provider directly accountable to Client to ISD Services)","Sum",0,{"v":100000,"d":"R 100,000.00"},0]
[null,1.25,"Professional Fees (Professional Service Provider directly accountable to Client to Provide Consulting Services)","Sum",0,{"v":100000,"d":"R 100,000.00"},0]
[null,null,"Total - Failure to include the highlighted provisional sums to the totals, the BOQ will be deemed as incomplete and the bidder will be disqualified."]

{"sheet":"Summary","index":1,"n_rows":60,"n_cols":9,"rows_kept":60,"merged":[[2,1,2,4],[3,1,3,2],[10,1,10,3],[11,1,11,3],[12,1,12,3],[13,1,13,3],[14,1,14,3]],"flags":["formulas_cached_only"]}
[]
[]
[]
[null,"ITEM",null,"DESCRIPTION","PRICE"]
[null,"1.","Bill 1","Preliminary & General",0]
[null,"2.","Bill 2","MV Overhead Line",0]
[null,"3.","Bill 3","Pole Mounted Transformers",0]
[null,"4.","Bill 4","LV Reticulation",0]
[null,"5.","Bill 5","Service Connections",0]
[null,6,"Bill 6","Dismantling & Enviromental",0]
[null,"Sub - Total A",null,null,0,null,276,0]
[null,"Contigency @ 10%",null,null,0]
[null,"Sub - Total B",null,null,0]
[null,"VAT",null,null,0]
[null,"TOTAL TENDER PRICE (including VAT)",null,null,0,null,null,{"v":1076547.85,"d":"R 1,076,547.85"}]
[{"$nulls":7},{"v":0.045,"d":"4.50%"},{"v":48444.65325,"d":"R 48,444.65"}]
[{"$nulls":7},{"v":0.04,"d":"4%"},{"v":43061.914000000004,"d":"R 43,061.91"}]
[{"$nulls":3},"Material Cost","Quantity",null,"Rate ","Total Cost"]
[{"$nulls":3},"(J) 10m Wood Pole - 200mm - 219mm Top Diameter",20,null,{"v":803.6,"d":"R 803.60"},{"v":16072,"d":"R 16,072.00"},{"v":788271.5,"d":"R 788,271.50"}]
[{"$nulls":3},"(K) 11m Wood Pole - 160mm - 179mm Top Diameter",95,null,{"v":778.85,"d":"R 778.85"},{"v":73990.75,"d":"R 73,990.75"},{"v":288276.35,"d":"R 288,276.35"}]
[{"$nulls":3},"(L) 11m Wood Pole - 180mm - 199mm Top Diameter",64,null,{"v":753.34,"d":"R 753.34"},{"v":48213.76,"d":"R 48,213.76"},{"v":1076547.85,"d":"R 1,076,547.85"}]
[{"$nulls":3},"(M) 11m Wood Pole - 200mm - 219mm Top Diameter",14,null,{"v":1209.94,"d":"R 1,209.94"},{"v":16939.16,"d":"R 16,939.16"},4]
[{"$nulls":3},"(C) 7m Wood Pole - 120mm - 139mm Top Diameter",242,null,{"v":207.3,"d":"R 207.30"},{"v":50166.600000000006,"d":"R 50,166.60"},3500]
[{"$nulls":3},"(D) 9m Wood Pole - 140mm - 159mm Top Diameter",48,null,{"v":343.55,"d":"R 343.55"},{"v":16490.4,"d":"R 16,490.40"},14000]
[{"$nulls":7},0]
[{"$nulls":3},"Conductor, ACSR Fox 8.37D Ungreased",28500,null,{"v":3.86,"d":"R 3.86"},{"v":110010,"d":"R 110,010.00"}]
[{"$nulls":3},"Cond, Aerial Bund 2 Core XLPE 35mmSQ Insulated Neutral",6864,null,{"v":25.26,"d":"R 25.26"},{"v":173384.64,"d":"R 173,384.64"}]
[{"$nulls":3},"Cond, Aerial Bund 3 Core XLPE 35mmSQ Insulated Neutral",10783,null,{"v":22.93,"d":"R 22.93"},{"v":247254.19,"d":"R 247,254.19"}]
[{"$nulls":3},"Cond, Aerial Bund 4 Core XLPE 35mmSQ Insulated Neutral",null,null,{"v":40.8,"d":"R 40.80"},0]
[{"$nulls":3},"Cond, Aerial Bund 2 Core XLPE 70mmSQ Insulated Neutral",null,null,{"v":28.72,"d":"R 28.72"},0]
[{"$nulls":3},"Cond, Aerial Bund 3 Core XLPE 70mmSQ Insulated Neutral",{"$nulls":3},0]
[{"$nulls":3},"Cond, Aerial Bund 4 Core XLPE 70mmSQ Insulated Neutral",null,null,{"v":71.53,"d":"R 71.53"},0]
[{"$nulls":3},"Cable 1kV 2C 4mm sq Concentric Cu",5000,null,{"v":7.15,"d":"R 7.15"},{"v":35750,"d":"R 35,750.00"}]
[{"$nulls":3},"Cable 1kV 2C 10mm sq Concentric Cu",null,null,{"v":14.3,"d":"R 14.30"},0]
[{"$nulls":7},0]
[{"$nulls":3},"Meter,Std ECU Keypad 20A",161,null,{"v":93,"d":"R 93.00"},{"v":14973,"d":"R 14,973.00"},{"v":49749,"d":"R 49,749.00"}]
[{"$nulls":3},"Passive Base Unit,ECU/CBU with Rail",161,null,{"v":216,"d":"R 216.00"},{"v":34776,"d":"R 34,776.00"}]
[{"$nulls":7},0]
[{"$nulls":3},"Link and Transformer Identification Label",49,null,{"v":55,"d":"R 55.00"},{"v":2695,"d":"R 2,695.00"}]
[{"$nulls":3},"Danger Sign (Electrical safety) 150 x 150 x 0.6mm",49,null,{"v":12,"d":"R 12.00"},{"v":588,"d":"R 588.00"}]
[{"$nulls":3},"Warning Fuse Label",22,null,{"v":10,"d":"R 10.00"},{"v":220,"d":"R 220.00"}]
[{"$nulls":3},"Transformer Maximum Fuse Label",19,null,{"v":15,"d":"R 15.00"},{"v":285,"d":"R 285.00"}]
[{"$nulls":3},"Feeder Maximum Fuse Label",22,null,{"v":15,"d":"R 15.00"},{"v":330,"d":"R 330.00"}]
[{"$nulls":3},"Pole Top Box (PTB) Phase Label",161,null,{"v":2.5,"d":"R 2.50"},{"v":402.5,"d":"R 402.50"}]
[{"$nulls":3},"Loose Fonts",5000,null,{"v":2.7,"d":"R 2.70"},{"v":13500,"d":"R 13,500.00"}]
[{"$nulls":7},0]
[{"$nulls":3},"Transformer 16kVA - 22kV/240V Single Pole Mount",6,null,{"v":8925.63,"d":"R 8,925.63"},{"v":53553.78,"d":"R 53,553.78"}]
[{"$nulls":3},"Transformer 32kVA - 22kV/+/- 240V Single Pole Mount",13,null,{"v":16669.39,"d":"R 16,669.39"},{"v":216702.07,"d":"R 216,702.07"}]
[{"$nulls":3},"Transformer 50kVA - 22kV/415V Single Pole Mount",null,null,{"v":21812.57,"d":"R 21,812.57"},0]
[{"$nulls":3},"Transformer 100kVA - 22kV/415V Single Pole Mount",null,null,{"v":29281.06,"d":"R 29,281.06"},0]
[{"$nulls":3},"Recloser 11+22kV 400A 8kA IRTU",null,null,{"v":86558,"d":"R 86,558.00"},0]
[{"$nulls":3},"Installation cost for SB",null,null,{"v":100000,"d":"R 100,000.00"},0]
[]
[]
[{"$nulls":6},{"v":49749,"d":"R 49,749.00"}]
[{"$nulls":6},{"v":3470706.15,"d":"R 3,470,706.15"}]
[{"$nulls":6},{"v":156181.78,"d":"R 156,181.78"}]
[{"$nulls":6},{"v":138828.25,"d":"R 138,828.25"}]
[{"$nulls":6},{"v":14000,"d":"R 14,000.00"}]
[{"$nulls":6},{"v":3829465.1799999997,"d":"R 3,829,465.18"}]

{"sheet":"Bill 2 - MV OHL","index":2,"n_rows":115,"n_cols":9,"rows_kept":115,"merged":[[0,6,2,8],[1,1,1,3],[5,2,5,3],[21,2,21,3],[25,2,25,3],[32,2,32,3],[37,2,37,3],[39,1,39,7],[40,1,40,7],[42,2,42,3],[49,2,49,3],[50,2,50,3],[52,2,52,3],[55,2,55,3],[58,2,58,3],[64,2,64,3],[72,1,72,7],[73,1,73,7],[75,2,75,3],[78,2,78,3],[114,1,114,7]],"flags":["formulas_cached_only"]}
[]
[null,"BILL 2 - MV OVERHEAD LINE"]
[]
[null,"ITEM","DESCRIPTION","DWG NO.","UNIT","QTY","SUPPLY","INSTALL","TOTAL"]
[null,2,"Medium Voltage Structures - General Arrangement"]
[null,null,"Supply & install, the unit rate shall include the transportation, materials (including x-arms) & labour required to assemble & erect the following structure types as per the structure drawing. The unit rate shall include the supply & installation of bonding, non-tension joints, insulator ties & deadend preforms to attach the conductor to the insulator hardware.                               "]
[null,2.1,"2 Phase Structures"]
[null,"2.1.1","Phase / Phase - Delta / 2,5m Wood X-arm - Intermediate - 0° Dev.",{"v":1340,"d":"D-ER-1340B"},"No",1,null,null,0]
[null,"2.1.2","Phase / Phase - Delta / 2,5m Wood X-arm - Strain - 0° Dev.",{"v":1343,"d":"D-DT-1343"},"No",2,null,null,0]
[null,"2.1.3","Phase / Phase - Delta / 2,5m Wood X-arm - Strain - Medium (1° +  60°) Dev.",{"v":1344,"d":"D-DT-1344"},"No",2,null,null,0]
[null,"2.1.4","Phase / Phase - Delta / 2,5m Wood X-arm - Strain - Terminal",{"v":1346,"d":"D-DT-1346"},"No",2,null,null,0]
[null,2.2,"3 Phase Structures"]
[null,"2.2.1","3 Phase - Staggered Vertical 600 Spacing - Intermediate - 0° Dev.",{"v":1710,"d":"D-DT-1710"},"No",{"$nulls":3},0]
[null,"2.2.2","3 Phase - Delta / 2,5m Wood X-arm - Intermediate - 0° Dev.",{"v":1740,"d":"D-ER-1740B"},"No",8,null,null,0]
[null,"2.2.3","3 Phase - Delta / 2,5m Wood X-arm - Strain - 0° Dev.",{"v":1743,"d":"D-DT-1743"},"No",1,null,null,0]
[null,"2.2.4","3 Phase - Delta / 2,5m Wood X-arm - Strain - Medium (1° +  60°) Dev.",{"v":1744,"d":"D-DT-1744"},"No",12,null,null,0]
[null,"2.2.5","3 Phase - Delta / 2,5m Wood X-arm - Strain - Terminal",{"v":1746,"d":"D-DT-1746"},"No",4,null,null,0]
[null,2.3,"Medium Voltage Auxiliary Structure - General Arrangement"]
[null,"2.3.1","Phase / Phase Take-off - 2,5m Wooden X-arm",{"v":1814,"d":"D-DT-1814"},"No",{"$nulls":3},0]
[null,"2.3.2","3 Phase Take-off - 2,5m Wooden X-arm",{"v":1804,"d":"D-DT-1804"},"No",{"$nulls":3},0]
[null,2.4,"Section & Equipment Link Assemblies"]
[null,null,"Supply & install 200A / 24kV load break units, the unit rate shall include transportation, labour & materials, including a X-arm(s) required to assemble & secure the link assembly onto a wood pole structure in accordance with the drawing."]
[null,"2.4.1","A Set of Links - Cut-outs - 2,5m Wood X-arm / Single Pole (dual phase)",{"v":1848,"d":"D-DT-1848"},"No",2,null,null,0]
[null,"2.4.2","A Set of Links - Cut-outs - 2,5m Wood X-arm / Single Pole (Three phase)",{"v":1848,"d":"D-DT-1848"},"No",4,null,null,0]
[null,2.5,"Wood Poles "]
[null,null,"Supply & install, the unit rate shall include the transportation, materials  & labour required to assemble and erect the following wood poles as per the structure drawing.\nExcavations and compaction measured elsewhere."]
[null,"2.5.1","(K) 11m Wood Pole - 160mm - 179mm Top Diameter",{"v":51,"d":"D-DT-0051"},"No",4,null,null,0]
[null,"2.5.2","(L) 11m Wood Pole - 180mm - 199mm Top Diameter",{"v":51,"d":"D-DT-0051"},"No",13,null,null,0]
[null,"2.5.3","(T) 12m Wood Pole - 180mm - 199mm Top Diameter",{"v":53,"d":"D-DT-0053"},"No",12,null,null,0]
[null,"2.5.4","(U) 12m Wood Pole - 200mm - 219mm Top Diameter",{"v":53,"d":"D-DT-0053"},"No",{"$nulls":3},0]
[null,"2.5.5","(W) 13m Wood Pole - 180mm - 199mm Top Diameter",{"v":56,"d":"D-DT-0056"},"No",3,null,null,0]
[null,2.6,"New Medium Voltage Anchors - General Arrangement"]
[null,null,"Supply & install, the unit rate shall include the transportation, materials & labour required to assemble and install the following new anchor types as per the structure drawing.\nPoles, excavations and compaction measured elsewhere."]
[null,"2.6.1","MV Stay Assembly ",{"v":341,"d":"D-DT-0341"},"No",45,null,null,0]
[null,"2.6.2","MV Strut Assembly",{"v":342,"d":"D-DT-0342"},"No",4,null,null,0]
[null,"2.6.3","MV Flying Stay Assembly",{"v":343,"d":"D-DT-0343"},"No",{"$nulls":3},0]
[null,2.7,"BIL Lightning Downwire"]
[null,null,"Supply & install, the unit rate shall include the transportation, materials & labour required to install, where required, a 3 x 3.35mm galvanised steel lightning downwire."]
[null,"2.7.1","MV BIL Downwire",{"v":310,"d":"D-DT-0310"},"No",9,null,null,0]
[null,"SUB TOTAL (BILL 2) PAGE 1 B/F",{"$nulls":6},0]
[null,"SUB TOTAL (BILL 2) PAGE 1 C/F",{"$nulls":6},0]
[null,2.8,"Excavations & Compaction"]
[null,null,"The unit rate shall include the determination of the pole and stay position, the hand/auger/compressor or blasting excavation of the hole. The contractor is to provide adequate measures to ensure a rock hole be excavated to the correct depth to facilitate the correct infrastructure. The rate shall include the transportation, materials & labour required to backfill & compact to 93% MOD AASHTO density. Where necessary, the supply and installation of suitable imported soil. Soil may be mixed with cement at a ratio of 1/8 to achieve the specified compaction. The rate for the use of mechanical devices form part of normal excavations.\nAll barricading to comply with the requirements of T&Q Procedure TQAPP043.\n(Pole Planting depths to be as per drawing D-DT-0332)                                                                     \nAll rock holes  to be verified by the Clerk of Works prior to excavation. \n"]
[null,"2.8.1","1.8m Deep Pole Hole for an 11m Wood Pole",{"v":330,"d":"D-DT-0330"},"No",17,null,null,0]
[null,"2.8.2","2m Deep Pole Hole for an 12m Wood Pole",{"v":330,"d":"D-DT-0330"},"No",12,null,null,0]
[null,"2.8.3","2.2m Pole Hole for a 13m Wood Pole",{"v":56,"d":"D-DT-056"},"No",3,null,null,0]
[null,"2.8.4","MV Stay Hole ",{"v":350,"d":"D-DT-0350"},"No",45,null,null,0]
[null,"2.8.5","MV Flying Stay Hole",{"v":343,"d":"D-DT-0343"},"No",{"$nulls":3},0]
[null,"2.8.6","MV Strut Hole ",{"v":351,"d":"D-DT-0351"},"No",4,null,null,0]
[null,"2.8.7","Provision for Rock Drilling of  holes (Irrespective of depth of hole, each hole to be verified by Engineer Clerk of works, Client representative  and Project manager as per internal or external invoice) - This rate includes importing soil and transport - Specialist service provider to be appointed by Consultant",null,"No",70,null,{"v":1750,"d":"1,750.00"},{"v":122500,"d":"122,500.00"}]
[null,"2.8.8","Provision for Blasting of  holes (Irrespective of depth of hole, each hole to be verified by Engineer Clerk of works, Client representative  and Project manager) - This rate includes importing soil and transport - Specialist service provider to be appointed by Consultant",null,"No",90,null,{"v":2000,"d":"2,000.00"},{"v":180000,"d":"180,000.00"}]
[null,2.9,"Conductoring "]
[null,null,"Supply  & install, the unit rate shall include the transportation, materials & labour required for the running out of, regulating of & making off of the following conductor in accordance with the manufacturer / drawings. The rate to include the supply and installation of conductor line splicing (if required). Conductor to comply with Eskom standards."]
[null,"2.9.1","Fox Conductor, ACSR Fox 8.37D Ungreased",{"v":3136,"d":"D-DT-3136"},"m",{"v":6406,"d":"6,406"},null,null,0]
[null,{"v":2.1,"d":"2.10"},"Conductor Jumpers"]
[null,null,"Supply & install, the unit rate shall include transportation, labour & materials required to install jumpers between the overhead line and link base. The rate shall include a Tap connector/non-tension joint, UV stabilised, low density polyethylene (LDPE) pipe and a new lug to attach the conductor to the link base."]
[null,"2.10.1","6.3 - 9.0mm Fox Jumper Covered with LDPE Pipe","D-DT-3166 \nD-DT-3127 \nD-DT-3153 \nD-DT-3098","No",63,null,null,0]
[null,2.11,"Statutory Crossing Hardware"]
[null,null,"Supply & install, the unit rate shall include the transportation, materials & labour required to install, where specified / required, statutory crossing line hardware."]
[null,"2.11.1","Pistol Strain Clamp (3 bolt) 5.0mm - 16mm (Eberhardt Martin)",{"v":7022,"d":"D-DT-7022"},"No",50,null,null,0]
[null,"2.11.2","31mm/kV, 10kN Capped porcelain post insulator",{"v":3017,"d":"D-DT-3017"},"No",50,null,null,0]
[null,"2.11.3","Tie, Top Groove (road x-ing) Full Wrap - Fox",{"v":3211,"d":"D-DT-3211"},"No",50,null,null,0]
[null,"2.11.4","Bird Flappers",null,"No",100,null,null,0]
[null,2.12,"Labelling & Signage "]
[null,null,"Supply& install, the unit rate shall include transportation, labour & materials required to install labels on auxiliary medium voltage structures. "]
[null,"2.12.1","Link Identification Label","TQCSS005","No",6,null,null,0]
[null,"2.12.2","Danger Sign (Electrical safety) 150 x 150 x 0.6mm",{"v":3202,"d":"D-DT-3202"},"No",6,null,null,0]
[]
[]
[]
[]
[]
[null,"SUB TOTAL (BILL 2) PAGE 2 B/F"]
[null,"SUB TOTAL (BILL 2) PAGE 2 C/F"]
[null,2.13,"Anti-Climbing Device"]
[null,null,"Supply & install, the unit rate shall include transportation, labour & materials required to install anti-climbing devices on:                                                                                          \n1) All Equipment Structures,\n2) All MV Strut Assemblies, and\n3) All Easy-Climbable MV Stay Assemblies."]
[null,"2.13.1","Anti-Climbing Device, Galvanised Barbed Wire Helically Wound","D-DT-3170 \nD-DT- 0399","m",4,null,null,0]
[null,2.14,"Ancillary Line Hardware"]
[null,null,"Supply & install, the unit rate shall include the transportation, materials & labour required to install, where specified / required, ancillary line hardware."]
[null,"2.14.1","Spiral Vibration Damper (11.72mm - 14.30mm) & (8.29mm - 11.71mm)",{"v":3175,"d":"D-DT-3175"},"No",50,null,null,0]
{"$rows_empty":34}
[null,"TOTAL (BILL 2)",{"$nulls":6},0]

{"sheet":"Bill 3 - Pole Mounted Tfrf","index":3,"n_rows":77,"n_cols":9,"rows_kept":77,"merged":[[0,6,2,8],[1,1,1,2],[5,2,5,3],[6,2,6,3],[10,2,10,3],[16,2,16,3],[20,2,20,3],[24,2,24,3],[27,2,27,3],[31,2,31,3],[34,2,34,3],[38,1,38,7],[39,1,39,7],[41,2,41,3],[76,1,76,7]],"flags":["formulas_cached_only"]}
[]
[null,"BILL 3 - POLE MOUNTED TRANSFORMERS"]
[]
[null,"ITEM","DESCRIPTION","DWG NO.","UNIT","QTY","SUPPLY","INSTALL","TOTAL"]
[null,3.1,"Transformer Structures - General Arrangement"]
[null,null,"Supply & install, the unit rate shall include the transportation, materials (including x-arm on ool) & labour required to assemble, erect & secure the transformer on the following structure types as per the structure drawing. "]
[null,null,"Links, Labelling, surge arresters & earthing measured elsewhere"]
[null,"3.1.1","Transformer 16-100 kVA Single pole mounted 'general arrangement'","D-DT-1860","No",{"$nulls":3},0]
[null,"3.1.2","Transformer 16-100 kVA Single pole mounted 'out-of-line'","D-DT-1866B","No",8,null,null,0]
[null,3.2,"Transformers "]
[null,null,"The unit rate shall include labour and material required to install the 22kV transformers onto the wood pole structure. (The supply rate is to include all minor material and M20 X 350mm threaded rods that are require for the transformer installation)."]
[null,"3.2.1","Transformer 16kVA - 22kV/240V Single Pole Mount",{"v":270,"d":"D-DT-0270"},"No",{"$nulls":3},0]
[null,"3.2.2","Transformer 32kVA - 22kV/+/- 240V Single Pole Mount",{"v":270,"d":"D-DT-0270"},"No",1,null,null,0]
[null,"3.2.3","Transformer 64kVA - 22kV/+/- 240V Single Pole Mount",{"v":270,"d":"D-DT-0270"},"No",2,null,null,0]
[null,"3.2.4","Transformer 50kVA - 22kV/+/- 240V Single Pole Mount",{"v":270,"d":"D-DT-0270"},"No",4,null,null,0]
[null,3.3,"Surge Arresters"]
[null,null,"Supply & install,  the unit rate shall include transportation, labour & materials required to assemble & secure the dual surge arrestors assemblies onto the transformer tank, including the connections between the surge arrester and the transformer bushing. The rate shall include a galvanised steel double mounted bracket (D-DT-3227) for securing the dual surge arrestors, nuts, bolts, washers and lock washers as specified."]
[null,"3.3.1","Surge Arrester Distribution Class 1, 31mm/kV 22kV/10kA MCOV 19.2kV","D-DT-0261","No",18,null,null,0]
[null,"3.3.2","Neutral Surge Arrester Distribution Class 1, 6kV/10kA Gapless",{"v":3088,"d":"D-DT-3088"},"No",7,null,null,0]
[null,3.4,"Earthing - Crowfoot"]
[null,null,"Supply & install, the unit rate shall include transportation, labour & materials required for the complete earthing of a transformer structure including the connections, excavation & backfilling of the earth trenches. \nThe rate shall include an earth resistance test."]
[null,"3.4.1","MV Earth Electrode at Transformer",{"v":627,"d":"D-DT-0627"},"No",7,null,null,0]
[null,"3.4.2","LV Earth Electrode at Transformer",{"v":627,"d":"D-DT-0627"},"No",7,null,null,0]
[null,3.5,"Conductor Jumpers"]
[null,null,"Supply & install, the unit rate shall include transportation, labour & materials required to install jumpers between the overhead line and transformer. The rate shall include a Tap connector/non-tension joint, UV stabilised, low density polyethylene (LDPE) pipe and a new lug to secure the jumper to the transformer bushing."]
[null,"3.5.1","6.3 - 9.0mm Fox Jumper Covered with LDPE Pipe","D-DT-3166\nD-DT-3127\nD-DT-3153\nD-DT-3098","No",28,null,null,0]
[null,3.6,"Labelling & Signage "]
[null,null,"Supply & install, the unit rate shall include transportation, labour & materials required to install labels on auxiliary medium voltage structures."]
[null,"3.6.1","Transformer Identification Label","TQCSS005","No",7,null,null,0]
[null,"3.6.2","Danger Sign (Electrical safety) 150 x 150 x 0.6mm","TQCSS005","No",7,null,null,0]
[null,3.7,"Anti-climbing Device (Galvanised Barbed Wire Helically Wound)"]
[null,null,"Supply & install, the unit rate shall include transportation, labour & materials required to install anti-climbing devices on auxiliary medium voltage structures as depicted on auxiliary drawings."]
[null,"3.7.1","Anti-climbing Device (Barbed Wire) for Poles","D-DT-3170 \nD-DT- 0399","No",5,null,null,0]
[null,3.8,"Wood Poles "]
[null,null,"Supply & install, the unit rate shall include the transportation, materials  & labour required to assemble and erect the following wood poles as per the structure drawing."]
[null,"3.8.1","(J) 10m Wood Pole - 200mm - 219mm Top Diameter",{"v":52,"d":"D-DT-0052"},"No",8,null,null,0]
[]
[]
[null,"SUB TOTAL (BILL 3) PAGE 1 B/F",{"$nulls":6},0]
[null,"SUB TOTAL (BILL 3) PAGE 1 C/F",{"$nulls":6},0]
[null,3.9,"Excavations & Compaction"]
[null,null,"The unit rate shall include the determination of the pole and stay position, the hand/auger/compressor or blasting excavation of the hole. The contractor is to provide adequate measures to ensure a rock hole be excavated to the correct depth to facilitate the correct infrastructure. The rate shall include the transportation, materials & labour required to backfill & compact to 93% MOD AASHTO density. Where necessary, the supply and installation of suitable imported soil. Soil may be mixed with cement at a ratio of 1/8 to achieve the specified compaction. The rate for the use of mechanical devices form part of normal excavations.\nAll barricading to comply with the requirements of T&Q Procedure TQAPP043.\n(Pole Planting depths to be as per drawing D-DT-0332)                                                                     \nAll rock holes  to be verified by the Clerk of Works prior to excavation. \nNote: Blasting rate to include excavation, backfill and compaction."]
[null,"3.9.1","1.7m Deep Pole hole for a 10m Wood Pole",{"v":330,"d":"D-DT-0330"},"No",8,null,null,0]
{"$rows_empty":33}
[null,"TOTAL (BILL 3)",{"$nulls":6},0]

{"sheet":"Bill 4 - LV Retic","index":4,"n_rows":82,"n_cols":9,"rows_kept":82,"merged":[[0,6,2,8],[1,1,1,5],[4,2,4,3],[5,2,5,3],[10,2,10,3],[36,2,36,3],[41,2,41,3],[45,2,45,3],[49,1,49,7],[50,1,50,7],[52,2,52,3],[56,2,56,3],[63,2,63,3],[66,2,66,3],[81,1,81,7]],"flags":["formulas_cached_only"]}
[]
[null,"BILL 4 - LV RETICULATION"]
[]
[null,"ITEM","DESCRIPTION","DWG NO.","UNIT","QTY","SUPPLY","INSTALL","TOTAL"]
[null,"4.1","Low Voltage Conductor - LV ABC Insulated Neutral "]
[null,null,"Measured lengths for stringing shall be net line route lengths and unit rates shall include for sag and off-cuts.\nSupply & install, the unit rate shall include the transportation, materials and labour required to install the following LV insulated aerial bundle conductor. The system shall be in accordance with SABS 1418 and installed in accordance with SABS 0198.  The unit rate shall include the supply and install of aerial bundle conductor and stringing (incl. tensioning) of the new aerial bundle conductor."]
[null,"4.1.1","1 x 35mm2 phase conductors + 54.6mm2 insulated neutral","D-DT-3141","m",{"$nulls":3},0]
[null,"4.1.2","2 x 35mm2 phase conductors + 54.6mm2 insulated neutral","D-DT-3141","m",{"v":2240,"d":"2,240 "},null,null,0]
[null,"4.1.3","3 x 35mm2 phase conductors + 54.6mm2 insulated neutral","D-DT-3141","m",{"v":6234,"d":"6,234 "},null,null,0]
[null,4.2,"Low Voltage Structures - General arrangement"]
[null,null,"Supply & install, the unit rate shall include the transportation, materials  & labour required  to install a new LV structure. The unit rate shall include the affixing of the assembly onto the wood pole and the attachment of the conductor.\nAnchors measured elsewhere"]
[null,null,"Single - Phase LV ABC Structures"]
[null,"4.2.1","ABC Suspension Assembly (0° - 30°)",{"v":1153,"d":"D-DT-1153"},"No",{"$nulls":3},0]
[null,"4.2.2","ABC Terminal Assembly",{"v":1154,"d":"D-DT-1154"},"No",{"$nulls":3},0]
[null,"4.2.3","ABC Strain Assembly (0° - 60°)",{"v":1155,"d":"D-DT-1155"},"No",{"$nulls":3},0]
[null,"4.2.4","ABC Strain Assembly (60° - 90°)",{"v":1156,"d":"D-DT-1156"},"No",{"$nulls":3},0]
[null,"4.2.5","ABC T from Intermediate",{"v":1157,"d":"D-DT-1157"},"No",{"$nulls":3},0]
[null,"4.2.6","ABC T from Strain",{"v":1159,"d":"D-DT-1159"},"No",{"$nulls":3},0]
[null,"4.2.7","ABC X Intermidiate-Strain Assemby",{"v":1160,"d":"D-DT-1160"},"No",{"$nulls":3},0]
[null,null,"Dual- Phase LV ABC Structures"]
[null,"4.2.8","ABC Suspension Assembly (0° - 30°)",{"v":1145,"d":"D-DT-1145"},"No",15,null,null,0]
[null,"4.2.9","ABC Terminal Assembly",{"v":1146,"d":"D-DT-1146"},"No",22,null,null,0]
[null,"4.2.10","ABC Strain Assembly (0° - 60°)",{"v":1147,"d":"D-DT-1147"},"No",7,null,null,0]
[null,"4.2.11","ABC Strain Assembly (60° - 90°)",{"v":1148,"d":"D-DT-1148"},"No",5,null,null,0]
[null,"4.2.12","T from Intermediate",{"v":1149,"d":"D-DT-1149"},"No",3,null,null,0]
[null,"4.2.13","ABC T from Strain",{"v":1151,"d":"D-DT-1151"},"No",6,null,null,0]
[null,"4.2.14","ABC X Intermidiate-Strain Assemby",{"v":1160,"d":"D-DT-1160"},"No",2,null,null,0]
[null,null,"Three - Phase LV ABC Structures"]
[null,"4.2.15","ABC Suspension Assembly (0° - 30°)",{"v":1100,"d":"D-DT-1100"},"No",46,null,null,0]
[null,"4.2.16","ABC Terminal Assembly",{"v":1120,"d":"D-DT-1120"},"No",48,null,null,0]
[null,"4.2.17","ABC Strain Assembly (0° - 60°)",{"v":1121,"d":"D-DT-1121"},"No",42,null,null,0]
[null,"4.2.18","ABC Strain Assembly (60° - 90°)",{"v":1122,"d":"D-DT-1122"},"No",10,null,null,0]
[null,"4.2.19","ABC T from Intermediate",{"v":1140,"d":"D-DT-1140"},"No",7,null,null,0]
[null,"4.2.20","ABC T from Strain",{"v":1142,"d":"D-DT-1142"},"No",13,null,null,0]
[null,"4.2.21","ABC X Intermidiate-Strain Assemby",{"v":1143,"d":"D-DT-1143"},"No",1,null,null,0]
[null,4.3,"Wood Poles "]
[null,null,"Supply & install, the unit rate shall include the transportation, materials  & labour required to assemble and erect the following wood poles as per the structure drawing."]
[null,"4.3.1","(C) 7m Wood Pole - 120mm - 140mm Top Diameter",{"v":50,"d":"D-DT-0050"},"No",{"$nulls":3},0]
[null,"4.3.2","(D) 9m Wood Pole - 140mm - 159mm Top Diameter",{"v":55,"d":"D-DT-0055"},"No",182,null,null,0]
[null,"4.3.3","(G) 10m Wood Pole - 160mm - 179mm Top Diameter",{"v":52,"d":"D-DT-0052"},"No",{"$nulls":3},0]
[null,4.4,"New Low Voltage Anchors - General Arrangement"]
[null,null,"Supply & install, the unit rate shall include the transportation, materials & labour required to replace a structure anchor with new. The unit rate shall include the determination of the anchor position as per the line deviation angle. The rate shall include the removal of the existing stayrod / strut pole from the ground as required and the re-installation of a new stayrod / strut pole. \nPoles, excavations and compaction measured elsewhere for new installations."]
[null,"4.4.1","LV Stay Assembly ","D-DT-1165","No",131,null,null,0]
[null,"4.4.2","LV Strut Assembly ","D-DT-1167","No",26,null,null,0]
[null,4.5,"LV Voltage Fuse Switch Units (incl. Bracket and Fuses)"]
[null,null,"Supply & install, the unit rate shall include the transportation, materials and labour required to fit a 160A frame size 3, pole mounted on-load fused disconnecting switch, the fused switch shall be supplied complete with the pole mounting bracket, nuts bolts, washers etc for securing the unit to a wooden pole. Fuses shall be supplied with the fused switch unit, as per the fuse ratings indicated below. The unit rate shall also allow for the supply, connection and installation of suitable jumpers between the fuse unit and the transformer and the connection of the ABC overhead line."]
[null,"4.5.1","On load disconnecting fused unit c/w 63A fuses",null,"No",3,null,null,0]
[null,"4.5.2","On load disconnecting fused unit c/w 80A fuses",null,"No",16,null,null,0]
[]
[null,"SUB TOTAL (BILL 4) PAGE 1 B/F",{"$nulls":6},0]
[null,"SUB TOTAL (BILL 4) PAGE 1 C/F",{"$nulls":6},0]
[null,4.6,"Pole Top Box"]
[null,null,"Supply & install, the unit rate shall include the transportation, materials and labour required to fit a pole mounted distribution box as specified complete with pole mounting brackets, cable ties, PG clamps, miniature circuit breaker(s), neutral, phase and earth bars, insulated copper tails for connecting to aerial bundle conductor, insulation piercing connectors, grommets and factory installed cable openings. Included shall be the stainless steel strapping and buckles and terminations of the tails onto the aerial bundle conductor. "]
[null,"4.6.1","Pole Top Box - Split Meter ","D-DT-3055","No",127,null,null,0]
[null,"4.6.2","Padlock, St Gen Master SR Orange","D-DT-3055","No",127,null,null,0]
[null,4.7,"Excavations & Compaction"]
[null,null,"The unit rate shall include the determination of the pole and stay position, the hand/auger/compressor or blasting excavation of the hole. The contractor is to provide adequate measures to ensure a rock hole be excavated to the correct depth to facilitate the correct infrastructure. The rate shall include the transportation, materials & labour required to backfill & compact to 93% MOD AASHTO density. Where necessary, the supply and installation of suitable imported soil. Soil may be mixed with cement at a ratio of 1/8 to achieve the specified compaction. The rate for the use of mechanical devices form part of normal excavations.\nAll barricading to comply with the requirements of T&Q Procedure TQAPP043.\n(Pole Planting depths to be as per drawing D-DT-0332)                                                                     \nAll rock holes  to be verified by the Clerk of Works prior to excavation. \n"]
[null,"4.7.1","1.3m Deep Pole Hole for an 7m Wood Pole",{"v":330,"d":"D-DT-0330"},"No",0,null,null,0]
[null,"4.7.2","1.5m Deep Pole Hole for an 9m Wood Pole",{"v":330,"d":"D-DT-0330"},"No",182,null,null,0]
[null,"4.7.3","1.7m Deep Pole Hole for an 10m Wood Pole",{"v":330,"d":"D-DT-0330"},"No",0,null,null,0]
[null,"4.7.4","LV Stay Hole ",{"v":350,"d":"D-DT-0350"},"No",131,null,null,0]
[null,"4.7.5","LV Strut Hole ",{"v":351,"d":"D-DT-0351"},"No",26,null,null,0]
[null,4.8,"Anti-Climbing Device (Galvanised Barbed Wire Helically Wound)"]
[null,null,"Supply & install, the unit rate shall include transportation, labour & materials required to install anti-climbing devices (galvanised barbed wire helically wound) on:                                                                                                                                           \n1) Auxiliary Low Voltage structures as depicted on the structure drawings, and\n2) All easy climbable structures (including stay and strut assemblies)."]
[null,"4.8.1","Anti-climbing Device, Galvanised Barbed Wire Helically Wound (Stays, struts and poles)","D-DT-3170 \nD-DT- 0399","No",26,null,null,0]
[null,4.9,"Labelling & Signage "]
[null,null,"Supply & install, the unit rate shall include transportation, labour & materials required to install labels on structures as set out in the Specification (ESKASAANO) or as depicted on the drawings."]
[null,"4.9.1","Warning Fuse Label","TQCSS005","No",26,null,null,0]
[" ","4.9.2","Feeder Maximimum Fuse Label","TQCSS005","No",1,null,null,0]
[null,"4.9.3","Transformer Maximum Fuse Label","TQCSS005","No",1,null,null,0]
[null,"4.9.4","Pole Top Box (PTB) Phase Label","TQCSS006","No",127,null,null,0]
[null,"4.9.5","Danger Sign (Electrical safety) 150 x 150 x 0.6mm",{"v":3202,"d":"D-DT-3202"},"No",27,null,null,0]
{"$rows_empty":9}
[null,"TOTAL (BILL 4)",{"$nulls":6},0]

{"sheet":"Bill 5 -  Service Connections","index":5,"n_rows":36,"n_cols":9,"rows_kept":36,"merged":[[0,6,2,8],[1,1,1,3],[5,2,5,3],[6,2,6,3],[10,2,10,3],[15,2,15,3],[20,2,20,3],[24,2,24,3],[28,2,28,3],[31,2,34,3],[35,1,35,7]],"flags":["formulas_cached_only"]}
[]
[null,"BILL 5 - SERVICE CONNECTIONS"]
[]
[null,"ITEM","DESCRIPTION","DWG NO.","UNIT","QTY","SUPPLY","INSTALL","TOTAL"]
[null,"5.1","Concentric Service Cable "]
[null,null,"Measured lengths for stringing shall be net line route lengths and unit rates shall include for sag, cut-offs etc."]
[null,null,"Contractor to take delivery of, safely store, transport to site and string conductor. Installation includes all glands, lugs, shrouds, termination and connections as required. "]
[null,"5.1.1","Cable 1kV 2C 6mm SQ Concentric CU ","D-DT-3140","m",{"v":7199,"d":"7,199 "},null,null,0]
[null,"5.1.2","Cable 1kV 2C 10mm SQ Concentric CU ","D-DT-3140","m",{"$nulls":3},0]
[null,"5.2","Service Poles"]
[null,null,"Supply & install, the unit rate shall include the transportation, materials & labour required to erect the following new service poles:\nProvisional Quantity - Quantities to be verified by CoW prior to purchasing."]
[null,"5.2.1","5m Pole, 80-99mm Top Diameter","D-DT-0058","No",{"v":131,"d":"131 "},null,null,0]
[null,"5.2.2","7m Pole, 120-139mm Top Diameter","D-DT-0050","No",{"v":56,"d":"56 "},null,null,0]
[null,"5.2.3","9m Pole, 140-159mm Top Diameter","D-DT-0055","No",{"$nulls":3},0]
[null,"5.3","Excavations & Compaction"]
[null,null,"The unit rate shall include the determination of the pole position, the hand/auger/compressor or blasting excavation of the hole. The contractor is to provide adequate measures to ensure a rock hole be excavated to the correct depth to facilitate the correct infrastructure. The rate shall include the transportation, materials & labour required to backfill & compact to 93% MOD AASHTO density. Where necessary, the supply and installation of suitable imported soil. Soil may be mixed with cement at a ratio of 1/8 to achieve the specified compaction. The rate for the use of mechanical devices form part of normal excavations.\nAll barricading to comply with the requirements of T&Q Procedure TQAPP043.\n(Pole Planting depths to be as per drawing D-DT-0332)                                                                     \nAll rock holes  to be verified by the Clerk of Works prior to excavation. \n"]
[null,"5.3.1","Hole for 5m service pole - 1m Deep",null,"No",{"v":131,"d":"131 "},null,null,0]
[null,"5.3.2","Hole for 7m service pole - 1.3m Deep",null,"No",{"v":56,"d":"56 "},null,null,0]
[null,"5.3.3","Hole for 9m service pole - 1.5m Deep",null,"No",{"v":0,"d":"0 "},null,null,0]
[null,5.4,"Service Connections"]
[null,null,"The unit rate shall include the transportation, materials and labour required to connect the following plant to undertake associated low voltage overhead line works (incl. all strain clamps and suspension clamps in accordance to Engineering Instruction EI-092-LVL - The introduction of Insulated Neutral on Low Voltage Aerial Bundle Conductor). The rate is to include testing and commissioning complete with Certificate of Compliance, sealing of meters and As-Built drawing on completion. The rate is also to include the compilation of a PCS file and control sheet (incl. obtaining of the relevant customer information that is required in the PCS file)."]
[null,"5.4.1","Type A - Direct - Service Connection from Pole Top Box to Customer ECU/Prepaid Meter (including re-tensioning & connections)","D-DT-0360","No",122,null,null,0]
[null,"5.4.2","Type B - Indirect - Service Connection from Pole Top Box to  Service Pole and from Service Pole to  Customer ECU/Prepaid Meter (including re-tensioning & all connections)","D-DT-0360","No",75,null,null,0]
[null,5.5,"Installation of ECU and Passive Base Unit (Supplied as free-issue material)"]
[null,null,"Supply (except for free-issue material) & install, the unit rate shall include the transportation, materials & labour required to install both Pasive Base Units and 20A ECU's for new customers. The contractor is required to make good (repair walls) where the installation has been undertaken. Supply rate to include any material that may be required for the installation of the ECU and Pasive Base Unit. "]
[null,"5.5.1","Split Meter  Power Rail + CIU Keypad 20A","D-DT-3145","No",187,null,null,0]
[null,"5..5.2","ReadyBoard, Split Meter","D-DT-3171","No",187,null,null,0]
[null,5.6,"Customer Data Collection & Labelling"]
[null,null,"Supply & install, the unit rate shall include the transportation, materials & labour required to install the complete customer marketing label (made up of loose fonts) on either the service pole or the customer dwelling. "]
[null,"5.5.1","Customer Data Collection, PCS File and Handover Forms to Eskom ",null,"No",187,null,null,0]
[null,"5.6.1","Customer Marketing Label - complete per stand",null,"No",187,null,null,0]
[]
[]
[]
[]
[null,"SUB TOTAL (BILL 5) PAGE 1 B/F",{"$nulls":6},0]

{"sheet":"Bill 6 - Dismantling","index":6,"n_rows":30,"n_cols":8,"rows_kept":30,"merged":[[0,6,2,7],[1,1,1,5],[5,2,5,3],[6,2,6,3],[7,2,7,3],[8,2,8,3],[9,2,9,3],[10,2,10,3],[11,2,11,3],[12,2,12,3],[29,1,29,6]],"flags":["formulas_cached_only"]}
[]
[null,"BILL 6 - DISMANTLING "]
[]
[null,"ITEM","DESCRIPTION","DWG NO.","UNIT","QTY","RATE","TOTAL"]
[null,6,"Dismantling"]
[null,null,"The unit rate shall allow for the complete dismantling and recovering of existing overhead line, hardware, assemblies and the removal of all poles and anchors."]
[null,null,"The rate shall include the backfilling and compaction of excavations, and where necessary, the supply and transportation of suitable ground as may be required to achieve the desired compaction.  Any damage to existing services shall be made good by the contractor at his own expense and to the approval of the Consultant."]
[null,6.1,"MV Conductor",null,"m",null,null,0]
[null,6.2,"LV Conductor",null,"m",656,null,0]
[null,6.3,"Service Cable",null,"m",255,null,0]
[null,6.4,"MV Structures",null,"no",null,null,0]
[null,6.5,"LV Structures",null,"no",11,null,0]
[null,6.6,"Transformers 16-32 kVA",null,"no",2,null,0]
{"$rows_empty":16}
[null,"TOTAL (BILL 6)",{"$nulls":5},0]