MHLATHUZE WATER: CONTRACT MW61/2/2022/2023: CONSTRUCTION OF 25-75KL PREFABRICATED ELEVATED STEEL RESERVOIRS, BULK AND RETICULATION PIPELINES AND BOREHOLE DRILLING IN WARDS 7 AND 14 UNDER THE UMHLABUYALINGANA MUNICIPALITY 


MHLATHUZE WATER 

WATER INTERVENTIONS FOR HOTSPOT AREAS IN UMHLABUYALINGANA LOCAL MUNICIPALITY

CONTRACT MW/61/2/2022/2023: CONSTRUCTION OF 25-75KL PREFABRICATED ELEVATED STEEL RESERVOIRS, BULK AND RETICULATION PIPELINES AND BOREHOLE DRILLING IN WARDS 7 AND 14 UNDER THE UMHLABUYALINGANA MUNICIPALITY 

SCOPE OF WORK

INDEX










    Page SW

21.
PART 1: CIVIL SCOPE OF WORK
SW 

21.1
STANDARDISED SPECIFICATIONS
SW 

31.2
PROJECT SPECIFICATIONS
SW 

5PROJECT SPECIFICATION:  PORTION 1
SW 

5SABS 1200 PS:  GENERAL
SW 

5PS-1
PROJECT DESCRIPTION
SW 

5PS-2
EXTENT OF THE WORKS
SW 

6PS-3
DESCRIPTION OF THE SITE AND ACCESS
SW 

6PS-4 
NATURE OF GROUND AND SUBSOIL INVESTIGATIONS
SW 

6PS-5 
ENGINEERING AND DESIGN
SW 

8PS-6
CONSTRUCTION AND MANAGEMENT REQUIREMENTS
SW 

10PS‑7
CONSTRUCTION PROGRAMME
SW 

11PS-8
SITE FACILITIES AVAILABLE
SW 

12PS-9
SITE FACILITIES REQUIRED
SW 

14PS 10.
EXISTING SERVICES
SW 

16PS-11
REQUIREMENTS FOR ACCOMMODATION OF TRAFFIC
SW 

17PS-12
OCCUPATIONAL HEALTH AND SAFETY  (Read with SANS 1921 - 1: 2004 clause 4.14)
SW 

18PS-13
ADVERSE WEATHER CONDITIONS
SW 

19PS-14
SITE MEETINGS AND REPORTING
SW 

19PS-15
PREFERENTIAL PROCUREMENT
SW 

19PS-16
EPWP SPECIFICATION
SW 

23PS 17
SUCONTRACTING OF A PROTION OF THE CONTRACT
SW 

25project specification :  portion 2
SW 

25SABS 1200 PSA:  GENERAL
SW 

27SABS 1200 PSD  :  EARTHWORKS
SW 

29SABS 1200 PSDB  :  EARTHWORKS (PIPE TRENCHES)
SW 

30SABS 1200 PSGA  :  CONCRETE (SMALL WORKS)
SW 

31SABS 1200 PS LB:  BEDDING (PIPES)
SW 

32SABS 1200 PS LD : SEWERS
SW 

36SABS 1200 PS LE  :  STORMWATER DRAINAGE
SW 

38PARTICULAR SPECIFICATION
SW 

38PA: BRICKWORK AND PLASTER
SW 

42PB: CARPENTRY, JOINERY AND IRONMONGERY WORK
SW 

44PC:  PAINTING
SW 

47PSP: STEEL PIPES
SW 

54PD: VALVES
SW 

57PZ: ENVIRONMENTAL SPECIFICATION
SW 


PE: THE CLIENT’S PRECONSTRUCTION HEALTH AND SAFETY PLAN
SW 155
1. PART 1: CIVIL SCOPE OF WORK

1.1
STANDARDISED SPECIFICATIONS
The standard specifications on which this contract is based are Standards South Africa's Standardized Specifications for Civil Engineering Construction SABS 1200. 

Although not bound in nor issued with this Document, the following Sections of the Standardized Specifications of SABS 1200 shall form part of this Contract: 

	AA
	1986
	:
	GENERAL

	AB
	1986
	:
	ENGINEER’S OFFICE

	C
	1980
	:
	SITE CLEARANCE (As amended 1982)

	DA
	1988
	:
	EARTHWORKS (Small Works)

	DB
	1989
	:
	EARTHWORKS (Pipe trenches)

	DK
	1984
	:
	GABIONS AND PITCHING

	DM
	1981
	
	EARTHWORKS (Roads and Subgrade)

	GA
	1982
	:
	CONCRETE (Small Works)

	HA
	1990
	:
	STRUCTURAL STEELWORKS

	HC
	1988
	:
	CORROSION PROTECTION FOR STRUCTURAL STEELWORKS



	LD
	1982
	
	SEWERS

	LE
	1982
	:
	STORMWATER DRAINAGE

	M
	1996
	:
	ROADS (General) 


The following SANS specifications are also referred to in this document and the Contractor is advised to obtain them from Standards South Africa (a division of SABS) in Pretoria.

SANS 1921 (2004): 
Construction and Management Requirements for Works Contracts 

· Part 1: 

General Engineering and Construction Works; and 

· Part 2:
Accommodation of Traffic on Public Roads Occupied by the Contractor. 

1.2
PROJECT SPECIFICATIONS
The project specification is covered in the following sections:

	ITEM
	DESCRIPTION

	
	STATUS

	
	PROJECT SPECIFICATION PORTION 1: GENERAL

	PS-1
	Project Description

	PS-2
	Extent of the Works

	PS-3
	Description of the Site and Access

	PS-4
	Nature of Ground and Subsoil Conditions

	PS-5
	Construction and Management Requirements

	PS-6
	Construction Programme

	PS-7
	Site Facilities Available

	PS-8
	Site Facilities Required

	PS-9
	Existing Services

	PS-10
	Requirements for Accommodation of Traffic

	PS-11
	Occupational Health and Safety

	PS-12
	Adverse Weather Conditions

	PS-13
	Site Meetings & Reporting

	PS-14
	Preferential Procurement

	
	

	
	PROJECT SPECIFICATION PORTION 2

	PSA
	General

	PSD
	Earthworks

	PSDB
	Earthworks (Pipe Trenches)

	PSG/PSGA
	Concrete (Small Works)

	PSLB
	Bedding (Pipes)

	PSLD
	Sewers

	PSLE
	Stormwater Drainage

	
	

	
	PARTICULAR SPECIFICATIONS

	PA
	Brickwork and Plaster

	PB
	Carpentry, Joinery and Ironmongery

	PC
	Painting

	PSP
	Steel Pipes

	PD
	Valves

	PE
	The Client’s Pre-Construction and Health Plan

	PES
	Environmental Specification


STATUS
The Project Specification, consisting of two parts, forms an integral part of the contract and supplements the Standard Specifications. 

Part A contains a general description of the works, the site and the requirements to be met.

Part B contains variations, amendments and additions to the Standardized Specifications and, if applicable, the Particular Specifications. 

In the event of any discrepancy between a part or parts of the Standardized or Particular Specifications and the Project Specification, the Project Specification shall take precedence. In the event of a discrepancy between the Specifications, (including the Project Specifications) and the drawings and / or the Bill of Quantities, the discrepancy shall be resolved by the Engineer before the execution of the work under the relevant item.

PROJECT SPECIFICATION:  PORTION 1
SABS 1200 PS:  GENERAL

PS-1
PROJECT DESCRIPTION 
PS-1.1
Employer’s Objective

uMkhanyakude District Municipality comprises of four (4) Local Municipalities that fall within its area of jurisdiction. The district municipality is a Water Service Authority (WSA) and Water Services Provider (WSP), responsible for the supply of water in the four local municipality. With growing challenges of the provision of water supply and the need to develop a water master plan for sustainable supply, the department of Cooperative Governance & Traditional Affairs (CoGTA) intervened by bringing in Mhlathuze Water as an Implementing Agent for the district to assist in addressing the challenges. This is in line with the district water master plan and COGTA intervention initiatives through Mhlathuze Water.

In order to address the numerous water supply challenges being experienced under the uMhlabuyalingana Municipality areas of jurisdiction, Mhlathuze Water intends to seek Water Service Infrastructure Grant (WSIG) funding on behalf of uMkhanyakude District Municipality to address the challenges on the ground.  

Interventions will be undertaken in hot spot areas identified in certain wards. In this instance, the wards will include Ward Nos 2, 3, 5, 6, 7, 8, 14, 15, 19 and 20.

Work in these wards has been split into work packages 1 to 5, as follows: 

	Work Package 
	Municipal Wards Covered in the Scope of Work

	Work Package 1
	3 and 6

	Work Package 2
	6, 2 and 5 

	Work Package 3
	7 and 14

	Work Package 4
	14, 15, 19 and 20

	Work Package 5
	8


The work will be undertaken in a number of contracts and packaged in line with available budgets and cashflows.

PS-1.2
Overview of the Works

Work under Work Package 3 covers Ward 7 and 14. It will be implemented in three contracts as follows:

	Contract No.
	Designation
	MW Contract No.
	Description 

	1
	ME
	MW/CCC
	Supply Installation and commissioning of Electro-Mechanical Equipment at Mahlakwe, Oqondweni and Mphakathini Booster Pumpstations and Equipping and Commissioning of Borehole at Mtiwe and Resuscitation of Mashabane WTW 

	2
	CE
	MW/DDD
	Construction of 25-75kl Prefabricated Elevated Steel Reservoirs, Bulk and Reticulation Pipelines and Borehole Drilling in Wards 7 and 14 under the Umhlabuyalingana Municipality


This contract is contract MW/DDD. Other works will be tendered separately and may be contracted simultaneously in separate contracts.

PS-2
EXTENT OF THE WORKS

Under this contract, the contractor is required to undertake the civil scope of works as follows:

· Establishment And Preliminary and General Items

· Construction of 25-75kl prefabricated reservoir (SBS type of similar),

· Construction of gravity bulk and distribution pipelines in Wards 7 and 14
· Fencing
· Other associated work as may be ordered.
PS-3
DESCRIPTION OF THE SITE AND ACCESS

PS-3.1 
Access

The project area is located within uMhlabuyalingana Local Municipality under the Umkhanyakude district Municipality. 

The coordinates of Ward 6 are as follows: 

27° 26' 44.85" S and 32° 37' 51.65" "E.
PS-4 
NATURE OF GROUND AND SUBSOIL INVESTIGATIONS
Subsoil geotechnical investigations have been undertaken on the site and the geotechnical investigations report is included under Part C4: Site Information.  No responsibility is accepted for any conclusions drawn by Tenderers from the results and information supplied (if any) and Tenderers must satisfy themselves as to the nature of materials to be excavated under this contract.   
PS-5 
ENGINEERING AND DESIGN
PS-5.1 
Design Services and Activity Matrix
The following matrix of responsibilities for design of permanent and temporary works will apply:

	Activity

Work designed by, per design stage
	Responsible Party

	Concept, feasibility and overall process
	Employer

	Basic engineering and detail layouts to tender stage
	Employer

	Final design approved for construction stage
	Employer

	Temporary works
	Contractor

	Permanent Works, including structural design and certification of prefabricated tank
	Contractor

	Preparation of as built drawings
	Contractor & Employer’s Agent


PS-5.2 
Employer’s Design
The Employer’s design will be for all permanent works and will be detailed in drawings, site instructions the technical specifications to be issued with the tender documents and issued during construction.

PS-5.3 
Design Brief
The contractor will be responsible for design of the following (which are all subject to approval by the Engineer):

· Site layouts for the contractor’s  camp and office accommodation

· Site layouts for the Engineer Representative’s temporary office accommodation

· Construction Methodology

· Formwork

· Scaffolding and all staging work

· All other temporary works

· Concrete Mix designs

The costs of the designs will be deemed to have been included in the scheduled items in the Schedule of Quantities. No other additional payments will be certified to cover these activities.

PS-5.4
Drawings

The following drawings will be required to be prepared by the contractor as a minimum:

· Site layouts for the contractor’s camp and office accommodation

· Site layouts for the Engineer Representative’s temporary office accommodation

· Scaffolding and all staging work

The costs of the designs will be deemed to have been included in the scheduled items in the Schedule of Quantities. No other additional payments will be certified to cover these activities.

The tender drawings are applicable to the contractor are detailed in Part C5 of these documents. These drawings have been used for setting up the Bills of Quantities.

PS-5.5
Design Procedures
The contractor will be required to furnish the following designs for approval by the Engineer at the indicated times:

· Site layouts of the Contractor’s camp and office accommodation – within 14 days from commencement date of the contract and in any case prior to the erection of the contractor’s camp and offices

· Layouts for the Engineer’s representative office – within 10 days from commencement date of the contract and in any case prior to the erection of the Engineer’s Representative’s temporary office premises.
· Formwork design – within 10 days of commencement of work and in any case prior to the construction of permanent reinforced concrete works.
· Scaffolding and all staging work – within 10 days of commencement of work and in any case prior to the construction of permanent reinforced concrete works.
· Concrete Mix Designs for the all classes of concrete as measured in the Schedule of Quantities prior to the placement of any concrete work

The costs of the designs will be deemed to have been included in the scheduled items in the Schedule of Quantities. No other additional payments will be certified to cover these activities.

PS-5.6
Interface with other Contractors
The contractor may be required to provide access to other contractors undertaking work as per the parallel contracts. The costs of this interface will be deemed to have been allowed for in the appropriate items in the Schedule of Quantities. No other additional payments will be certified to cover these activities.  

PS-6
CONSTRUCTION AND MANAGEMENT REQUIREMENTS

PS-6.1
General
The Contractor is referred to SANS 1921: 2004: Construction and Management Requirements for Works Contracts, Part 1: General Engineering and Construction Works, and Part 2: Accommodation of Traffic on Public Roads. These specifications shall be applicable to the contract under consideration and the Contractor shall comply with all requirements relevant to the project. 

Certain aspects however require further attention as described hereafter. 

PS-6.2
Quality Assurance (QA)     (Read with SANS 1921 – 1: 2004 clause 4.4)

The Contractor will be solely responsible for the production of work that complies with the Specifications to the satisfaction of the Engineer.  To this end it will be the full responsibility of the Contractor to institute an appropriate Quality Assurance (QA) system on site.  The Engineer will audit the Contractor's quality assurance (QA) system on a regular basis to verify that adequate independent checks and tests are being carried out and to ensure that the Contractor's own control is sufficient to identify any possible quality problems which could cause a delay or failure.

The Contractor shall ensure that efficient supervisory staff, the required transport, instruments, equipment and tools are available to control the quality of his own workmanship in accordance with his QA-system. His attention is drawn to the fact that it is not the duty of the Engineer or the Engineer’s representative to act as foreman or surveyor.

PS-6.3
Management and disposal of water 
(Read with SANS 1921-1: 2004 clause 4.6)

The Contractor shall pay special attention to the management and disposal of water and stormwater on the site. It is essential that all completed works or parts thereof are kept dry and properly drained. Claims for delay and for repair of damage caused to the works as a result of the Contractor’s failure to properly manage rain and surface water, will not be considered. 

PS-6.4
Disposal of spoil or surplus material
(Read with SANS 192-1: 2004 clause 4.10)

The Contractor shall dispose all surplus and unsuitable material in legal spoil areas of his own choice. He shall be responsible for all arrangements necessary to obtain such spoil sites. 

PS-6.5
Testing 
(Read with SANS 1921 – 1 : 2004 clause 4.11)

PS-6.5.1
Process control

The Contractor shall arrange for all tests required for process control to be done by a laboratory acceptable to and approved by the Engineer.

The Contractor may establish his own laboratory on site or he may employ the services of an independent commercial laboratory. Whatever method is used, the Contractor must submit the results of tests carried out on materials and workmanship when submitting work for acceptance by the Engineer. The costs for these tests shall be deemed to be included in the relevant rates and no additional payment will be made for testing as required.

PS-6.5.2
Acceptance control
The process control test results submitted by the Contractor for approval of materials and workmanship may be used by the Engineer for acceptance control. However, before accepting any work, the Engineer may have further control tests carried out by a laboratory of his choice. The cost of such additional tests will be covered by a provisional sum provided in the schedule of quantities, but tests that failed to confirm compliance with the specifications, will be for the account of the Contractor.

PS-6.6
Survey beacons
(Read with SANS 1921 - 1 : 2004 clause 4.15)

The Contractor shall take special precautions to protect all permanent survey beacons or pegs such as bench-marks, stand boundary pegs and trigonometrical beacons, regardless whether such beacons or pegs were placed before or during the execution of the Contract. If any such beacons or pegs have been disturbed by the Contractor or his employees, the Contractor shall have them replaced by a registered land surveyor at his own cost.

PS-6.7
Existing Services
(Read with SANS 1921 - 1 : 2004 clause 4.17)

The Contractor shall make himself acquainted with the position of all existing services before any excavation or other work likely to affect the existing services is commenced. 

The Contractor will be held responsible for any damage to known existing services caused by or arising out of his operations and any damage shall be made good at his own expense. Damage to unknown services shall be repaired as soon as possible and liability shall be determined on site when such damage should occur.

PS-6.8
Management of the environment 
(Read with SANS 1921 - 1 : 2004 clause 4.19)

The Contractor shall pay special attention to the following:

(a)
Natural Vegetation

The Contractor shall confine his operation to as small an area of the site as may be practical for the purpose of constructing the works. 

Only those trees and shrubs directly affected by the works and such others as the Engineer may direct in writing shall be cut down and stumped. The natural vegetation, grassing and other plants shall not be disturbed other than in areas where it is essential for the execution of the work or where directed by the Engineer. 

(b)
Fires

The Contractor shall comply with the statutory and local fire regulations. He shall also take all necessary precautions to prevent any fires. In the event of fire the Contractor shall take active steps to limit and extinguish the fire and shall accept full responsibility for damages and claims resulting from such fires which may have been caused by him or his employees. 

PS-6.9
Overhaul
No payment will be made for overhaul on this contract unless provision is made thereof in specific items. 

PS-6.10
Excavations 

Due to the depths of reservoir excavations, the Contractor is to allow in their tendered rates for excavation, for shoring and protection of excavations.  No additional payment will be made for protection of excavations for whatever reason.
PS-6.10
Security
The Contractor shall provide security watchmen for the contract as he deems fit at no extra cost for the Employer.  The Contractor must ensure that all his employees as well as the employees of his subcontractors are able to identify themselves as members of the construction team.

PS‑7
CONSTRUCTION PROGRAMME

PS-7.1
Preliminary programme

The Contractor shall include with his tender a preliminary programme on the prescribed form to be completed by all Tenderers. The programme shall be in the form of a simplified bar chart with sufficient details to show clearly how the works will be performed within the time for completion as stated in the Contract Data.

The Contractor shall be deemed to have allowed fully in his tendered rates and prices as well as in his programme for all possible delays due to normal adverse weather conditions and special non-working days as specified in the Special Conditions of Contract, in the Project Specifications and in the Contract Data.

In determining his construction programme, the contractor should allow for disruptions/stoppages/requirements and intermittent “hold” of work while awaiting Engineer’s inspections at the following critical stages:

	Stage
	Delay

	1.
	Setting of civil structures, buildings and pipeline routes and before excavation 
	1 day

	2.
	Excavation works for pipelines and prior to preparation of bedding


	1 day

	3.
	Following preparation of bedding and laying of pipes and prior to backfilling.  


	1 day

	4.
	Prior to commencement of pressure testing of pipelines
	1 day

	
	Completion of bulk excavations and prior to placing blinding and/or surface preparations 
	1 day

	
	Completion of placement of shuttering and prior to casting of concrete 
	1 day


No additional payments, other than through scheduled items, will be made for these stoppages/disruptions/constraints.

In addition, the contractor is required to establish the Engineer’s facilities within 14 days of commencement. Should the contractor fail to provide approved establishment within the stipulated 14 days, the contractor will pay a penalty calculated as follows:

· Mileage of the Engineer’s Representative from other offices from the nearest business centre to site and back to office at R8.00/km.

· Rented Office space equivalent to that stipulated in this contract at offices in Mkuze or other place closer to the site.

The Employer intends to award this contract for commencement of construction works by end of March 2023.

PS-7.2
Programme in terms of Clause 5.6 of the General Conditions of Contract


It is essential that the construction programme, which shall conform in all respects to Clause 5.6 of the General Conditions of Contract, be furnished within the time stated in the Contract Data. The preliminary programme to be submitted with the tender shall be used as basis for this programme. The Contractor's attention is also drawn to clause 5.7.1 of the General Conditions of Contract 2015.
The Employer intends to award this contract for commencement of construction works by end of March 2023.
PS-8
SITE FACILITIES AVAILABLE

PS-8.1
Contractor's camp site and depot
(Read with SANS 1921 - 1 : 2004 clause 4.14)

The Contractor will be permitted to locate his offices, storage facilities, workshops, latrines, etc, on a site approved by the Engineer, in liaison with the community.
Temporary buildings and fencing are to be neat and presentable and the surrounding areas must at all times be kept in a neat, clean and orderly condition.  The Contractor must not cut down or damage any trees nor make any excavation without the written permission of the Engineer and will be required to restore the site to its original condition on completion of the Works.

All buildings and latrines shall be in accordance with the Local Authority and State Heath regulations and shall be kept in a clean, sanitary condition to the satisfaction of the Engineer.

PS-8.2
Accommodation of Employees
No employees except for security guards will be allowed to sleep or be accommodated on the site in urban areas. 

No housing is available for the Contractor's employees and the Contractor shall make his own arrangements to house his employees and to transport them to site. 

No informal housing or squatting will be allowed.

The Contractor shall provide the necessary ablution facilities at his camp site and the site of the works for the use of his employees. Chemical toilets only will be allowed where temporary facilities have to be provided.

PS 8.3
Source of Water Supply
The Contractor shall make his own arrangements for the supply of water for construction purposes. The source of water shall be subject to the approval of the Engineer.

The Water Services Authority (WSA) and Water Services Provider (WSP) in the area is Umkhanyakude District Municipality.  Should the contractor’s source of water be Umkhanyakude District Municipality, the contractor will be required to ensure that the water account with the WSP is in good standing prior to the issue of completion certificate. The Engineer will withhold any payments until arrears are cleared with the WSP. 
PS 8.4
Source of Power Supply

The power supply authority is Eskom.  The Contractor will be required to make his own arrangements with, and pay all the requisite connection and consumption charges to Eskom for whatever temporary power supplies he may require for his use on the site and his tender will be held to include for all such costs and charges.  

PS-9
SITE FACILITIES REQUIRED

PS-9.1
Facilities Required for the Engineer

PS 9.1.1
Temporary/Permanent Offices

The Contractor shall be asked to provide a temporary office for use by the Engineer. The offices should be able to accommodate one full time Engineer’s Representative and two assistants. The temporary offices should be of modular type (Parkhomes Specification/M Projects or similar). The walls and doors should be made of 40mm polystyrene insulation with Chromadek cladding internally and externally. The ceiling shall be made of 40mm white Chromadek insulated panels. The 2 No. windows are to be made of aluminium with aluminium burglar guards and vertical blinds.

The Engineer’s offices are to be equipped with the following as a minimum:

· Three desks each with lockable drawers

· Three high back swivel chairs

· Three visitors chairs

· A facility to store/hang drawings

· An electric refrigerator of at least 200 litres capacity

The Contractor should also make arrangements for covered facilities to enable the accommodation of approximately 12– 16 people during progress site meetings, to be held fortnightly or monthly.
The facilities are to be provided, to the satisfaction of the Engineer, within 14 days of commencement date. The Engineer may withhold certification of the first progress payment (and subsequent payments, as appropriate) until these facilities are provided. 

PS 9.1.2
Computer/IT Facilities

The Contractor shall provide the Engineer’s Representative with the following computer equipment to be used solely to generate site administration documents such as Minutes of Site Meetings, Inspection Forms, etc:

· A functional laptop complete with mouse and bag, with at least 500GB Hard Drive, Intel Processor and 2GB RAM, all supplied new. The laptop software to include MS Windows and full MS Office software( Excel, MSWord, MS Power Point,)

· A 3 in 1 (printer/scanner/fax) printer capable of printing black and white copies at the rate of 7 pages per minute to a resolution of 600 x 600 rendered dpi.

The hardware and software will revert to the Contractor on completion of the contract. Perishables such as toners (for the printer) paper for printing, will be paid for separately under a Provisional Sum provided for in the Schedule of Quantities.

The facilities are to be provided, to the satisfaction of the Engineer, within 14 days of commencement date. The Engineer may withhold certification of the first progress payment until these facilities are provided.

PS 9.1.3
Laboratory Facilities

The Contractor will not be required to provide a testing laboratory on site for use by the Engineer.  However, the contractor will be required to provide the following:

· Concrete cube strength test results from a recognised laboratory for all concrete poured on site.  
· Compaction test results for all roadworks layerworks and embankment backfill as detailed 

· Compaction test results for bedding and backfill material along pipelines trenches 

The contractor should therefore include in their tendered rates the costs for the requisite concrete cube tests.
PS 9.1.4
Sanitary Facilities

All latrines shall conform to the requirements of the Local Authority and shall be subject to approval by the Engineer.  All sanitary fees and charges due under the Local Authority or State Health Regulations or bylaws shall be paid by the Contractor.  Throughout the progress of the contract, all latrines shall be maintained by the Contractor in a clean, sanitary condition to the satisfaction of the Engineer.  

PS 9.1.5
Telephone Facilities

The Contractor will not be required to provide a telephone for use by the Engineer. The contractor will however be required cove cellphone costs for the engineer’s site staff for airtime valued at R150/week. Appropriate items have been provided in the Schedule of Quantities to cover these costs.

PS 9.1.6
Housing Facilities

The Contractor will not be required to provide housing facilities for the Engineer's staff.  However, a provisional sum has been provided in the schedule of quantities for payment through the contract for accommodation for the Engineer’s staff. 
PS 9.1.7
Parking Facilities

The Contractor will be required to provide two uncovered parking bays for the Engineer.

PS 9.1.8
Engineer's Transport
The Contractor will not be required to provide transport for the Engineer’s staff.

PS 9.1.9
Security
The Contractor will be responsible for providing adequate security for the Works and for the site establishment.  All costs associated with the provision of security staff shall be borne by the Contractor and should allowed for in the rates tendered for items in the Schedule of Quantities. No additional payments will be made for security measures taken during the contract period, other through the schedule items in the Schedule of Quantities. 

PS 9.1.10
Survey Equipment
The contractor shall provide the following survey equipment, in good condition, for use by the Engineer throughout the duration of the contract:

· A dumpy level

· Measuring tape 

· An assistant, when required, to assist the Engineer to operate survey equipment, when provided

PS 9.1.11
Contract staff to assist the Engineer
The following staff will be recruited by the contractor to assist the Engineer in carrying out his services:

	Description of Staff
	No. Required
	Remarks

	Environmental Monitoring 
	One
	Provisional sum provided for appointment as directed by the Engineer. Personnel directed by and report to Engineer

	Technical Assistant
	One
	

	Geotechnical Consultant
	One
	

	Community Liaison Officer
	One
	

	Health and Safety Inspector
	One
	

	Independent inspectors 
	TBA
	


The required personnel will be identified by the Engineer and report to the Engineer. Provisional Sums and the relevant mark-up Items are provided for in the Schedule of Quantities to cover these costs

PS 10.
EXISTING SERVICES
PS 10.1
Care, Damage and Protection
Known services will be indicated in the tender and contract documents. The Contractor will be responsible for identifying all services with the relevant Service Providers. 

The Contractor shall familiarize himself with all services and expose them at the start of the Contract to verify their position and establish their depths.

No additional payment will be made to the Contractor for identifying and locating services. Therefore the Contractor will have to include the costs thereof in the scheduled items in the Schedule of Quantities.

Any information regarding existing services is given in good faith and without guarantee.
PS 10.2
Blasting

No blasting will be permitted unless the Contractor can satisfy the Engineer that his proposed blasting methods and controls are such that no damage will be caused to the adjoining building structures, pipelines or services.  In any event the Engineer will require the Contractor to plan and execute each blast in such a manner as to ensure that no damage will be caused to any structure, pipeline or service.  In addition, the Engineer will require vibro-recordings to be taken at no additional cost to the Employer.  No blasting is to be carried out in Eskom servitudes or wayleaves unless the Eskom authorities have been advised in writing three weeks prior to blasting.  Where blasting is done adjacent to Eskom power lines, the Contractor shall arrange for a representative of Eskom to be present prior to and during any blast.

PS 10.3
Environmental Aspects
The Contractor will be required to plan and undertake his work in a manner that minimises its impact on the natural environment.  Trees and other vegetation shall, wherever possible, be left undisturbed.  Trees that are marked by the Engineer shall not be damaged and in the event of the Contractor doing so, a penalty will be deducted from monies due to the Contractor.

Every effort shall be made by the Contractor to prevent pollution of the adjacent areas and river and to reduce the noise, dust and fumes emanating from his construction activities.

PS 10.4
Dealing with Water

Where necessary, the Contractor shall construct temporary drainage channels to divert ground water from his excavation and excess water must be pumped out.

No compensation for any variation of the actual conditions during construction from the data given will be considered.   Neither will additional compensation be considered for data omitted or inaccurately given.

The rates tendered shall allow for the requirements of this clause and all incidentals.

PS 10.5
Servitudes and Rights of Way
The Employer will, where necessary, obtain permanent servitudes and rights of way along the road routes indicated on the tender drawings.  New servitudes will only be registered after completion of the Works.  

PS 10.6
Dealing with Damaged Services
In the event of any service being damaged or accidentally disconnected for any reason, the Contractor shall immediately contact the relevant authority for instruction and shall report the occurrence of the incident.  The damage is to be repaired as soon as possible to the approval of the Engineer and the authority.  The Contractor will be held responsible for paying all costs incurred by the authority or himself as a result of each such incident, where relevant.

PS 10.7
Accommodation of Traffic
The Contractor shall ensure the safe and expeditious passage of traffic at all times and shall provide all necessary temporary road traffic signs, barricades, flagmen, etc to safeguard the travelling public.  Any detours or bypasses constructed by the Contractor shall be adequately signposted, as per the South African Road Traffic Signs Manual, and maintained in such a manner as to provide safe and easy passage of traffic.

PS 10.8
Spoil Material

No indiscriminate spoiling of material will be allowed.  All surplus or unsuitable material shall be spoiled, levelled and spread in designated areas as directed by the Engineer.  All haul will be regarded as freehaul. 

PS 10.9
Finishing and Tidying and Defects Liability Period

On no account must rubble and spoil materials, other materials, equipment or unfinished operations be allowed to accumulate in such a manner as to unnecessarily impede the activities of other Contractors or Authorities.

Finishing and tidying must not simply be left until the end of the construction period.  The Contractor will be entitled, subject to prior agreement with the Engineer and within reasonable limits, to request that work in a particular area and/or work of a particular discipline, be inspected for partial completion.  The specified defects liability period in respect of any specific section of the Works shall commence on the date on which the relevant section is accepted by the Engineer as being completed, i.e. fully commissioned, including finishing and tidying.

On completion of the Contract the Contractor shall ensure that all materials used in the construction of the temporary Site office, workshop and storage yard are removed from Site.  Waste materials such as construction debris and soil contaminated with oil and fuel are to be disposed of at the solid waste disposal site used approved by the Engineer. Prior to the handover of the Site to the Employer, the Contractor and the Engineer will conduct a post construction audit to determine if any additional measures that are to be taken.  The Completion Certificate will only be issued after this stage.

PS 10.10
Employee Accommodation
(See Subclause 3.2.1 of Section A of Part 2 and Subclause 1.2.1 of Section A of Part 3 of SABS 0120)
The Contractor shall conform in all respects with the provisions of any Act, Regulations or By-Law of Department of Human Settlement, which may be applicable to employee accommodation.  Save for a security guard on active duty, no employees may be housed on Site or the Contractor’s campsite after normal working hours.

PS 10.11
Employment of Local Labour

The Employer has determined that 100% of the Contractor’s unskilled labour force shall be made up from the local community.  A labour sub-committee (of a Project Steering Committee) comprising representatives of the community and other stakeholders will be responsible for the recruitment of all local labour.  The Contractor will be required to provide details of the numbers of semi-skilled and unskilled workers he will require, together with their anticipated starting dates.  The PSC through its labour sub-committee will then make this labour available to the Contractor.  

A minimum of 50% of the local labour shall comprise of women and, where appropriate, disabled labour shall be employed.  It is a requirement that tenderers acquaint themselves fully with requirements for registration with Unemployment Insurance Fund.

The Employer requires that the successful contractor registers all labour with the Unemployment Insurance Fund.  The local labour rate has been determined at R29.37 per hour per labourer per day or as may be advised by Department of Human Settlement from time to time.  This is a net rate excluding UIF contributions.  The task for excavation by hand has been agreed at 2,4 m³/day (e.g. 0,76 m x 1,0 m x 3,15 m).  

During project execution, the successful contractor will be required to provide progress reports indicating to what level these requirements have been met. 

PS 10.12
Frequency of Labour Wages Payments 

The contractor will be required to pay labour on a fortnightly basis

PS 10.13
Training and Capacity Building

During project execution, it is the desire of the Employer that an identified number of community members receive appropriate level of non accredited training in either pipelaying activities or construction management activities. Within 14 days of appointment, the successful contractor will be required to provide, together with his method statement, a proposal for consideration by the Project Steering Committee for activities in which the community members can receive training. This proposal will be considered by the Project Steering Committee after which the Contractor will be given an instruction on the training to provide. Training will be provided to local labour that is already in the employ of the contractors as per clause PS 10.11.  It must be noted that the Contractor will be required to pay the labour based on their daily rates indicated in PS 10.11. 

The operators of the infrastructure to be provided will require training at commissioning stage.  Training shall be be provided under the contract and will include provision of training and operation and maintenance manuals. 
Should the contractor fail to provide this training, the Employer reserves the right to seek training from alternative sources. In that case, the cost of the training sought will be deductible from any monies due to the contractor.

A provisional sum has been provided in the schedule of quantities for training by a nominated subcontractor as necessary. 
PS-11
REQUIREMENTS FOR ACCOMMODATION OF TRAFFIC

PS-11.1
General
The Contractor will be responsible for the safe and easy passage of public traffic past and on sections of roads of which he has occupation or where work has to be done near traffic. 

Accommodation of traffic, where applicable shall comply with SANS 1921-2: 2004: Construction and Management Requirements for Works Contracts, Part 2: Accommodation of Traffic on Public Roads occupied by the Contractor. The Contractor shall obtain this specification from Standards South Africa if accommodation of traffic will be involved on any part of the construction works. 
PS-11.2
Basic Requirements

The travelling public shall have the right of way on public roads, and the Contractor shall make use of approved methods to control the movement of his equipment and vehicles so as not to constitute a hazard on the road.

The Contractor shall ensure that all road signs, barricades, delineators, flagmen and speed controls are effective and that courtesy is extended to the public at all times. 

Failure to maintain road signs, warning signs or flicker lights, etc, in a good condition shall constitute ample reason for the Engineer to suspend the work until the road signs, etc, have been repaired to his satisfaction.

The Contractor may not commence constructional activities affecting existing roads before adequate provision has been made to accommodate traffic in accordance with the requirements of this document and the South African Road Traffic Signs Manual. 

The Contractor shall construct and maintain all temporary drainage works necessary for temporary deviations. 

The Contractor shall provide and grant access to persons whose properties fall within or adjoin the area in which he is working. 

PS-11.3
Traffic Safety Officer

Where warranted by traffic conditions on or near the site, the Contractor shall nominate a suitable member of his staff as traffic safety officer to be responsible for the arrangement and maintenance of all the measures for the accommodation of traffic for the duration of the project. Duties of the traffic safety officer shall be as set out in SANS 1921 Part 2 and shall also be in compliance with the Occupational Health and Safety Act No 85 of 1993 and the Construction Regulations 2003.

PS-11.4
Payment

The Contractor’s tendered rates for the relevant items in the Bill of Quantities shall include full compensation for all possible additional costs which may arise from this, and no claims for extra payment due to inconvenience as a result of the modus operandi will be considered. 

Items that may be considered for payment are specified in SABS 1200 Standardized Specifications and the related project specification. 

PS-12
OCCUPATIONAL HEALTH AND SAFETY  (Read with SANS 1921 - 1: 2004 clause 4.14)
PS-12.1
General statement

It is a requirement of this contract that the Contractor shall provide a safe and healthy working environment and to direct all his activities in such a manner that his employees and any other persons, who may be directly affected by his activities, are not exposed to hazards to their health and safety. To this end the Contractor shall assume full responsibility to conform to all the provisions of the Occupational Health and Safety Act No 85 and Amendment Act No 181 of 1993, and the OHSA 1993 Construction Regulations 2003 issued on 18 July 2003 by the Department of Labour. 

For the purpose of this contract the Contractor is required to confirm his status as mandatary and employer in his own right for the execution of the contract by entering into an agreement with the Employer in terms of the Occupational Health and Safety Act by executing the Agreement form C1.2.4 included in Section C1: Agreements and Contract Data. 

PS-12.2
Health and Safety Specifications and Plans to be submitted at tender stage

(a)
Employer's Health and Safety Specification 

The Employer's Health and Safety Specification will be included in the tender documents as part of the Project Specifications. 

(b)
Tenderer's Health and Safety Plan 

The successful Tenderer shall, on receipt of notification that he has been awarded the contract, submit without delay his own documented Health and Safety Plan for the execution of the work under the contract. His Health and Safety Plan must at least cover the following:

(i)
a proper risk assessment of the works, risk items, work methods and procedures in terms of Regulations 7 to 28;

(ii)
pro-active identification of potential hazards and unsafe working conditions;

(iii)
provision of a safe working environment and equipment;

(iv)
statements of methods to ensure the health and safety of subcontractors, employees and visitors to the site, including safety training in hazards and risk areas (Regulation 5);

(v) monitoring health and safety on the site of works on a regular basis, and keeping of records and registers as provided for in the Construction Regulations;

(vi) details of the Construction Supervisor, the Construction Safety Officers and other competent persons he intends to appoint for the construction works in terms of Regulation 6 and other applicable regulations; and

(vii) details of methods to ensure that his Health and Safety Plan is carried out effectively in accordance with the Construction Regulations 2003. 

The Contractor's Health and Safety Plan will be subject to approval by the Employer, or amendment if necessary, before commencement of construction work. The Contractor will not be allowed to commence work, or his work will be suspended if he had already commenced work, before he has obtained the Employer's written approval of his Health and Safety Plan. 

Time lost due to delayed commencement or suspension of the work as a result of the Contractor's failure to obtain approval for his safety plan, shall not be used as a reason to claim for extension of time or standing time and related costs 

PS-12.3
Cost of compliance with the OHSA Construction Regulations

The rates and prices tendered by the Contractor shall be deemed to include all costs for conforming to the requirements of the Act, the Construction Regulations and the Employer's Health and Safety Specification as applicable to this contract.  Should the Contractor fail to comply with the provisions of the Construction Regulations, he will be liable for penalties as provided in the Construction Regulations and in the Employer's Health and Safety Specification.

Items that may qualify for remuneration will be specified in the Safety Specifications included or in the Project specifications. 

PS-13
ADVERSE WEATHER CONDITIONS

In terms of Clause 42.3 of the General Conditions of Contract, extension of time will be considered for abnormal rainfall. The numbers of days per month on which work is expected not to be possible as a result of normal rainfall, and for which the Contractor shall make provision in his tendered rates, prices and programme, are listed in Table     PS-12.1 hereafter. Only the number of days lost as a result of adverse weather conditions, exceeding the number of days listed in Table PS‑12.1, will qualify for consideration of extension of time.

During the execution of the Works, the Engineer's Representative will certify a day lost due to abnormal rainfall and adverse weather conditions only:

· if no work was possible on the relevant working day on any item which is on the critical path according to the latest approved construction programme; or

· if less than 30% of the work force and plant on site could work during that specific working day.

Extension of time as a result of abnormal rainfall and adverse weather conditions shall be calculated monthly being equal to the number of working days certified by the Engineer's Representative as lost due to rainfall and adverse weather conditions, less the number of days allowed for as in Table PS-13, which could result in a negative figure for certain months. The total extension of time as a result of abnormal climatic conditions for which the Contractor may apply, shall be the cumulative algebraic sum of the monthly extensions. Should the sum thus obtained be negative, the extension of time shall be taken as nil."

Table PS-13:   Expected N⁰ of Working Days Lost Monthly Due to Normal Rainfall
	MONTH
	Expected number of working days lost as result of normal rainfall

	JANUARY

FEBRUARY

MARCH

APRIL

MAY 

JUNE

JULY

AUGUST

SEPTEMBER

OCTOBER

NOVEMBER

DECEMBER
	*5

5

4

1

1

1

1

1

2

3

4
5

	
TOTAL 
	
33 days


(Based on information obtained from the Weather Bureau, Department of Environment Affairs.  The average monthly rainfall figures quoted, are included for information and palnning in terms of programming of the works. These shall be taken into consideration for calculation of extension of time. The number of working days lost for December and January allows for the builders' holidays)

PS-14
SITE MEETINGS AND REPORTING

The Contractor will be required to attend site meetings organised by the Engineer. In these meetings he (the Contractor) will be required to provide progress reports and other reports to monitor the outputs of the contractor, as may be required from time to time, to be presented in a format prescribed by the Engineer. The frequency of such meetings will be monthly, as a minimum. However the frequency can be reviewed, depending on the progress of the contract.

PS-15
PREFERENTIAL PROCUREMENT

For the purpose of this contract the Contractor shall comply with the preferential procurement statement provided in F.3.11 and T2.2 of the Tender Data. 

PS-16
EPWP SPECIFICATION

PS-16.1
Labour Intensive Competencies of Supervisory and Management Staff

Contractors shall only engage supervisory and management staff in labour intensive works that have completed the skills programme outlined in Table 1: 

Table 1: Skills programme for supervisory and management staff
	Personnel
	NQF level
	Unit standard titles
	Skills programme description

	Foreman / Supervisor
	4
	Implement Labour-Intensive Construction Systems and Techniques.
	This unit standard must be completed, and

	
	
	Use Labour-Intensive Construction Methods to Construct and Maintain Roads and Stormwater Drainage
	any one of these 3 unit standards

	
	
	Use Labour-Intensive Construction Methods to Construct and Maintain

Water and Sanitation Services
	

	
	
	Use Labour-Intensive Construction Methods to Construct, Repair and Maintain Structures
	

	Site Agent / Manager (i.e. the contractor’s most senior representative that is resident on the site)
	5
	Manage Labour-Intensive Construction Processes
	Skills Programme against this single unit standard


PS-16.2
Employment of Unskilled and Semi-Skilled Workers in Labour-Intensive Works

PS-16.2.1
Requirements for the sourcing and engagement of labour.

PS-16.2.1.1
Unskilled and semi-skilled labour required for the execution of all labour intensive works shall be engaged strictly in accordance with prevailing legislation in accordance with the Code of Good Practice for the Expanded Public Works Programme.

PS-16.2.1.2
The following are some of the considerations that are elaborated in the Code of Good Practice for Expanded Public Works Programmes.
PS-16.2.2
Training of Targeted Labour
PS-16.2.2.1
The contractor shall provide all the necessary on-the-job training to targeted labour to enable such labour to master the basic work techniques required to undertake the work in accordance with the requirements of the contract in a manner that does not compromise worker health and safety.

PS-16.2.2..2
Accredited training may be provided before the commencement of a project. 

PS-16.2.2.3
The cost of accredited training of targeted labour will be funded through various funding sources such as National Skills Fund from the Department of Higher Education and Training, funds from the Implementing Public body, funding from SETAS etc. This training should take place as close to the project site as practically possible. The Public Body implementing the project must ensure that training applications for beneficiaries are made by its relevant project manager assisted by relevant training officials from the National Department of Public Works. 

PS-16.2.2.4
The Public Body must ensure that preference of the training of beneficiaries in technical skills over life skills is made. In addition, the Public Body is required to maximize opportunities for training to beneficiaries to be carried out before the implementation of projects. 

PS-16.2.2.5
The Public body must ensure that workers who have received training will be placed on the project to work after receiving the training. 

PS-16.2.2.6
If a provisional sum for training is made in the contract the contractor shall pay an allowance equal to 100% of the daily wage rate to workers who attend accredited training.

PS-16.3
Generic Labour-Intensive Specification 

The Generic Labour-intensive specification below (informed by SANS 1921-5, Construction and management requirements for works contracts - Part 5: Earthworks) covers activities which are to be performed by hand, and should be included in the scope of works without amendment or modification as set out below.

This specification establishes general requirements for activities which are to be executed by hand involving the following:

· trenches having a depth of less than 1.5 metres

· stormwater drainage

· low-volume roads (typically less than 500 vehicles per day); 

· sidewalks and non-motorised transport infrastructure 

· water and sanitation 

PS-16.3.1
Precedence

Where this specification is in conflict with any other standard or specification referred to in the Scope of Works to this Contract, the requirements of this specification shall prevail.

PS-16.3.2
Hand excavateable material

Hand excavateable material is:

a)  granular materials:

i) whose consistency when profiled may in terms of table 2 be classified as very loose, loose,    medium dense, or dense; or 

ii) where the material is a gravel  having a maximum particle size of 10mm and contains no cobbles or isolated boulders, no more than 15 blows of a dynamic cone penetrometer is required to penetrate 100mm;

b)  cohesive materials:

i) whose consistency when profiled may in terms of table 2 be classified as very soft, soft, firm, stiff and stiff / very stiff; or 

ii) where the material is a gravel  having a maximum particle size of 10mm and contains no cobbles or isolated boulders, no more than 8 blows of a dynamic cone penetrometer is required to penetrate 100mm;

Note

1. A boulder is material with a particle size greater than 200mm, a cobble and gravel is material between 60 and 200mm.

2. A dynamic cone penetrometer is an instrument used to measure the insitu shear resistance of a soil comprising a drop weight of approximately 10 kg which falls through a height of 400mm and drives a cone having a maximum diameter of 20mm (cone angle of 60° with respect to the horizontal) into the material being used.

	Table 2: Consistency of materials when profiled 

	GRANULAR MATERIALS 
	COHESIVE MATERIALS 

	CONSISTENCY 
	DESCRIPTION 
	CONSISTENCY 
	DESCRIPTION 

	Very loose 
	Crumbles very easily when scraped with a geological pick. 
	Very soft 
	Geological pick head can easily be pushed in as far as the shaft of the handle. 

	Loose 
	Small resistance to penetration by sharp end of a geological pick. 
	Soft 
	Easily dented by thumb; sharp end of a geological pick can be pushed in 30-40 mm; can be moulded by fingers with some pressure. 

	Medium dense 
	Considerable resistance to penetration by sharp end of a geological pick. 
	Firm 
	Indented by thumb with effort; sharp end of geological pick can be pushed in upto 10 mm; very difficult to mould with fingers; can just be penetrated with an ordinary hand spade. 

	Dense 
	Very high resistance to penetration by the sharp end of a geological pick; requires many blows for excavation. 
	Stiff 
	Can be indented by thumb-nail; slight indentation produced by pushing geological pick point into soil; cannot be moulded by fingers. 

	Very dense 
	High resistance to repeated blows of a geological pick. 
	Very stiff 
	Indented by thumb-nail with difficulty; slight indentation produced by blow of a geological pick point. 


PS-16.3.3
Trench excavation 

All hand excavateable material in trenches having a depth of less than 1,5 metres shall be excavated by hand. 

PS-16.3.4
Compaction of backfilling to trenches (areas not subject to traffic) 

Backfilling to trenches shall be placed in layers of thickness (before compaction) not exceeding 100mm. Each layer shall be compacted using hand stampers 

a)
to 90% Proctor density; 

b)
such that in excess of 5 blows of a dynamic come penetrometer (DCP) is required to penetrate 100 mm of the backfill, provided that backfill does not comprise more than 10% gravel of size less than 10mm and contains no isolated boulders, or 

c)
such that the density of the compacted trench backfill is not less than that of the surrounding undisturbed soil when tested comparatively with a DCP. 

PS-16.3.5
Excavation 

All hand excavateable material including topsoil classified as hand excavateable shall be excavated by hand. Harder material may be loosened by mechanical means prior to excavation by hand. 

The excavation of any material which presents the possibility of danger or injury to workers shall not be excavated by hand.

PS-16.3.6
Clearing and grubbing 
Grass and small bushes shall be cleared by hand. 

PS-16.3.7
Shaping 
All shaping shall be undertaken by hand. 

PS-16.3.8
Loading 
All loading shall be done by hand. Haulage equipment should be selected in a manner that allows loading by hand to the extent possible.

PS-16.3.9
Haul 
Excavation material shall be hauled to its point of placement by means of wheelbarrows where the haul distance is not greater than 150 m. 

PS-16.3.10
Offloading 
All material, however transported, is to be off- loaded by hand, unless tipper-trucks are utilised for haulage.

PS-16.3.11
Spreading 
All material shall be spread by hand. 

PS-16.3.12
Compaction 
Small areas may be compacted by hand provided that the specified compaction is achieved. Appropriate rollers should be used where higher (than can be achieved by hand) levels of compaction are required. 

PS-16.313

Grassing 
All grassing shall be undertaking by sprigging, sodding, or seeding by hand. 

PS-16.314

Stone pitching and rubble concrete masonry 
All stone required for stone pitching and rubble concrete masonry, whether grouted or dry, must to be collected, loaded, off loaded and placed by hand.  

Sand and stone shall be hauled to its point of placement by means of wheelbarrows where the haul distance is not greater than 150m. 

Grout shall be mixed and placed by hand.  

PS-16.3.15
Manufactured Elements 
Elements manufactured or supplied by the Contractor, such as manhole rings and cover slabs, precast concrete planks and pipes, masonry units and edge beams shall not individually, have a mass of more than 320kg.  In addition the items shall be large enough so that four workers can conveniently and simultaneously acquire a proper hand hold on them. 

PS 17
SUCONTRACTING OF A PROTION OF THE CONTRACT

The successful Tenderer will be required to employ local and disabled people and moreover, subcontract up to a maximum of 30% of the project value to local contractors. The “local contractors” will be located in the Umkhanyakude District Municipality area of jurisdiction and where specifically required by the Employer, the area where construction works are being undertaken.  

PROJECT SPECIFICATION:  PORTION 2
AMENDMENTS TO THE STANDARD AND PARTICULAR SPECIFICATIONS

INTRODUCTION

In certain clauses the standard, standardized and particular specifications allow a choice to be specified in the project specifications between alternative materials or methods of construction and for additional requirements to be specified to suit a particular contract. Details of such alternative or additional requirements applicable to this contract are contained in this part of the project specifications. It also contains additional specifications required for this particular contract.

The number of each clause and each payment item in this part of the project specifications consists of the prefix PS followed by a number corresponding to the number of the relevant clause or payment item in the standard specifications. The number of a new clause or payment item, which does not form part of a clause or a payment item in the standard specifications and which is included here, is also prefixed by PS, but followed by a new number which follows on the last clause or item number used in the relevant section of the standard specifications.

project specification :  portion 2

sabs 1200 PSA:  GENERAL

PSA-3
MATERIALS

PSA-3.1 
Quality 

Where there is a standardization mark programme for any material, all such material supplied shall bear the official standardization mark.

Alternative materials or equipment proposed by the Contractor shall be tested. The test, as well as the materials or equipment, shall be approved by the Engineer prior to any such materials or equipment being built into the works and all costs involved in testing shall be deemed to be included in the rates tendered.

PSA-3.3
Applicable Standards for Cement  (Additional Subclause)
The standard cement specifications SABS 471, SABS 626, SABS 831 and SABS 1466, referred to in clause 3.3, have been withdrawn and are replaced by the new SANS 50197-1 and -2: Common cements, and SANS 50413-1 and -2: Masonry cement. These specifications will be applicable to this contract, and the descriptions and  types of cements specified, will be based on  the designations as defined in these specifications.

PSA-4.
PLANT

PSA‑4.2
Contractor's Office, Stores and Services 

The Contractor's camp shall be kept neat and clean at all times and all surplus or rejected material shall be removed from the site.

PSA-5
CONSTRUCTION
PSA 5.1
Survey

PS A 5.1.1
Setting Out Of The Works

Substitute the first sentence in A 5.1.1 with the following:

“Setting out of the works is the sole responsibility of the Contractor and shall be done from survey beacons  identified by the Engineer. The Contractor shall, within two (2) weeks after the site has been handed over to him, confirm himself that the survey beacons are correct.  Any discrepancy shall immediately be reported in writing to the Engineer.  Any costs or subsequent costs arising from discrepancies, which had not been reported to the Engineer within the aforementioned period, shall be the sole responsibility of the Contractor. A grid of final terrace levels over the site of the works will be issued to the Contractor at the commencement of the contract and it is the Contractors responsibility to preserve all setting out pegs based on this information as given for the duration of the contract.”

PS A 5.4
Protection Of Overhead And Underground Services

Add the following paragraph :

”The Contractor shall as soon as possible after handing over of the site, commence with the detection to existing services, continue with it without interruption, and finalise it at least 7 days before excavation starts at that particular section.”

PSA-5.8
Ground and access to works

Add the following:

”On completion of operations the Contractor shall restore the ground surface, wherever it may have been disturbed, to its original condition by filling in all ruts with material similar to the material within the rut and levelling the ground and, where necessary, planting grass and shrubs as may be required.  Any boundary fences which have been removed or damaged by his operations and activities shall be repaired and/or reinstated at the Contractor’s expense”.

PSA-5.9
Accommodation of Traffic (additional subclause)

Where construction work has to be carried out on or near public roads, the Contractor shall deal with traffic as specified in SANS 1921-2 (2004): Construction and Management Requirements for Works Contracts, Part 2 : Accommodation of Traffic on Public Roads occupied by the Contractor. The Contractor is also referred to Project Specification 
PS-10. 

PSA-8.
MEASUREMENT AND PAYMENT 

PSA-8.3
Scheduled fixed-charge and value-related items 

PSA-8.3.2
Establishment of Facilities on the Site  

PSA-8.3.2.1
Facilities for the Engineer 

Add the following additional subitems:

(d)

Carports (state number) 


 Unit : Sum

The tendered rate shall cover all costs as specified in Subclause 8.3.2.3 of SABS 1200 A (and 5.5 of SABS 1200 AB to provide these facilities as specified in Clauses PSAB-3.2, 3.3 and 4.2. if applicable).

PSA-8.3.2.2
Facilities for Contractor
For this contract the facilities for the Contractor will not be measured and paid for separately as itemised in Subclause 8.3.2.2. The subitems (a) to (j) will be consolidated into one item and payment under item PSA-8.3.2.2 shall be deemed to cover all these subitems. 
PSA-8.4
Scheduled time-related items 

PSA-8.4.2
Operation and maintenance of Facilities on Site  

PSA-8.4.2.1
Facilities for Engineer 

Add the following additional subitems:

(e)
Carports 


 Unit : Sum

(f)
Survey instruments 


 Unit : Sum

The rates tendered shall cover all costs as specified in Subclause 8.4.2.3 of SABS 1200 A and 5.5 of SABS 1200 AB to operate and maintain these facilities as specified in Clauses PSAB-3.2, 3.3 and 4.2.

PSA-8.4.2.2
Facilities for Contractor
Consolidate subitems (a) to (j) of Clause 8.4.2.2 into one item as in PSA-8.3.2.2. Payment under PSA-8.4.2.2 shall be deemed to cover subitems (a) to (j).
project specification  :  portion 2

sabs 1200 PSD  :  EARTHWORKS 

PSD-1
EARTHWORKS

The Contractor is referred to SANS 1921 - 5: Earthworks activities which are to be performed by hand
PSD-3
MATERIALS

PSD-3.1
Classification for excavation purposes

PSD-3.1.2
Classes of excavation
The classes of excavation in clause 3.1.2 shall in general apply to all excavations where use is made of conventional methods and plant and equipment.

Where labour-intensive methods applicable to targeted labour are specified, soft excavations shall be defined as follows:

“PSD-3.1.2(a)
Soft excavation
Soft excavation for labour-intensive work where excavations are to be carried out by hand methods, shall be excavation in material that can be efficiently removed and loaded with picks, shovels and other hand tools by an average able-bodied person or group of persons. Soft excavation shall include small boulders that can be removed by hand methods.

Soft excavation can be further broken down by introduction of an additional class such as “Soft Excavation Class A”, which is excavation defined as soft, but which can only be excavated with difficulty.

The criteria for classifying Soft Excavation Class A shall be as follows:

Granular material: -
dense material with high resistance to penetration by the point of a geological pick; several blows are required for removal of material;  7 to 15 blows of the dynamic cone penetrometer are required to penetrate 100 mm; and

Cohesive materials -stiff to very stiff material requiring 6 to 8 blows of the dynamic cone penetrometer to penetrate 100 mm, where: 

"stiff" material 
can be indented by thumbnail; slight indentation produced by pushing a  geological pick point into the soil; cannot be moulded by fingers; and where:

"very stiff" 
material
can be indented by thumbnail with difficulty; slight penetration of point produced by blow of geological pick.

Where soft excavation class A material is encountered, it shall be measured and paid for as an extra over soft excavation.

PSD-5
CONSTRUCTION

PSD-5.1
Precautions

PSD-5.1.1
Safety
PSD-5.1.1.2
Safeguarding of excavations
· Add the following subparagraph:

“(g) 
The Contractor or his agent or his representative shall not require or allow any person to work under unsupported overhanging material or in an excavation which is more than 1,5 m deep, and any excavation which has not been adequately supported or braced if there is a danger of the overhanging material or the sides of the excavation collapsing.  The support, shoring or bracing to be designed and constructed by the Contractor, shall be strong and sturdy enough to support the sides of the excavation in question.”

PSD-5.2.2.1
Excavations for general earthworks and for structures
· Add the following additional subparagraph:

“(f) 
The Contractor shall so plan his cut-to-fill operations that all excavated material is used in the manner that is most appropriate.

The Contractor shall conserve all suitable surplus material and he shall not borrow, spoil or waste any material unnecessarily.  If excavated material designated for a particular purpose become contaminated, is incorrectly used or becomes unavailable through injudicious planning of excavation operations, the Contractor shall replace the contaminated material and make good any shortfall with material of quality at least equal to that of the said selected material.

Where selection of excavated material is required, the method of excavation shall be so arranged as to avoid double handling.  Wherever possible excavated material shall be placed in its final position without being stockpiled.  If stockpiling is unavoidable, materials intended for different uses shall be stockpiled separately

project specification  :  portion 2

sabs 1200 PSDB  :  EARTHWORKS (Pipe trenches)

PSDB-5
CONSTRUCTION

PSDB- 5.1
Precautions

PSDB-5.1.5
Trench Excavations (additional subclause)
The precautions for excavations as specified in Clause 5.1.1 of Section 1200 D, 1200 DA, and the relevant clauses in PSD and PSDA, shall also apply to all trench excavations.

The Contractor shall take all the steps necessary to ensure that no person is required or allowed to work in a trench or any other unsupported overhanging excavation which is more than 1,5 m deep, and any excavation which has not been adequately supported, shored or braced if there is any danger whatsoever of the sides of the excavation collapsing. The support, shoring or bracing to be designed and constructed by the Contractor, shall be strong and sturdy enough to support the sides of the excavation in question.

project specification  :  portion 2

sabs 1200 psGA  :  CONCRETE (SMALL WORKS)

PS GA-3

MATERIALS

PS GA-3.2

Cement
PS GA-3.2.1
Applicable specifications
The standard cement specifications SABS 471, SABS 626, SABS 831, SABS 1466 and SABS 1491, have been withdrawn and are replaced by SANS 50197-1: Common cements, and SANS 50413-1: Masonry cement. These specifications will be applicable to this contract and the descriptions and types of cements, where specified, will be based on the designations as defined in these specifications.

PS GA-5.4.1.4 
Prescribed mix concrete 

Add the following :

“The structural concrete in this contract shall comply with the following specification.

· The minimum 28 day strength shall be as specified in drawings

· The maximum water/cement ration shall be 0.42

· The minimum cement content shall be 400 kg/m3

· The cement used must be extended with a minimum of 30% Fly Ash or 50% GGBS

A detailed mix design by an approved concrete testing laboratory before any concrete is poured in the works and provision shall be made by the contractor for the cost of the design in his rates. 

PS GA-8:
MEASUREMENT AND PAYMENT

PS GA-8.1
Measurement and rates
PS GA-8.1.2
Reinforcement
Replace subclause 8.1.2.2 with the following:

PSGA-8.1.2.2
Mild steel and high tensile steel will be measured by mass for the diameters or range of diameters as scheduled.

Welded mesh will be scheduled separately for each type and mass per square metre of mesh.”

Replace subclause 8.1.2.3 with the following:

“PSGA-8.1.2.3
The unit rate for steel bars shall cover the cost of supply, cutting, bending, placing in position, and fixing of the reinforcing and supporting steel scheduled. The rate shall also include the provision of all spacer devices and binding wire, as well as the cost of tests in terms of SANS 920.

The unit rate for welded mesh shall cover the supply, cutting and placing of mesh, as well as the cost of all waste due to laps.”

Project specification:  portion 2

sabs 1200 PS lb:  bedding (pipes)

PS LB 3.3
BEDDING

Add the following to LB 3.3:

All pipes shall be classified as rigid pipes and shall be laid on a Class C bedding except sub soil  drainage, which shall be classified as flexible pipes.

PS LB 5
CONSTRUCTION

PS LB 5.1
General
PS LB 5.1.4
Compacting
Substitute "90 % of mod AASHTO" in LB 5.1.4 with "93 % of mod AASHTO (100 % for sand)".

PS LB 8
MEASUREMENT AND PAYMENT

PS LB 8.2
Scheduled Items
PS LB 8.2.2.4
From stockpile (provisional)

a)
Selected granular material 
  Unit  :  m3
b)
Selected fill material 
  Unit  :  m3
The rate shall cover the cost of obtaining, handling and transport regardless the distance, of the required bedding material from the stockpile, the delivery thereof at positions that are spaced along the trench in such a way as suits the working method of the Contractor, as well as the removal of material displaced by this importation within the free-haul distance.

Project specification:  portion 2

SABS 1200 PS LD : SEWERS
PSLD 2.3 
DEFINITIONS

Add to the Sub-Clause:

Normal Blasting

The method which an experienced blaster employs when carrying out general blasting of hard rock material in trenches.

Close Proximity Blasting

The method which an experienced blaster employs when carrying out blasting of hard rock close to adjacent service or structures requiring additional but smaller charges in order to break up the hard rock without damaging the adjacent services or structures.

PSLD 3 
MATERIALS

PSLD 3.1.1 
Vitrified Clay Pipes

Delete Sub-Clause 3.1.1.2 and substitute:

Vitrified clay sewer pipes shall be plain ended “ Vitro” (or equal) pipes having a crushing strength of at least 45Kn/m. The joints of pipes of 100mm and 150mm diameter shall comprise natural rubber rings within polypropylene couplings.

PSLD 3.1.3 
FC Pipes

The FC pipes and fittings comply with the applicable requirements for Series 4 pipes as set out in SABS 819.

The FC pipes and couplings shall be bitumen dipped.

PSLD 3.4 
Bedding

Bedding of sewers shall be for flexible pipes (SABS 1200 LB) or concrete encased.

PSLD 3.5.2 
Precast Concrete Manhole Sections

Add the following end of the Sub-Clause:

Joints between all wall sections and under roof slab shall be primed and sealed with a plasticized butyl rubber compound (“Bltujoint Putty” by ABE or similar approved) complete with one layer of 200mm wide compatible PVC tape and primer (similar or equal to the “Corro Clad” system supplied by Denso South Africa (Pty) Ltd) to be supplied and applied circumferentially to the outside of each wall section joint.

PSLD 3.5.6 
Mortar

Delete the sub-clause and substitute the following:

Mortar for brickwork and, where so ordered by the Engineer, for external plasterwork to manholes shall be composed of one part of cement to three parts of clean pit sand. Mortar for the internal plasterwork to manholes where ordered and to the benching within manholes shall be composed of one part of cement to three parts of sand.

PSLD 3.5.8 
Manhole Covers and Frames

Add to the first paragraph of the Sub-Clause:

After installation all exposed portions of the CI cover and frame shall be thorough cleaned and painted with two coasts of approved epoxy tar, particular attention being paid to the painting of the underside of the covers and frames.

Precast concrete manhole cover slabs, adaptor slabs and lids shall comply with the applicable requirements of SABS 1294 and to the details shown on the drawings. The precast concrete cover slab shall be so designed as to withstand a point load in the centre, as specified in Clause 8.7 of SABS 1294, of 50 kN for light duty covers and 100Kn for heavy duty covers. The lifting lugs shall be made of 6mm dia grade 316 stainless steel rod. The openings and undersides of all covers and slabs be coated with two coats of “Proofex 3”.
PSLD 4 
PLANT

PSLD 4.1 
Pipe Handling and Rigging Equipments

Add to the Sub-Clause

The Contractor will be responsible for clearing the areas required for pipe storage which shall include the removal of rock, stones and all combustible material. He shall also be responsible for maintaining the area in a clean and tidy condition for the duration of the Contract.

Upon delivery of the pipes, fittings, specials and valves, these will be inspected jointly by the Engineer’s Representative and the Contractor. Any pipes, etc found to be damaged shall be returned to the factory for repair or replacement; in which case the costs of additional transport, repair or replacement shall be borne by the Contractor.

The Contractor will be held fully responsible for the care and safety of all pipes and fittings, etc on site and shall bear the cost of all renewals which may be necessary to make good losses, damages or breakages. Furthermore, he shall fully responsible for handling and re-loading material at the storage areas and for transporting and offloading of all such materials to their correct places along the pipeline route.

PSLD 5 
CONSTRUCTION

PSLD 5.4 
Connections to Manholes

Add the following paragraph to the sub-clause:

The rates tendered for the construction of manholes are to include for whatever additional costs there may be over and above the tendered rates for the supply, lay, joint, bed and test pipelines, for the supply and fixing the short lengths of pipes entering and leaving manholes.

PSLD 5.6.1 
General

The underside of all manhole roofs and edges of the access opening therein and precast concrete covers and lids shall be painted with two coats of “Proofex 3” as supplied by Fosroc (Pty) Ltd, P.O. Box 477, New Germany,3620, or similar approved rubberized bitumen coating so as to protect the concrete from the effects of sewage gases.

The tendered rates for manholes shall include for this work.

PSLD 5.6.5 
Precast Concrete Manholes

In the first sentence, delete “Delete LD-5” and substitute with “with drawings”

PSLD 5.7 
Concrete Casing to Pipes

Add to the sub-clause:

Concrete casing is to be of 20/19 grade concrete with a minimum thickness of 100 mm below, above top and on each side of the pipe as and where ordered by the Engineer.

PSLD 5.9.3 
Recording Location

Delete the last sentence and substitute

The records shall be handed to the Engineer, in a form acceptable to the Engineer, at the time when the Contractor claims payment for the relevant work.

PSLD 6 
TOLERANCES

PSLD 6.2 
Overall Centre-line Control and Manhole Locations

In second line delete “+-300mm” and substitute “+-150mm”

PSLD 6.3 
Manhole Invert-levels

In second line read “+- 25mm” for “+-50mm”

PSLD 7 
TESTING

PSLD 7.1.4 
Sub Clause

Delete the Sub-Clause and substitute the following:

The sewer, and the house connections along its length, shall be tested simultaneously between manholes or chambers, as applicable. The house connections and the section of the sewer under test shall be suitably “plugged” at the open ends using plugs or stoppers which have been braced adequately.

PSLD 7.2.2 
Water Test

The Water Test will not be acceptable under this Contract.

PSLD 7.2.6 
Watertightness Testing of Manholes

Wherever ordered in writing by the Engineer that a manhole is to be tested, it is to be tested in his presence or in the presence of his authorized representative, in the following manner.

All sewer inlets and outlets to and from the manhole shall be closed with expanding plugs or other apparatus. Water is then to be introduced into the manhole up to a level 25mm below the underside of the roof slab. The water level is to be maintained for not less than one hour or such longer periods as may be necessary to accurately record the rate of leakage, if any. Careful and accurate records shall be kept at frequent and regular intervals of the variation in the level of the water in the manhole and of the quantity  of the water added so that the rate of leakage may be properly determined. In the event of the rate of leakage, if any, exceeding 1.25l/h/m of depth of manhole, or in the event of any weakness, defect or fracture or visible signs of leakage occurring in the manhole under test, the Engineer shall have the right to order the test to be discontinued and the Contractor shall thereupon, at his own expense, search for and rectify any weakness or defect in the manhole under test, such work or rectification to consist of repair or replacement or both. The manhole shall thereafter be refilled with water and retested in the manner specified. This process shall be repeated until a satisfactory test is obtained.

The Contractor will be paid once only for the hydraulic testing of any given manhole at the rate per manhole to be quoted by him in the Schedule of Quantities. The Contractor’s prices for the hydraulic testing of manholes shall include for all arrangements for the supply of water for testing the cost of water used in testing where the water is not obtained free of cost from the Employer for all work of rectification for retesting and fro all labour required to carry out the specified tests.

PSLD 8 
MEASUREMENT AND PAYMENT

PSLD 8.2.5 
Inspection Chambers

Delete the first and second lines and substitute the following:

Separate items will be scheduled for manholes, backdrops and inspection chambers, etc of each type and of each depth (measured from top of cover to invert) in increments of 1.0m for the first one metre thereafter  in increments of 0.5m. The rate shall cover the cost of dealing with any excavation (in all materials, including backfilling and the disposal of surplus materials).

PSLD 8.2.6 
Erf Connections

Add at end of Sub-Clause:

“or servitude boundary”

PSLD 8.2.11 
Connection to Existing Sewers

The tendered sum is to include for breaking into the existing sewer manholes, dealing with the flow, caulking in the new pipe and for breaking out and reforming benching as required, making the manholes watertight.

PSLD 8.2.13 
Intermediate and Hard Rock Excavation (New Sub-Clause)

Insert new Sub-Clause as follows:

8.2.13 Extra over item ‘Manholes’ above for

a) Intermediate excavation




………………………………. Unit : m3
b) Hard rock excavation by normal blasting or other methods as selected by the contractor (see PSLD 2.3)





………………………………. Unit : m3
c) Hard rock excavation by close proximity blasting (see PSLD 2.3)
...…………. Unit : m3
d) Boulder excavation Class A



……………….……………… Unit : m3
Separate items will not be provided for depth increments. Volumes will be computed from the plan area of either the intermediate or hard rock material, excluding the plan area of the specified pipe trench, which is within the area occupied by the manhole plus a side allowance of 600mm and the depth from the top of either the intermediate or hard rock material to the bottom of the same material or to the underside of the Manhole base slab, whichever is the lesser.

The rates shall cover the additional cost of the excavation and handling of the more difficult material and the disposal of material

project specification  :  portion 2

sabs 1200 PS le  :  stormwater drainage

PS LE 3
MATERIALS

PS LE 3.1.1
Material for Subsoil Drainage
PS LE 3.1.1.1
Pipes
Pipes for subsoil drainage shall be uPVC pipes complying with the requirements of SABS 791, but shall be perforated or slotted.

The size of perforations in perforated pipes shall in all cases be 8 mm in diameter ± 1,5 mm and the number of perforations per metre shall be not less than 26 for 110 mm pipes and 52 for 160 mm pipes.  Perforations shall be spaced in two rows for 110 mm pipes and in three rows for 160 mm pipes.

Slotted pipes shall have a slot width of 8 mm ± 1,5 mm.  The arrangement of slots shall be subject to the Engineer's approval, but the total slot area shall be not less than that presented for perforations.

Pipes without slots or perforations required for conveying ground water from the subsoil drainage proper to the point of discharge, shall be uPVC pipes as specified above.

PS LE 3.1.1.2
Crushed-stone
Crushed-stone in subsoil drains shall be 19 mm single-sized stone complying with the grading requirements of stone for concrete in SABS 1083.

PS LE 3.1.1.3
Geotextile Blanket
The geotextile blanket around subsoil drains shall comply with the requirements of PS DK 3.1.4 in all respects.

PS LE 3.1.1.4
Sand

Sand obtained from approved commercial sources shall be clean, hard and durable and shall comply with the following grading requirements:

D15  :  0,2 mm to 0,4 mm
D85  :  1,2 mm to 4,7 mm

PS LE 5
CONSTRUCTION

PS LE 5.1
Trench Bottom
PS LE 5.1.3
Unsuitable Founding Conditions
Substitute "90 % of MAASHTO maximum density" in LE 5.1.3 with "90 % of MAASHTO maximum density (100 % for sand)".

PS LE8.2
BEDDING AND LAYING

PS LE 8.2.14
Supply And Install Subsurface Drains According To Drawings 
  Unit  :  m
The length shall be measured on the centre line of the completed subsurface drain.

The rate shall cover the cost of supplying, transporting, off-loading and installing all materials as well as for cutting, wasting, overlapping and installing of the materials where applicable.

PARTICULAR SPECIFICATION

pa: BRICKWORK AND PLASTER
PA1
SCOPE

PA1.1
This specification covers the general requirements for buildings and other masonry structures, including plastering.

PA2
INTERPRETATION

PA2.1
Other relevant Standards/Specification


This specification should be read together with SABS 1200 AA. 

PA2.2
Applicable Edition of Standards


Each standard specification referred to in this specification shall be deemed to be the latest edition, applicable on the tender closing date. 

PA2.3
Definitions and Symbols


For purposes of this specification, the definitions and symbols given in the National Building Regulations and Building Standards Act, 1977 (referred to further on in this specifications as "Building Act"), where applicable, shall apply.  (Definitions: pages 5 to 14, Symbols : page 23.)

PA3

MATERIALS

PA3.1
Cement


Cement shall conform to the requirements of SABS 471.

PS3.2
Lime


Lime shall be of approved manufacture, well burnt and of uniform quality conforming with SABS 523.

PA3.3
Sand


Sand to be used for mortar and plaster shall comply with the requirements of SABS 1090.
PA3.4
Clay Bricks


Clay bricks must conform to SABS 227. A sample of bricks to be used for construction must be given to Engineer for approval before construction bricks are delivered to site.


The contractor will be required to carry out necessary tests and provide certificates for compliance of the bricks with SABS 227. The cost of these tests will be deemed part of the scheduled rates and no additional payment will be made therefore.


Best quality engineering bricks shall be used for all foundation and concealed situations. 

PA3.5
Damp-Proofing


Material used as a dampproof course shall conform to the requirements contained either in SABS 248 or in SABS 952.  Type FV fibre-felt sheets or Type C polyethylene sheets shall be supplied under the contract.

PA3.6
Fibre Cement Sheets


Fibre cement flat sheets, minimum 15 mm thick, shall comply with the requirements of SABS 685.

PA3.7
Storage

PA3.7.1
Cement and Lime


Cement and lime stored on the site shall be properly protected against moisture to the satisfaction of the engineer. 

PA4
CONSTRUCTION

PA4.1
Brickwork


Brickwork shall be well and regularly bonded, with no false headers and none but whole bricks except where legitimately required as closers.  All bricks must be thoroughly dampened before laying and each brick is to be laid with full joints and pressed into its bed so as to squeeze out superfluous mortar and give a finished joint not exceeding 8 mm thick in the case of the face work or 13 mm thick in the case of plastered walls or work not exposed to view.  All joints, both horizontal and vertical, notwithstanding any grade custom to the contrary, are to be filled solid with mortar for their full width and depth, each course being flushed with mortar, worked well down into all vertical joints before the succeeding course is laid.  Horizontal joints and vertical joints of face work shall be pointed flush in manholes and catchpits, but shall be pointed and finished with a tooled recessed joint elsewhere.  Plastered walls shall have the joints raked out to a depth not less than 13 mm and not more than 20 mm, and subsequently refilled with mortar of the same proportions as the original bedding mortar.  In no circumstances may joints to be so formed as to expose any perforation in the units.


Wire ties, where required, shall be stainless steel and are to be installed at 5 per square metre.
PA4.2
Mortar


The mix proportions for the mortar are given below:



Portland cement
50 kg



Lime


0-40 l



Sand*


200 l max.



* measured loose and damp

PA4.3
Plastering


Plaster shall be of the same proportions as the bedding mortar. Any other plaster mixes will be subject to the approval of the Engineer.

PA4.4
Dampproof Courses


The areas to be covered by dampproof courses are indicated on the drawings.  Dampproof shall be laid on a surface which shall not contain any sharp objects which may perforate the membrane.  The full width of the wall and the whole area under the floor is to be covered by the membrane and shall overlap by not less than 100 mm under the floor, and by not less than 150 mm under the wall.  All joints shall be effectively sealed.  Where shown on the drawing, the dampproof course is to be stepped up one course of brickwork in the inner skin.  Proper returns are to be made at all doorframes.

PA4.5
Window Sills


Windowsills shall be formed as shown on the drawings and as hereafter described:


Dampproof sheeting shall be provided one brick course below the sill and shall be turned upwards and terminate behind the window frame to provide an efficient weather-tight seal.


All external sills and some internal sills, where shown, shall be formed in quarry tiles and other internal sills where shown are to be of fibre cement sheet minimum thickness 15 mm to SABS 685 with approximately 20 mm projection beyond the finished face of the walls.


External sills shall be laid to a 20( weathered slope while internal sills shall be laid horizontal.


All tiles shall be bedded in 3:1 cement mortar and neatly pointed.

PA4.6
Lintels with Brickwork Reinforcement


Lintels over doors, windows and openings, where ordered by the Engineer, shall be reinforced with four layers of BRC brickforce, or approved equal.  The latter reinforcement shall extend a minimum of 450 mm beyond any opening.  All joints in the six courses of brickwork above the opening shall be fully flushed with cement mortar.  Shoring to soffits of lintels shall be left in position for at least 14 days after building the lintel and the brickwork shall be kept damp with wet bags for the whole of this period.

PA4.7
Wall Vents


Ventilator openings shall be formed through walls where indicated and shall be provided with double brick terracotta louvred air bricks (fitted with plastic insect screens) both externally and internally (where scheduled) set flush into the work and neatly pointed.  Internal wall vents are to be of an approved plaster of paris type where scheduled.

PA4.8
Building in Frames, etc


Door and window frames are to be set up, built into position, bedded and pointed in cement mortar, with any necessary cutting to brickwork, fitting and making good, as the brickwork is built up.  In the case of doorframes, wrought iron right angled cramps are to be fixed to doorframes and built into brickwork at every eighth course.


Where pipes, frames, brackets or other such parts pass through or have to be set into brickwork, the bricks shall be carefully cut and fitted to maintain regularity of courses and uniformity of joints, the shaped bricks being embedded and pointed to conform with the surrounding brickwork.  Where such parts have to be set into position after brickwork is built, holes shall be left wherever possible, in preference to cutting out bricks, and the work shall be subsequently made good in the manner described.

PA4.9
Floor Finishes

PA4.9.1
Granolithic Floor Screed


Granolithic shall consist of one part cement, one part sand and two parts 5 mm stone chips and oxide where required, thoroughly mixed as for concrete and placed in a layer not less than 20 mm thick, levelled or graded and trowelled to a smooth uniform surface.  To ensure proper bond, the concrete surface to be covered shall be clean, roughened by chipping, flushed with water and coated with cement grout just before placing of the granolithic layer.  Granolithic finish is to be steel floated with V joints in squares of 1,20 m to 1,80 m, the joints extending for the full depth of the granolithic.  Joints are not required in the granolithic screed where it is to be overlaid by tiles or carpeting.

PA4.10
Chasing Walls


Where indicated by the electrical contractor, the construction contractor shall chase brickwork and concrete work to accommodate electrical conduit - such chasing shall precede plastering or rendering and on no account shall plastering or rendering be commenced until the electrical tubing has been installed.  No horizontal or diagonal chases shall be permitted.


Elsewhere, electrical conduit shall either be cast into concrete or shall be run on the surface afterwards as may be directed by the Engineer.

PA4.11
Weather


In any period of interruption caused by inclement weather, and at the completion of each day's bricklaying, freshly laid brickwork should be protected.

PARTICULAR SPECIFICATION 
pb: CARPENTRY, JOINERY AND IRONMONGERY WORK
PB1

SCOPE

PB1.1
This specification covers the general requirements for carpentry, joinery and ironmon​gery work for civil engineering projects and the methods by which the finished work is to be measured for the purpose of payment.

PB2

INTERPRETATION

PB2.1
Other Standards/Specification


This specification is to be read with SABS 1200 AA .

PB2.2
Applicable Edition of Standards


Each standard specification referred to in this specification shall be deemed to be the latest edition, at the closing date of tenders for this contract. 

PB3

MATERIALS

PB3.1
Timber


Roof timber forming a permanent part of the work shall conform to the requirements of the relevant standard specifications SABS 563, SABS 653, SABS 876, SABS 1089 or SABS 1245.


All timber other than that used for temporary works or shuttering shall be treated as specified in SABS 1288 and SABS 05, and allowed to dry thoroughly before being used.  

PB3.2
Fibre Cement Sheets


Fibre cement flat and corrugated sheets shall comply with the requirements of SABS 685.  The flat sheets shall be minimum 15 mm thick.

PB3.3
Hardware


Locks, hinges and other hardware shall be provided to doors; all ironmongery and fixings shall be chromium plated on brass except where otherwise specified.

PB3.3.1
Hinges


Hardwood doors in hardwood frames are to be provided with brass butt hinges as scheduled with three hinges per leaf.

PB3.3.2
Door Locks and Furniture


External door to be fitted with a night latch (to be supplied by the Employer) and a Henderson No 463 bow handle, secured with brass bolts passing through the door with nuts on the inside.

PB3.3.3
Cabin Hooks


One 200 mm brass cabin hook complete with eyes to be fitted to each door including for hardwood block plugged to walls or post as scheduled.

PB4

MEASUREMENT AND PAYMENT

PB4.1
The work will be measured and paid for in accordance with the units and rates scheduled.  

PB4.2
The tendered rates for doors are to include for the manufacture, fitting hanging and protective painting  thereof.

PB4.3
The tendered rates for ironmongery shall include for the supplying and fitting complete with non-corrosive screws and/or bolts.

PARTICULAR SPECIFICATION
pc:  PAINTING
PC1

SCOPE

PC1.1
This specification covers the general requirements for painting, including methods of preparation of materials to be painted, cleaning, priming, undercoating and finishing, and also methods by which the finished work will be measured and paid for.

PC2

INTERPRETATION

PC2.1
Supporting Specification


This specification must be read together with SABS 1200 AA 

PC2.2
Applicable Edition of Standards


Each standard specification referred to in this specification shall be deemed to be the latest edition at the tender closing date. 

PC3

MATERIALS
PC3.1
Emulsion Paints for Exterior Use


Emulsion paints for exterior use shall comply with SABS 634.

PC3.2
Calcium Plumbate Primer


Calcium plumbate primer shall comply with SABS 912.

PC3.3
Undercoats for Paints


Undercoats for air-drying protective and decorative paints shall comply with SABS 681.

PC3.4
Structural Steel Paints


Structural steel paints shall comply with SABS 684.

PC3.5
Colours of Paints


Specification for colours of paints shall comply with CKS 279.
PC3.6
Paints Generally


Paints shall be of the best quality and of approved manufacture.  Tints shall be selected during the course of the work, and for this purpose the Contractor, before placing orders for paints, shall submit samples to the Engineer for approval as to quality and tints.  All paints shall be brought on to site in unopened tins and no adulteration will be permitted.

PC4
CONSTRUCTION

PC4.1
Painting Generally


Paints must be applied strictly in accordance with the manufacturer's instructions relating to preparation of surfaces, undercoats and application.


No painting on exterior work is to be done in wet weather, or upon surfaces which are not thoroughly dry and all work is to be entirely free from dust before painting is proceeded with.  All paintwork shall be properly cleaned and rubbed down between each coat.  No coat shall be applied until the Engineer has passed the previous one as dry, hard and satisfactory.


All colours for paintwork and all makes and composition of paint shall first be approved by the Engineer before putting the work in hand.


All paint marks and spots on surfaces on which they are not intended shall be removed to the satisfaction of the Engineer and the work shall not be accepted until this is assiduously carried out.  Where required, paintwork shall be finished to a straight line.


Painting must be carried out in co-operation with other contractors and may be allowed to proceed only at the discretion of the Engineer.


Identification colour marking shall comply with SABS 0140.

PC4.2
The Preparation of Steel Surfaces for Coating


Cleaning and preparing steel in order to produce a surface suitable for application of coatings shall comply with the methods specified in SABS 064.  Grease, oil and watersoluble salts shall be removed as specified under Clause 3.  Mill, scale, rust, weathered paint and most contaminants shall be removed by blast cleaning.  If this method is impracticable, hand-tool cleaning shall be carried out if permitted by the Engineer.


The coating shall be applied after cleaning and after the corrosion-inhibiting wash has been used.

PC4.3
Galvanised Steel


After the surface has been properly cleaned and prepared as specified in Clause 6, SABS 064, calcium plumbate priming paint conforming to SABS 912 shall be applied, followed by finishing paint conforming to SABS 684, Type B.  The priming coat shall not be allowed to weather before application of the finishing coat(s) specified in the Schedule of Quantities.

PC4.4
Painting Woodwork


The surface of the wood should be properly prepared by planing and sandpapering.  Knots in the wood shall be carefully sealed by means of a shellac-based knotting solution.  All woodwork shall be adequately primed.  When paint coats are applied, the primer shall always be harder than the following undercoat.


The topcoat as specified in the Schedule of Quantities.

PC4.5
Painting Plastered Walls


All plastered walls are to be sealed and primed.  Thereafter the walls are to be given three coats of exterior quality PVA paint, all as specified in the Schedule of Quantities.

PC4.6
Painting Concrete Surfaces


All concrete surfaces which are to be painted are to be thoroughly brushed and washed with a detergent and cold water.  Thereafter the surfaces are to be primed and then painted with two coats of exterior quality PVA paint, unless otherwise specified in the Schedule of Quantities.

PC4.7
Varnishing


All hardwood is to be prepared, stopped and sealed with "007 Longlife Marine varnish" before installation.  After installation and sanding down, two further finishing coats are to be applied, allowing for rubbing down between coats, all in accordance with the manufacturer's instructions.
PC5
BASIS OF MEASUREMENT AND PAYMENT FOR PAINTING

The cost of painting metalwork is to be included in the tendered prices for supply and installation.  Painting to walls and ceilings will be paid for per square metre of surface painted.  Other items will be paid for per linear metre or on a lump sum basis, as set out in the Schedule of Quantities.

PARTICULAR SPECIFICATION

psp: STEEL PIPES
SCOPE

This specification covers the design, manufacture and supply of bare, electric welded low carbon steel pipes, specials and other fittings for the conveyance of water at ambient temperatures and at medium pressures.

2.
INTERPRETATIONS

2.1
Supporting specifications

2.1.1
Where this specification is required for a project, the following specifications 


shall form part of the contract document:


(a)  Project specifications;


(b)  SABS 1200A and SABS 1200AA, as applicable;

2.1.2
Reference is made to the latest issues of the following standards:

DWS
1131
Lining and coating of steel pipes and specials.

SABS
1200
As given in 2.1.

SABS
62
Steel pipes and pipe fittings up to 150 mm nominal bore, suitable for





 screwing to


SABS 1109 
pipe threads.

SABS
719
Electric welded low carbon steel pipes for aqueous fluids (ordinary 





duties).

SABS
974
Rubber joint rings (non-cellular).

SABS
1431
Weldable structural steels.

SABS
044
Welding.

SABS
0121
Cathodic protection of buried and submerged structures.

BS
534
Steel pipes and specials for water and sewage.

BS
2633
Class 1 arc welding of ferritic steel pipework for carrying fluids.

BS
2815
Compressed asbestos fibre jointing.

BS
4360
Weldable structural steels.

BS
4416
Method for penetration testing of welded or brazed joints in metals.

BS
4504
Flanges and bolting for pipes, valves and fittings.  etric series.

BS
5500
Specification for unfired fusion welded pressure vessels.

SIS
05 59 00
Pictorial surface preparation standards for painting steel surfaces 





(Swedish)

API
5L
Line pipe.

API
1104
Standard for welding pipelines and related facilities.

AWWA
June 1955
Design of wye branches for steel pipe.

AWWA
M11
Steel pipe - a guide for design and installation.  (Second edition)

ISO
2084
Pipeline flanges for general use

2.2
Application

This specification contains clauses that are generally applicable to the design, manufacture and supply of steel pipes, specials and fittings for duties up to 4,6 MPa.  Should no other specification for pipes of outside diameter larger than 2 220 mm be included in a contract, then the requirements of this document shall apply.

2.3
Definitions

For the purposes of this specification the definitions and abbreviations given in the applicable specifications listed in 2.1 and the following definitions shall apply:

     
Skelp:    The jointing edges of steel coils used to manufacture spiral welded pipes.

     
H:   The cross-sectional shape of a weld at skelp

     
Cut and shut bend:  See definition with sketches in BS 2633

3.
MATERIALS

3.1 
Pipes and specials

Materials used for the manufacture of pipes and specials of nominal bore up to 150 mm shall conform to SABS 62 and API 5L:  steel grades up to X52, whilst that for pipes and specials of nominal bore over 150 mm shall conform to SABS 719:  steel grades A, B and C, as well as API 5L:  steel grades X46, X52, X56 and X60.

Flanges shall be manufactured from steel plates conforming to BS4360, or SABS 1431 grade 300W.  Specials and fittings shall be manufactured from materials conforming to SABS 62 for nominal bores up to 150 mm, and to BS 534 for nominal bores over 150 mm.

3.2
Rubber joint rings

     
Rubber rings shall comply with SABS 974 Class F.

3.3
Jointing materials

Bolts, studs, nuts and washers for flanges shall be of materials conforming to the requirements of BS4504 unless otherwise specified.  Gaskets for flanged joints shall be of compressed asbestos fibre to BS 2815 grade A, and full faced with a minimum thickness of 3 mm.  For pressures up to and including 1,6 MPa, cloth-inserted rubber may be used.

4.
PLANT

The Contractor shall supply and maintain suitable tools, plant and equipment to manufacture and supply steel pipes, specials and fittings to the required standard.

5.
GENERAL REQUIREMENTS

5.1
Design of pipes

The design stress for pipes subjected to the specified design pressures shall be 60% of the minimum yield stress of the steel.  

Unless otherwise specified in the Schedule of Quantities or on the drawings, the minimum pipe wall thickness to prevent buckling of straight piping due to internal sub-atmospheric pressures, shall not be less than the following:

	Outside Diameter of Pipe

(mm)
	Minimum Wall Thickness (mm)



	160    to 558,8
	4.5

	609,6 to 660,4
	5

	711,2 to 812,8
	6

	863,7 to 1092
	8

	1118  to 1245
	10

	1397  to 1620
	12

	1708  to 1860
	14

	2020  to 2220
	16


5.2
Dimensional requirements

Unless otherwise specified in the Schedule of Quantities or on the drawings, all line pipes shall be of one fixed standard length between 9 metres and 19,5 metres.  Standard pipes from which samples for destructive testing have been cut may be jointed together by butt-welding to form single pipe lengths of the required standard length.

The tolerances on all other dimensions shall be in accordance with SABS 719 clause 4.1, except that for pipe outside diameters bigger than 1 250 mm it shall be +6 mm and 6 mm.  The tolerances on the outside diameters of pipe ends and bodies shall be as specified for pipe diameters of 250 mm to 1 250 mm.

5.3
Fabrication

5.3.1
Welding


Welds shall comply with SABS 719, SABS 044 and BS 2633 as modified below.

a) Sections 1, 2 are excluded.

b) Section 8

In addition to clause 8.1 the following shall also apply:

All butt-welds and branch fillet welds on specials shall where considered possible (refer clause 3.2.4.2, Section 3) have an internal weld.  The weld bead of this internal weld shall not extend above the prolongation of the original inside surface of the pipe by more than 1,0 mm.  Internal reinforcement in the form of backing rings at weld seams shall not be permitted.

c) Section 10

Procedure qualification and qualifying tests shall be restricted to branch connections only.

The internal weld bead/upset metal and flash on the inner surface shall not exceed 1 mm. For pipes and specials to be jointed by butt welding, the internal weld bead shall not protrude more than 1 mm into the bore of the pipe or special.  For electric resistance welded pipes, the height of upset metal and flash on the inner surface shall not exceed 1 mm.  For pipes and specials to be jointed by butt welding, the internal weld bead shall be ground flush with the pipe body for a length of 200 mm from the ends to be jointed.  For pipes and specials to be coupled by flexible couplings, external weld reinforcement or upset metal and flash shall be ground flush with the pipe body for a length of 200 mm from the end to be coupled.

Where automatic submerged-are welding is employed, at least one pass shall be made on the inside and at least one pass on the outside.  This shall apply for double jointing of pipes in the factory as well.  The number of longitudinal weld seams shall not exceed:

i) for pipes up to 1 000 mm nominal diameter;

ii) for pipes larger than 1 000 mm and up to 2 220 mm nominal diameter.

For pipes to be jointed by flexible couplings the pipe manufacture is required to weld steel plates not less than 50 mm x 75 mm x 6 mm thick to each end of all pipes during the pipe manufacturing process, (i.e. before priming, lining and coating).

All manual or semi-automatic welds and repair welds shall only be undertaken by welders qualified under the tests laid down in the Code of Practice for Welding SABS 044.

5.3.2
Pipes

     
Pipes shall be manufactured in conformity with SABS 719.

5.3.3
Specials and fittings

5.3.3.1  
General

All specials and fittings shall be designed and manufactured by the Contractor in accordance with the general arrangement shown on the drawings and/or described in the Schedule of Quantities, in conformity with SABS 62 or sections 3 and 4 of BS534.  In the latter case specials shall be manipulated or fabricated by welding from pipes which have been tested to SABS
719.  Detailed drawings shall be approved by the Engineer.

5.3.3.2
Bends

Bends shall either be smooth formed or segmented.  The maximum angle between oblique butt-ends of segments for gussetted bends shall not exceed 22£ degrees.  Cut-and-shut bends shall not be permitted.  Segmented bends shall be classified as short, medium and long with radii equal to one, two or three diameters respectively.  All bends shall however be of a long radii type, unless otherwise specified in the Schedule of Quantities or on the drawings.

5.3.3.3
Branch connections

Branch connections shall have barrel and branch plate thicknesses such that the maximum stress shall not be greater than that for an uncut pipe of the theoretically required minimum thickness.  However, where it is more economical to provide external reinforcement in the form of saddle-type rings or triform shoes, these forms of reinforcement shall be used to achieve the same results.  The attachment of reinforcement to the pipe branches shall be by full penetration welding.  Branch connections shall be as remote as possible from the seam weld on the barrel, and except where specifically indicated to the contrary on the drawings, the positioning and extent of external reinforcement is to be determined by the following methods:

      (i)
Saddle-type reinforcement:  section 13.3 of AWWA Manual M11.

     (ii)
Triform-shoe reinforcement: in accordance with "Design of Wye Branches for Steel Pipe" by H.S. Swanson and co-authors, published in the Journal of the AWWA, June 1955.

Scour valve tees are to be at right angles to the barrel of the pipe, but tangential to the circumference at the invert of the pipe.  The flanges are to be aligned to suit the gradient of the pipeline as indicated on the drawings.

Unless otherwise specified complete flanged air valve and access branches shall be supplied loose with the one end profiled and prepared for welding to the pipe or special.  Branches are to be prealigned to suit the pipeline gradient as indicated on the drawings.

5.3.3.4
Reducers

Taper pieces shall not have more than two longitudinal weld seams.

5.3.3.5
Flexible couplings

Flexible couplings shall be of the Viking-Johnson type with centre register, except where specified to the contrary in the Schedule of Quantities or on the drawings.  Flexible couplings shall be supplied complete with all necessary bolts, nuts and rubber jointing rings.

5.3.3.6
Insulated joints

Insulated joints shall have their insulation material arranged as given in SABS 0121, unless otherwise specified.

5.3.3.7
Flanges

Flanges shall be of the steel-plate for welding type and shall have flat joint faces, with dimensions and joint surfaces in accordance with BS 4504 or ISO 2084, unless otherwise specified in the Schedule of Quantities or on the drawings.  For flange thickness not covered in BS 4504 and for domed and conical ends the various thicknesses and methods shall be calculated in accordance with section 3 and where applicable manufactured in accordance with the remainder of BS 5500.  Back surfaces may be left unmachined.  All flanges shall be suitable for field welding to pipes and specials and shall conform to BS 2633, section 7, with preparation of plate flanges as shown in figure 41 ("slip-on") for pipes and specials up to 100 mm N.B. and figure 39 or 40 ("bore and fillet") for pipes and specials 125 mm N.B. and larger.  Unless otherwise specified, jointing material i.e. bolts, nuts and washers, in conformity with BS4504 shall be supplied by others.

6.
MARKING OF PIPES AND SPECIALS

All pipes and specials shall be clearly hard stamped alongside a longitudinal or spiral weld on one end of the pipe with the following:

     
(a)  grade and thickness of steel;

     
(b)  serial number of the pipe or specials;

     
(c)  nominal diameter;

     
(d)  hydraulic test pressure.

The applicable drilling table shall be stamped on the periphery of all flanges.  Bends shall have their centre plane marked with two small punch marks close to both ends to facilitate correct positioning in laying.

7.
STORAGE, HANDLING AND TRANSPORT

Pipes and specials shall be protected against damage at all stages from manufacture to delivery.  The ends of all pipes and specials shall be protected against denting.  Pipes shall be transported and stacked in a manner such as to prevent deformation of the pipe body in excess of 2 percent of the diameter.  Dents causing a protrusion in excess of 3 mm into the interior of the pipe shall be repaired by cutting out.  The Contractor shall be responsible for dispatching and transporting of the pipes to site and off-loading.   Suitable access along the pipeline route will be provided unless otherwise specified.

Access for delivery on site might be restricted by poor weather conditions and the Contractor shall make due allowance for such disruption.  Unless otherwise specified the pipes shall be off-loaded adjacent to the laying position, and placed on sandbags or other approved protective supports.

As indicated on the drawings, the Contractor shall stack the pipes, specials and fittings at the top or bottom of very steep inclines from where the pipeline construction Contractor will transport them to their destination as required.  He will furthermore provide in the rates for his delivery trucks to be hauled/towed up the steep inclines along the pipeline route where necessary.

8.
INSPECTION AND METHODS OF TEST

8.1
General

Factory inspection, supervision of tests, and adjudication of test records shall be carried out by an independent Inspectorate appointed by the Employer to act on behalf of the Engineer.  Tests and inspections shall be carried out at the manufacturer's works at his expense.  He shall provide all necessary testing facilities, labour, instruments, equipment and samples that might be required, free of charge.  The Inspectorate shall be afforded every facility during the course of manufacture and testing to enable the inspection to be carried out effectively.  All test samples shall be selected by the appointed inspectors, and all instruments used for testing purposes shall be approved by the inspectors and if in their opinion any instrument should require calibration, such instruments shall be calibrated at the expense of the Contractor, by the SABS or other such body as may be approved by the Inspectorate.  No mechanical working or straining of pipes and specials shall be allowed after testing and inspection.

8.2
Non-destructive inspection

8.2.1
Visual inspection

All finished pipes and specials shall be visually examined and shall be free of injurious defects as defined in API 5L section 10.7.  In addition welds on specials shall be inspected by the application of a penetrant-dye on the inside of the welds.  No trace of the dye should appear on the outside.

8.2.2
Ultrasonic inspection to API 5L

Pipes shall be made by an approved welding process and 100 percent of all longitudinal or spiral welds on straight pipes shall be checked with an approved ultrasonic method capable of continuous and uninterrupted inspection of the weld seam in accordance with API 5L, sections 9.14, 9.15, 9.16, and 9.17, except that the equipment shall be checked with an applicable reference standard at least twice every working turn.

8.2.3
Radiographic inspection to API 1104

(a)
Longitudinal welds:  All electric fusion welded pipes shall be inspected by radiological methods for a distance of 200 mm from each pipe end.

(b)
Spiral welds: All electric fusion welded pipes shall be inspected by adiological methods for a distance of 100 mm from each end of each length of pipe and of the complete "H" at all skelp and welds, including 150 mm of the spiral welds in both directions away from the intersection points of the skelp and welds.

(c)
Circumferential butt welds and welds on specials: 100 percent of the weld length shall be examined.  When consistently acceptable results are obtained, the number of welds to be so tested may be reduced by mutual agreement between the Engineer, Inspectorate and Contractor.

(d)
Repairs

      (i)
Straight piping - 100 percent of the total length of all repairs shall be examined radiographically.  Where repairs are made before ultrasonic inspection, and such repairs pass ultrasonic inspection, no further radiographic inspection of same is required.

    (ii)
Specials - 100 percent of all repairs shall be examined radiographically.

(e)
Pipes for rail, road and river crossings:  100 percent of the total length of all welds shall be examined radiographically.

8.2.4
Hydrostatic testing

All pipes shall be hydrostatically tested to a pressure such as to produce a circumferential tensile stress in the steel not less than 90 percent of the minimum yield stress of the steel, or 9 MPa, whichever is the lesser.  Each individual straight pipe shall be subjected to a hydrostatic test in accordance with the methods described in API 5L section 5.  Leaks or sweats shall be considered injurious defects.  Should it not be possible to hydrostatically test straight piping and/or specials, a liquid penetrant test shall be done on all welds over and above the non-destructive tests specified above.  This will only be applicable with the prior written approval of the Engineer.

8.2.5
Liquid penetrant testing

Where requested by the Inspectorate, liquid penetrant testing shall be done in accordance with BS 4416.

8.2.6
Magnetic particle testing 

Where requested by the Inspectorate, magnetic particle testing shall be done in accordance with ASME Boiler and Pressure Vessel Code, Section V, Article 7.

8.3
Repair of injurious defects

Injurious defects found by non-destructive testing of welds, visual examination, hydrostatic testing or determined by any other means to exceed the limitations in API 5L section 10.7 shall be repaired in accordance with API 5L sections 10.8 and 10.9, but subject always to the requirements of this specification.

 8.4
Destructive testing

8.4.1
Tests

Destructive tests shall be performed in accordance with SABS 719 clause 7.2 on the first pipe and thereafter on one of every 500 subsequent pipes.

8.4.2
Sampling and compliance with the Specification. 

This shall be performed in accordance with SABS 719 clause 6.

9.
MEASUREMENT AND PAYMENT

Measurement and payment shall be per linear metre of straight pipe fabricated, supplied and delivered to site.  Measurement and payment of specials and fittings shall be per the number of each special and fitting fabricated, supplied and delivered to site.  Where pipe linings and coatings are applied prior to delivery, the rates for pipes, specials and fittings shall include for all such linings and coatings as required under Departmental Specification DWS 1131, unless otherwise specified in the Schedule of Quantities.

PARTICULAR SPECIFICATION

pd: VALVES
PD 1
GATE VALVES

Gate Valves shall bear the official mark of SABS and be SABS approved. They shall comply with SABS 664 for waterworks pattern valves of the types, classes and sizes listed in the Schedule of Quantities and shall be provided with the following :

	
	Description
	Specification

	1
	Flanges
	Double flanged, to be in accordance with and drilled off-centre to SABS 1123, Table 1600, 2500 or 4000 as scheduled. 

	2
	Spindles
	Non rising, bronze or stainless steel with spindle nut either bronze or gunmetal

	3
	Handwheels
	Direction of rotation for opening valves shall be clockwise when viewed from the top and appropriate wording must be embossed at the top indicating direction of “close” and “open” with arrow heads

	4
	Tests
	Valves to be subjected to “closed end” and “open end” pressure tests to one and half times the working pressure. Valve body shall be tested to twice working pressure. Under all the tests, no leakage to occur

	5
	Paint
	As in PD4 

	6
	Other
	· Type B gunmetal trim

· Valves should permit repacking of the gland whilst valve is under pressure

· Factory test certificates to be provided with each valve

· Rates in the schedule of quantities to include requirements to comply with specification




PD 2
REFLUX VALVES

Reflux valves shall, except where otherwise specified, be double flanged single door swing type and shall be fitted with gun metal seats and bronze hinge and clack pins.  In the case of reflux valves to be mounted horizontally, the design shall be such that the gate rests against the seat in the absence of flow or of differential pressure, without the aid of springs or external counterweights.  Reflux valves shall comply with the requirements of SABS 144 for working pressures as required for each application, but not less than 1600 kPa working pressure.

PD 3
AIR VALVES

PD 3.1
General
The materials and workmanship employed in the manufacture of air valves shall be of a similar standard to that set out in SABS 664 for waterworks pattern gate valves and they shall be provided with individual test certificates for each valve from the manufacturer; all valves are to be inspected, and the hydraulic tests witnessed, by an Inspector to be appointed by the Engineer, and the tendered rates for the valves shall include for making arrangements for independent inspections.   The Inspectors' fee and recoverable expenses will be for the account of the Employer, fees and expenses arising from abortive or repeat visits due to non-compliance with the specified requirements will be for the Contractor's account and will be deducted from amounts due to the Contractor.

PD 3.2
Types of Air Valves

Air Valves shall be standard types (epoxy coated flanges; stainless steel sleeve, bolts, nuts, studs etc), of the double orifice type, and shall be equal or similar to the "Vent-O-Mat" (RBX series: 50 mm dia valves: 050 RBXc2511; 80 mm valves: 080 RBXc1601) type in which a small orifice, manufactured from Grade 316 stainless steel and having a minimum orifice size of 2,0 mm diameter, shall be capable of releasing accumula​tions of air at all pressures throughout the specified working pressure range and shall be drop-tight at 0,5 Bar.   The large orifice shall be suitable for admitting or expelling large quantities of air during emptying and filling of the pipeline.  The opening of the valve (to atmosphere) shall be enclosed by a stainless steel mesh which has been fixed into the valve body to prevent the entry of small insects or vermin into the valve.

All welding of stainless steel shall be carried out in workshops dedicated to the fabrication of stainless steel products.   Care shall be taken that the correct welding rods and approved welding procedures have been used for each application, and the Engineer shall have the right to request a certificate from the manufacturer in which the weld procedures used for the manufacture of valves supplied are stated.

All welds and weld beads, internal and external, shall be smoothed down by grinding and buffing.    All stainless steel shall be pickled and passivated before the valve is assembled and tested.

PD 3.3
Testing

Each air valve is to be subjected to the following tests at the factory :


(a)
First, fill the valve with water and apply the factory test pressure through the inlet of the valve.   Under this condition there shall be no weeping from any part of the valve.


(b)
Second, drain the valve and refill the valve with water and apply the maximum working pressure through the inlet of the valve and maintain for at least five minutes.   Under this condition there shall be no loss of water from the valve.


(c)
Third, gradually reduce the pressure applied under (b) above to atmospheric pressure, empty the valve and refill slowly expelling the air through the valve until it is full of water.   Raise the pressure to the minimum working pressure, maintain that pressure for at least five minutes and again there shall be no loss of water from the valve.


(d)
Fourth, maintain the minimum working pressure applied in (c) above, isolate the water inlet and introduce small amounts of compressed air into the valve without lowering the pressure in the valve.   The lower float shall drop away from the upper float when sufficient air has accumulated in the valve.   As soon as the accumulated air in the valve has discharged through the small orifice, the valve shall again close to a watertight condition.    This process shall be repeated for at least five different pressures which are equally spaced between the specified minimum and maximum operating pressures, and the valve shall close automatically when all the air has escaped without any dribbling and shall have a drop-tight shut-off.

PD 3.4
Table of Particular Requirements for Air Valves

	
Scheduled Items


	Nominal diameter (mm)
	80
	80
	25/50

	Class
	40
	25
	16

	Flange Size and Rating
	SABS 1123

Table 4000
	SABS 1123

Table 2500
	SABS 1123

Table 1600

	Flange Drilling
	SABS 1123

Table 4000
	SABS 1123

Table 2500
	SABS 1123

Table 1600

	Factory Test Pressure (metres head of water)
	800
	500
	320

	Field Test Pressure (metres head of water)
	as for pipeline
	as for pipeline
	as for pipeline

	Working Pressure (metres head of water) :
	
	
	

	(a) Maximum
	400
	250
	160

	(b) Minimum
	10
	10
	10


PD 4
PAINTING OF VALVES

PD 4.1
The cleaning and painting of valves as specified hereunder is to be carried out at the factory prior to despatch to site.

PD 4.2
All cast iron surfaces of every valve shall be prepared for painting to a thoroughly clean condition free of all grease and deleterious matter.    Steel surfaces shall be prepared in accordance with Swedish Standard SIS 05 5900 for a Sa 2.5 finish.

PD 4.3
Internal surfaces shall then be treated with two coats of Copon Hicote 151E or other approved non-toxic epoxy resin paint to give a total minimum dry film thickness of 160 micrometres; both coats being applied within 48 hours of commencement of painting.

PD 4.4
External surfaces shall, immediately after cleaning, be treated with one of the following alternative paint systems :


(a)
System 1 - for valves situated in underground chambers or exposed conditions.



Apply three coats of an approved epoxy coal tar paint to give a minimum total dry film thickness of 240 micrometres; all three coats being applied within 72 hours of commencing the first coat.


(b)
System 2 - for valves situated in pump stations etc.

Apply one coat of zinc chromate primer followed by one coat of undercoat tinted where necessary, and a final coat of best quality gloss enamel.    The total dry film thickness of the system shall be not less than 200 micrometres.

PD 4.5
Non-ferrous metal or stainless steel surfaces shall not be painted.

PD 4.6
After erection on site all valves shall be cleaned and the paint work refurbished where necessary to restore the condition to that at the time of leaving the factory.

PD 5
PAYMENT

The prices quoted for all valves are to include for independent factory testing of valves, which test will be witnessed by Inspectors appointed by the Engineer.
PARTICULAR SPECIFICATION
pZ: ENVIRONMENTAL SPECIFICATION
EMPLOYER'S ENVIRONMENTAL MANAGEMENT SPECIFICATION FOR ENVIRONMENTAL MANAGEMENT OF CONSTRUCTION PROJECTS

TABLE OF CONTENTS


PAGE
PZ1
Introduction
SW.58
PZ2
Site Establishment and Housekeeping
SW.63
PZ3
Construction
SW.66
PZ4
Reinstatement and Rehabilitation
SW.76
PZ
EMPLOYER'S ENVIRONMENTAL MANAGEMENT SPECIFICATION FOR ENVIRONMENTAL MANAGEMENT OF CONSTRUCTION PROJECTS

PZ1
INTRODUCTION

PZ1.1
SCOPE

This specification is additional to the South African Bureau of Standards Standardised Specification for Civil Engineering Contracts and must be read in conjunction with the said specification.

This specification covers the principles, responsibilities and requirements generally applicable to implement effective environmental management during the execution of any construction contract. The aim of this specification is to ensure that construction activities are conducted in an environmentally and socially responsible manner. 

PZ1.2
INTERPRETATIONS

This specification contains clauses that are generally applicable to the implementation of effective environmental management on construction contracts. Interpretations of, and variations to, this specification are set out in the project specification. 

PZ1.2.1
Supporting specifications:

Reference is made to the SABS 1200 standards which are to be read in conjunction with this specification. All aspects of these SABS requirements which are relevant to environmental management during construction contracts will apply.

PZ1.2.2
Principles

The following principles should be considered at all times during construction phase activities:

· The Environment is considered to be composed of both biophysical and social components.

· Construction is a disruptive activity and all due consideration must be given to the environment, particularly the social environment, during the execution of a project to minimise the impact on affected parties. 

· Minimisation of areas disturbed by construction activities will minimise many of the construction related environmental impacts of the project and reduce rehabilitation requirements and costs.

· As minimum requirements, all relevant standards relating to international, national, provincial and local legislation, as applicable, shall be adhered to. This includes requirements relating to waste emissions (e.g. hazardous, airborne, liquid and solid), waste disposal practices, noise regulations, road traffic ordinance etc.

· All effort should be made to minimise, reclaim or recycle ‘waste’ material.

PZ1.3
DEFINITIONS

For the purpose of this specification, the definitions given in SABS 1200 shall apply.

Additional definitions which shall apply to this specification are as follows:

Environmental Control Officer: Either an Employer’s staff member or an Environmental Consultant assigned to the project on a part or full-time basis. The Environmental Control Officer will be part of the Project staff and will advise the Engineer on all environmental matters relating to the works, in terms of this specification and the project specification, if applicable. 

Environmental Officer: Either an Employer’s employee (e.g. Quality Assurance Inspector) or Consultant designated to monitor the implementation and compliance with the environmental specifications and environmental management plan on a daily basis.

Cleared surface: “surface vegetation” as referred to in SABS 1200 C 2.3 will be deemed to be any woody or herbaceous vegetation but exclude grasses, sedges, rushes and reeds. Clearing and grubbing shall for the purpose of this specification mean the removal of all woody and herbaceous vegetation including stumps, but excluding grass and groundcover vegetation.

Engineer: Is to read Engineer or Supervisor (in the case of the NEC contract), whichever is applicable to the Contract.

Interested and Affected Parties (IAP): All persons who may be affected by the project either directly or indirectly, or who have an interest or stake in the area to be affected by the project. IAPs include landowners, tribal or local authorities, public interest groups etc.

Liquid Waste Stream: Any reagent solutions, fuels, oils, greases, contaminated run-off, sewerage and wash water, etc. 

Open Trench: Open trench will, for the purpose of this specification, be deemed to include: clearing and grubbing; stripping of topsoil; trenching; placing of bedding; pipe-laying; placing of selected fill; backfilling to ground level; removing excess material; construction of cross berms to channel water (if required); and replacement of topsoil to final finished level (refer to Figure 1: Appendix A).

Progressive Reinstatement: Reinstatement of disturbed areas to topsoil profile on an ongoing basis, immediately after selected construction activities (e.g. backfilling of a trench) are completed. This allows for passive rehabilitation (i.e. natural recolonisation by vegetation) to commence. See also ‘Open Trench’ and ‘Rehabilitation’.

Project Manager: The person responsible for co-ordinating and integrating activities across multiple, functional lines.

Rehabilitation: Rehabilitation is defined as the return of a disturbed area to a state which approximates the state (where possible) which it was before disruption. Rehabilitation for the purposes of this specification is aimed at post-reinstatement revegetation of a disturbed area and the ensurance of a stable land surface. Revegetation should aim to accelerate the natural succession processes so that the plant community develops in the desired way, i.e. promote rapid vegetation establishment.

Riparian vegetation: Vegetation occurring on the banks of a river or stream (i.e. vegetation fringing a water body). In this specification, riparian vegetation in terms of removal, storage and replacement (see PZ3 17.1 and PZ3 17.2), is only applied to sedge, grass, ground-cover, reed, bulrush, or herbaceous component of riparian vegetation and excludes the woody component. 

Sedges: Grass-like plants growing in wetland/ marshy areas or adjacent to water. 

Subsoil: Subsoil is the soil horizons between the topsoil horizon and the underlying parent rock. Subsoil often has more clay-like material than the topsoil. Subsoil is of less value to plants, in terms of nutrient (food) and oxygen supply, than topsoil. When subsoil is exposed it tends to erode fairly easily. 

Timeous: At least 5 working days prior to an activity.

Topsoil: This is defined as the A horizon of the soil profile. Topsoil is the upper layer of soil from which plants obtain their nutrients for growth. It is often darker in colour, due to the organic (humic) fraction. Topsoil is deemed for the purposes of this specification as the layer of soil from the surface to the specified depth required for excavation (see PZ3 5.3, relevant SABS 1200 clause and project specification). Where topsoil is referred to, it is deemed to be both the soil and grass / ground cover fraction. (see ‘Cleared Surface’) 

Veld: This is defined for the purpose of this specification as unimproved natural vegetation areas (e.g. grasslands). 

Water body: Any open body of water including streams, dams, rivers, lakes, and the sea.

Wetland: A seasonally, temporally, or permanently wet area which also may exhibit a specific vegetation community. It is often marshy in character.

Wetland Vegetation: Vegetation which is indicative of a wetland environment - for example, sedges, rushes, reeds, hydrophilic grasses and ground-covers, but for the purposes of this specification excludes woody species.

Xeriscaping: Landscaping with vegetation which has a low water usage. The objective is to conserve as much water as possible, whilst still beautifying an area (i.e. conservation and aesthetics). Concept embraces utilising indigenous as opposed to exotic plants.

PZ1.4
ABBREVIATIONS

DWAF
: Department of Water Affairs and Forestry

ECO
: Environmental Control Officer

EMP
: Environmental Management Plan

EMPR
: Environmental Management Programme Report

EO

: Environmental Officer

IAPs
: Interested and Affected Parties

IEM
: Integrated Environmental Management

MSDS
: Material Safety Data Sheet

NEC
: New Engineer Contract or The Engineering and Construction Contract

(  :   Indicates the project specification must be referred to, to clarify the clause. 

PZ1.5
DRAWINGS

Drawings referred to in this specification are included in C4.4 Drawings of Section C4 Site Information.

PZ1.6
FORMS

Forms referred to in this specification are included in Part T2 or attached to this environmental specification. 

PZ1.7
CONDITIONS OF CONTRACT

PZ1.7.1
Duties and Powers of the Project Manager

The Project Manager is ultimately responsible for ensuring compliance with the environmental specification and upholding the Employer’s Environmental Policy on a project. 

The Project Manager:

· arranges information meetings for or consults with IAPs about the impending construction activities;

· may on the recommendation of the Engineer and /or Environmental Officer order the Contractor to suspend any or all works on site if the Contractor or his SubContractor/ supplier fails to comply with the said specifications;

· maintains a register of complaints and queries by members of the public at the site office as per attached pro-forma. This register is forwarded to the Environmental Control Officer on a monthly basis. 

PZ1.7.2
Duties and Powers of the Engineer / Supervisor (NEC)

The Engineer or Supervisor is responsible for:

· enforcing the environmental specification on site;

· monitoring compliance with the requirements of the specification;

· assessing the Contractor’s environmental performance in consultation with the Environmental Officer from which a brief monthly statement of environmental performance is drawn up for record purposes;

· documenting, in conjunction with the Contractor, the state of the site prior to construction activities commencing. This documentation will be in the form of photographs or video record.

PZ1.7.3
Duties and Powers of the Environmental Control Officer

The Environmental Control Officer:

· briefs the Contractor about the requirements of the Environmental Specification and/ or Environmental Management Plan, as applicable;

· advises the Project Manager and Engineer/ Supervisor about the interpretation, implementation and enforcement of the Environmental Specification and other related environmental matters; 

· attends site meetings, as necessary; 

· monitors the Constructor’s compliance with this specification and the project environmental specification as applicable;

· undertakes periodic audits of the effectiveness of the environmental specifications on the site; 

· communicates environmental policy issues to the Project Manager;

· provides technical advice relating to environmental issues to the Engineer/ Supervisor and Project Manager;

· reports on the performance of the project, in terms of environmental compliance.

PZ1.7.4
Duties and Powers of the Environmental Officer

The Environmental Officer:

· attends site meetings;

· monitors the site for compliance with the Environmental Specification and EMP;

· reports on the performance of the project in terms of environmental compliance to the ECO and Project Manager as per the pro-forma attached; 

· liaises with the ECO on matters of policy and those requiring clarity and advice.

PZ1.7.5
Extent of the Contractor’s Obligations

The Contractor is required to:

· provide information on previous environmental management experience and company environmental policy; 

· supply method statements for all activities requiring special attention as specified and/or requested by the Project Manager, Environmental (Control) Officer and/or Engineer during the duration of the Contract; 

· be conversant with the requirements of this environmental specification and the project specification as applicable;

· brief his staff about the requirements of the environmental specification;

· comply with requirements of the Environmental (Control) Officer in terms of this specification and the project specification, as applicable, within the time period specified;

· ensure any sub-Contractors/ suppliers who are utilised within the context of the contract comply with the environmental requirements of the Employer, in terms of the specifications. The Contractor will be held responsible for non-compliance on their behalf;

· bear the cost of any delays, with no extension of time granted, should he or his Sub-Contractors/ Suppliers contravene the said specifications such that the Engineer orders a suspension of work. The suspension will be enforced until such time as the offending party(ies), procedure, or equipment is corrected;

· bear the costs of any damages/ compensation resulting from non-adherence to the said specifications or written site instructions;

· comply with all applicable legislation in terms of 7.6 below;

· ensure that he informs the engineer timeously of any foreseeable activities which will require input from the Environmental (Control) Officer. 

The Contractor will conduct all activities in a manner that minimises disturbance to directly affected residents and the public in general, and foreseeable impacts on the environment. 

PZ1.7.6
Compliance with Applicable Laws

The supreme law of the land is “The Constitution of the Republic of South Africa”, which states: 

“Every person shall have the right to an environment which is not detrimental to his or her health or well being”

Laws applicable to protection of the environment in terms of Environmental Management (and relating to construction activities) include but are not restricted to:

Animals Protection Act, Act No 71 of 1962

Atmospheric Pollution Prevention Act, No 45 of 1965

Conservation of Agricultural Resources Act, No 43 of 1983

Environmental Conservation Act, No 73 of 1989

Environmental Planning Act, Act No 88 of 1967

Fertilisers, Farm Feeds, Agricultural Remedies and Stock Remedies Act, No 36 of 1947

Forest Act, No 122 of 1984

Forest and Veld Conservation Act, Act No 13 of 1941

Hazardous Substances Act, No 15 of 1973

Lake Areas Development Act No 34 of 1975

Land Survey Act, No 9 of 1921

Minerals Act, No 50 of 1991

Mountain Catchment Act, No 63 of 1970

National Monuments Act, No 28 of 1969

National Parks Act, No 57 of 1976

National Resources Development Act, Act no 51 of 1947

Occupational Health and Safety Act, No 85 of 1993

Provincial and Local Government Ordinances and Bylaws

Soil Conservation Act, Act No 76 of 1969

Water Act, No 54 of 1956

Water Services Act No 108 of 1997

and all regulations framed thereunder and amendments there to. 

PZ1.7.7
Compliance with the Environmental Specification

The Contractor is deemed not to have complied with the Environmental Specification if:

· within the boundaries of the site, site extensions and haul/ access roads there is evidence of contravention of clauses; 

· if environmental damage ensues due to negligence; 

· the Contractor fails to comply with corrective or other instructions issued by the Project Manager or Engineer within a specified time, 

· the Contractor fails to respond adequately to complaints from the public.

Application of a penalty clause will apply for incidents of non-compliance. The penalty imposed will be per incident. Unless stated otherwise in the project specification, the penalties imposed per incident or violation will be:

Failure to demarcate working servitudes
R1000

Working outside of the demarcated servitude
R2000

Failure to strip topsoil with intact vegetation
R1000

Failure to stockpile topsoil correctly
R500

Failure to stockpile materials in designated areas
R500

Pollution of water bodies (including increased suspended solid loads)
R1000

Failure to control stormwater runoff
R1000

Failure to provide adequate sanitation
R500

Unauthorised removal of woody vegetation
R2000

Failure to erect temporary fences
R500

Failure to provide adequate waste disposal facilities and services
R500

Failure to reinstate disturbed areas within the specified time-frame
R3000

Failure to rehabilitate disturbed areas within the specified time-frame
R3000

Any other contravention of the project specific specification
R400

Any other contravention of the particular (general) environmental specification
R300

PZ2
SITE ESTABLISHMENT AND HOUSEKEEPING

PZ2.1
LAYOUT

The Contractor will take into account any of the limitations identified in the project specification with regard to establishment of site, in particular the location of access routes, and establishment layout.

Notwithstanding the provision of a project specification, the Contractor will provide the Project Manager and Environmental Control Officer with a layout design of the site indicating the position of all of the following, as applicable: offices, ablution facilities, storage areas, workshops, laboratories, batching plant, particulate matter stockpile area (i.e. soil/ granular chemicals/ cement fines etc), waste disposal facilities, hazardous substances storage area, access routes, etc. This layout plan is to be submitted prior to site establishment for acceptance. Any changes to this plan require review by the Project Manager in conjunction with the ECO.

The Contractor will take into account prevailing wind directions when designing the site layout to minimise impacts due to dust, unpleasant odours etc.

The Contractor will take into account the positions of residences when designing the site layout in order to minimise noise impacts on the residents.

Site security lighting is to be positioned such that the direct beam is focused away from residential properties and does not pose a nuisance or danger to road users.

No site establishment will be allowed within 100 m of a water body or drainage channel or on a flood plain unless approved by the Environmental (Control) Officer or specified in the project specification.

PZ2.2
SITE CLEARANCE

No trees or shrubs may be removed without the prior permission of the Environmental Officer, unless in keeping with the final site reinstatement and rehabilitation plan.

Topsoil is to be stripped from all areas where permanent or temporary structures and access roads are to be constructed. Topsoil conservation is to be in terms of clause PZ3 5.3 of this document.

PZ2.3
SERVICES

PZ2.3.1
Sanitation

Portable chemical toilets are to be utilised at site unless a connection to sewer is possible or a proper septic tank system is installed. In the case of the septic tank, the installation will require the relevant approvals from the local authority and will require removal upon completion of the contract, unless otherwise directed.

Sanitation facilities will be located within 100 m from any point of work, but not closer than 50 m to a water body.

PZ2.3.2
Solid Waste Facilities

Facilities for solid waste collection are to be provided. These are to be at least a 200 l drum and clearly identified as the point for waste disposal. 

Waste is to be separated into paper, glass and metal with separate collection points for each. The Contractor will ensure that the appropriate recycling Contractors receive this waste.

The Contractor is to institute a daily litter collection programme. The collected waste is to be disposed of regularly and proportionately to its generation at a site designated for waste disposal.

No burning will be permitted on any site unless by approved incineration methods and in a low risk fire area. In the case of incineration, ash is to be co-disposed with spoil in a designated spoil dump. 

No burying of waste will be allowed on any site.

PZ2.3.3
Cooking and Heating Facilities

No open fires will be allowed anywhere on site.

Contained fires (i.e. in a fire drum) will be allowed for heating and cooking only in designated areas, in other cases cooking is restricted to gas or electrical equipment.

PZ2.4
FUELS, HAZARDOUS SUBSTANCES AND OTHER LIQUID POLLUTANTS

PZ2.4.1
Storage and handling

All potentially hazardous raw and waste materials are to be handled by trained staff and stored on site in accordance with manufacturer’s instructions and relevant legal requirements. The product MSDS is to be lodged with the Engineer.

Storage and handling areas for fuels, lubricants, chemicals and other hazardous substances are to be paved with concrete to prevent accidental contamination of the soil. Alternatively, an impermeable liner may be placed beneath above-ground storage tanks. The integrity of the liner is to remain intact for the duration of the contract, until removal.

Open storage vessels, for example shutter lubricant drums, are to be stored under cover to prevent ‘splash’ contamination.

All storage areas are to be bunded (with at least sandbags) and have a peripheral collection drain, with oil interceptors (if required).

The bunded area is to be sufficiently large to contain a spillage equivalent to the volume of one container of the substances stored.

All products to be dispensed from 200 litre drums will be done so with appropriate equipment, and not dispensed by tipping of the drum.

Daily checks are to be conducted on the dispensing mechanism of above-ground storage tanks to ensure the timeous identification of faults.

Collection containers (e.g. drip trays) are to be placed under all dispensing mechanisms of hydrocarbon or hazardous liquid substances to ensure contamination from leaks and dispensing is contained.

The dispensing mechanism of diesel and petrol storage tanks is to be stored in a container when not in use. 

PZ2.4.2
Control of pollutants

A drainage diversion system is to be installed to divert runoff from areas of potential pollution, e.g. batching area, vehicle maintenance area, work shops, chemical and fuel stores, etc if applicable.

Contaminated runoff and waste water is to be directed into a collection system (e.g. sump, attenuation dam, PVC porta-ponds etc.) for treatment or collection and disposal. The final collection point (e.g. sump) is to be PVC lined. 

Collected contaminated runoff/ wastewater is to be pumped out of the final collection point and disposed of at an appropriate landfill site. Sump liners are to be treated in the same manner.

The treated waste water, effluent and contaminated runoff may require analysis prior to discharge as detailed in the project specification or instructed by the Environmental Officer. 

Details regarding proposed methods for treatment of pollutants are to be submitted to the Environmental (Control) Officer for acceptance upon award of the Contract.

Any spillages, irrespective of their size, are to be contained and cleaned up immediately. The Pollution Control section may provide technical assistance for clean up, if required. No spills may be hosed down into a stormwater drain or sewer.

Use of specialised cleanup techniques and/ or products may be required depending on the spill. This will be instructed by the Environmental Control Officer. These will be to the Contractor’s cost. 

PZ2.5
GENERAL

Site staff are not permitted to use any open water body or other natural water source (e.g. springs) for purposes of bathing, or the washing of clothes, machinery or vehicles. Nor draw water from a spring without the permission of the community utilising that spring.

PZ2.6
MEASUREMENT AND PAYMENT

Measurement and payment for compliance with clauses PZ2.1 to 5 of the specification are deemed to be fully included in the Contractor’s rates for fixed and time related Preliminary and General Items scheduled under SABS 1200 A or AA. 

PZ3
CONSTRUCTION 

PZ3.1
CONSTRUCTION METHODS AND PROGRAMME

PZ3.1.1
Construction Method

The Contractor will provide method statements for construction activities (14 working days prior to the activity commencing) relating to the following environments and those listed in the project environmental specification, unless methods have been prescribed in this or the project environmental specification:

· rivers, streams, or any other open water body;

· wetlands;

· access roads (see PZ3.13 below);

· steep slopes (i.e. steeper than 1:4) or less if friable material is present;

· indigenous bush/ forest;

· close proximity (i.e. 50 m or less) to a residential dwelling;

· drilling and/or blasting of rock.

If a construction method employed by the Contractor is not environmentally acceptable to the Employer, the Contractor may be instructed to cease the utilisation of that method in favour of a more environmentally acceptable one, proposed either by himself or the Employer. 

PZ3.1.2
Construction Programme

The Contractor will programme construction so as to minimise the impact on the environment and provide this programme to the Environmental Control Officer for perusal and acceptance at the onset of the contract period. The Environmental Control Officer is to made aware of any amendments to the construction programme or alterations to the scope of work in order that their impacts on the environment can be assessed.

The Contractor (through the Project Manager) will ensure that all affected landowners/ authorities are advised of the proposed programme at the beginning of the contract period.

PZ3.2
AREAS OCCUPIED / DEMARCATION OF SITE

Routes for temporary access and haul roads are to be located within the approved demarcated areas and vehicle movement is to be confined to these roads. Movement of vehicles outside the designated working areas is not permitted without authorisation from the Engineer.

All construction activities are restricted to working areas designated on the drawings and/or demarcated and approved by the Engineer. Materials including spoil are stockpiled at designated areas.

Any areas disturbed outside of the demarcated areas or without permission of the Environmental (Control) Officer or Engineer will be subject to reinstatement and rehabilitation (as per PZ4 below) to the Contractor’s cost.

In terms of pipeline projects, a general maximum working servitude width of 15 m will apply for machine excavation unless otherwise indicated in the project specification. A maximum width of 6 m will apply for manual excavation. These maximum working servitude widths may vary depending on the sensitivity of the environment, as detailed in the project specification.

In sensitive biophysical environments, for example wetlands, indigenous forest / bush, pristine natural grasslands, and sensitive social environments, as defined in the project specification or by the Environmental Control Officer, the working servitude is reduced as indicated in the project specification.

The working servitude shall contain all construction related activities, including, stockpiling of materials, placing of toilets, vehicle movement areas, etc.

Demarcation of linear projects (executed with machine excavation) and features (e.g. pipelines, access roads, etc.) will be by means of wooden stakes. These stakes will be at least 1 m high, painted white and placed at least every 15 m, on either side of the linear feature, in all areas where works are occurring. Progressive movement of stakes is required as linear projects progress.

In the case of a fenced site, the boundary fences will be denoted as the outermost limit of the site, but internal areas may be demarcated with stakes as above. The site boundaries of non-fenced, but ‘contained’ projects are to be delineated using stakes or temporary fencing, depending on the hazard which that site poses.

PZ3.3
SUPPLY OF WORKS FACILITIES

No water may be abstracted from water bodies for the purposes of construction, without approval of the Engineer in consultation with the Environmental Control Officer.

PZ3.4
CLEANLINESS

SABS 1200 AD, clause 5.2.4, second sentence, is to read: “No rubbish or debris shall be deposited below the full supply level (FSL).”

PZ3.5
SITE CLEARANCE

PZ3.5.1
Clearance

Spoil sites will require clearing and grubbing in addition to those areas in terms of SABS 1200 C 5.1.

The site shall only be cleared immediately prior to construction activities commencing i.e. at the last practicable stage.

No trees or indigenous shrubs may be removed without the prior permission of the Environmental (Control) Officer, unless in keeping with the final site reinstatement and rehabilitation plan.

PZ3.5.2 
Disposal of materials

Material obtained from clearing and grubbing operations shall be disposed of at appropriate municipal disposal facilities. They are not to be disposed of as per Paragraph 1 of Sub-clause 3.1 of SABS 1200 C.

Wood obtained from clearing and grubbing operation remains the property of the landowner/ community and must be stacked at sites designated by relevant person. The Contractor will be required to remove and dispose of any wood from site at a designated site for vegetation disposal, should the landowner/ community not require it.

All tree trunks and branches of diameter greater than 50mm are to be cut into lengths not exceeding 2400mm.

Brush wood (i.e. < 50mm diameter) is to be disposed of, or utilised as specified in the project specification or upon instruction of the Engineer. 

PZ3.5.3
Conservation of topsoil

The Contractor is required to strip topsoil (as defined in this specification) together with grass, groundcover and sedges from all areas where permanent or temporary structures are located, construction related activities occur, and access roads are to be constructed, etc. The depth to which topsoil will be stripped shall be 200mm unless stated otherwise in the project specification. 

Topsoil is to be handled twice only - once to strip and stockpile, and secondly to replace, level, shape and scarify.

Topsoil is to be replaced along the contour.

Topsoil is to be replaced by direct return (i.e. replaced immediately on the area where construction is complete), rather than stockpiling it for extended periods. This is feasible for progressive construction (e.g. pipelines), but not necessarily so for reservoirs, site establishments, dams, etc.

Topsoil stockpiles are not to exceed 2 m in height.

Topsoil stockpiles are to be maintained in a weed free condition (i.e. no ‘broad-leafed’ plants regarded as weeds in terms of the Conservation of Agricultural Resources Act No 43 of 1989, or those plants regarded as a ‘general nuisance in the area’ are to be growing on the stockpiles). The Environmental Control Officer will provide guidance as to which plants are weeds and require removal.

The stockpiles are not to be contaminated with sub-soil, or any other waste material.

Topsoil may not be compacted in any way, nor may any object be placed or stockpiled on it.

Topsoil may not be compacted in any way, nor may any object be placed or stockpiled on it.

Topsoil which is to be stockpiled for periods exceeding 4 months is to be vegetated. In summer a mixture of Eragrotis tef (Teff) and Eragrostis curvula (Weeping Lovegrass) (ratio 1:2) is to be applied at an application rate of 6 kg/ha, unless otherwise instructed in the project specification. 

In winter, a mixture of Lolium multiflorum (Annual/Italian Rye grass) and Eragrostis curvula (Weeping Lovegrass) (ratio 1:1) is to applied at an application rate of 6kg/ha (see PZ4 5.3 for sowing times), unless otherwise instructed in the project specification. Fertiliser is to be applied as per PZ4 5.2.

PZ3.5.4
Cutting of trees

Any tree branches which require removal are to be properly pruned and sealant applied to the cut surface, if required.

The Contractor’s attention is drawn to Sub-clause 5.2.3.3 of SABS 1200 C with respect to work in indigenous forests.

Any indigenous trees or bush which require removal in terms of the project, and which have not been identified in the project specification or EMP, are to be timeously indicated to the Environmental Officer prior to work affecting them.

PZ3.5.5
Landscape Preservation and Conservation of Flora

Notwithstanding Clause 5.7 of SABS 1200 C, the Contractor will be required to transplant designated plants to alternative locations as specified in the project specification or identified by the Environmental Control Officer, upon the instruction of the Engineer. 

Transplanting shall be undertaken by employing the following method:

Removal
· Mark the orientation of the tree/shrub (for example, the north-facing side of the trunk indicated by a small arrow made with indelible ink) trunk. Do not scratch a mark on the surface of the trunk;

· Delineate a circle from the trunk with a radius equivalent to the drip-line of the tree, or as indicated by the Environmental Control Officer on site;

· Excavate the tree with an intact rootball.

Replanting
· A hole 500mm larger in diameter than the anticipated rootball must be prepared in advance of the tree removal in order that the tree can be replanted immediately;

· The tree must be positioned as per its original orientation;

· A planting method known as ‘puddling’ must be employed. This method involves the addition of soil and water simultaneously to expels air from the planting hole. Place the tree in its new hole, making sure the top surface of the rootball is level with the ground level. Place a hose pipe in the hole and leave it running whilst extra soil is added around the rootball;

· ‘Compact’ the tree in the hole and attach tree stays for stabilisation.

Compensatory planting of species may be required should transplantation not be feasible, as indicated in the project specification or upon instruction of the Engineer.

PZ3.6
EARTHWORKS

PSZ3.6.1
Backfill material

With reference to SABS 1200 DB sub-clause 3.5, no material stripped or excavated which is classed, in terms of this specification, as topsoil, may be used as backfill in any excavation.

PZ3.6.2
Excavation and backfilling

During excavation ‘conservation of topsoil’, as specified in PZ3 5.3 above will apply.

Excavated material is to be stockpiled along a pipeline trench within the working servitude, unless otherwise authorised. 

Surplus excavated soft, intermediate and hard rock material shall not be disposed of along the pipeline trench as indicated in SABS 1200 DB sub-clause 5.6.3 and 5.6.4, but shall be removed to a spoil site (see PZ3.15 below) designated during the project if applicable, or agreed by the Engineer in conjunction with the Environmental Control Officer and Project Manager.

In certain cases, for example to help stabilise the disturbed area or to reinstate the natural aesthetics of an area, excess excavated intermediate and hard material may be disposed of in a designated manner along a pipeline trench, as indicated by the Environmental Control Officer and Project Manager, or in the project specification. In this case, rock material shall not exceed 250mm in maximum dimension (see PZ4 2.1). 

In terms of SABS 1200 DB 5.6.5 and SABS 1200 LB 3.4.2, deficiency of backfill material shall not be made up by excavation within the free haul distance of 0.5km of site, without the prior approval of the Engineer of the source of the material. Where backfill material is deficient, it should ideally be made up by importation from an approved borrow pit (i.e. one which operates within the ambient of an EMPR.) (See also PZ3 14 below). 

The Contractor will backfill in accordance with the requirements of progressive reinstatement.

The maximum length of open trench shall be specified in the project specification. 

PZ3.7
SAFETY

All works which may pose a hazard to humans and animals are to be adequately protected and appropriate warning signs erected. The Contractor’s attention is drawn to SABS 1200 D section 5.1 in this regard.

With reference to SABS 1200 D 5.1.1.3, where blasting is required in terms of the project, the Contractor will ensure that all structures in the vicinity that could be affected by the activity will be inspected and their condition photographically recorded (as necessary), prior to blasting.

Notice of intent to blast is to be provided to landowners timeously. 

Speed limits, appropriate to the vehicle driven, are to be observed at all times on access roads. Operators and drivers are to ensure that they limit their potential to endanger humans and animals at all times, by observing strict safety precautions.

PZ3.8
PLANT

PZ3.8.1
Silencing of plant 

With reference to SABS 1200 A amend: “built up areas”: to read as “all areas within audible distance of residents (albeit urban, peri-urban or rural areas).”

Appropriate directional and intensity settings are to be maintained on all hooters and sirens.

Silencer units on equipment and vehicles are to be maintained in good working order. 

Construction activities are to be confined to normal working hours (07h30 - 17h00) Mondays to Saturdays, except for the activities designated to be carried out at night. 

PZ3.8.2
Appropriate use of plant

The Contractor will at all times use plant which is appropriate to the task in order to minimise the extent of damage to the environment.

PZ3.9
DEALING WITH WATER ON WORKS

PZ3.9.1
Disinfection of Potable Water Infrastructure

Disinfection water is to be neutralised before release of this water to the environment. 

PZ3.9.2
Discharge of water from site

Any water which is discharged from site is to comply with the relevant Water Quality Guidelines implemented by DWAF. 

Water discharged to the stormwater / sewer system may only be done so with the permission of the relevant local authority.

PZ3.10
CONTROL OF EROSION

Surface erosion protection measures will be required to prevent erosion where slopes are steeper than 1:8 on all soil types.

Erosion protection measures required may include all or some of the below, as specified in the project specification or upon instruction of the Engineer in conjunction with the Environmental (Control) Officer:

· use of groundcover or grass

· construction of cut off berms (earth and/or rockpack) - these are to be angled across the contour and normally would approximate an angle of 30o from the bisector of the contour. 

· placing of brush wood on bare surface;

· pegging of wattle trunks or branches along the contour;

· hard landscaping, e.g. use of Loffelstein walls, ground anchors, gabions etc.

Scour chambers are to be fitted with energy dissipaters, or the jet of water directed onto a protected (i.e. grouted stone pitching/ rock pack/ reno mattress) area to dissipate water velocity and to control and prevent erosion.

Storm water drainage measures might be required on site to control runoff and prevent erosion. 

PZ3.11
CONTROL OF POLLUTION

No waste in a solid, liquid or gaseous state shall be emitted from or spilled on the site without the approval of the Engineer. 

No mixed concrete shall be deposited directly onto the ground prior to placing. A board or other suitable platform is to be provided onto which the mixed concrete can be deposited whilst it awaits placing.

Excess concrete from mixing shall be deposited in a designated area awaiting removal to an approved landfill site. 

The Contractor will contain wash water from cement mixing operations, by directing the water into a sump for collection. The material contained in the sump will be removed to an appropriate landfill site. 

No concrete rubble shall be present at the site. 

Liquid wastes will not be disposed of to storm water drains. They may be disposed of to sewer only if permitted by (local council) legislation.

In the event of pollution of a water body (including sediment loading), the Contractor will provide alternative water supply to users of that water body until the quality of the water body is restored to its previous unpolluted state. For the sake of this clause, pollution is deemed to be a state which is substandard to the normal quality of the water body, but is not necessarily in contravention of the South African Water Quality guideline standards for a prescribed activity.

Any ancillary damages resulting from pollution of a water body will be repaired / remediated at the Contractor’s cost. 

Where, due to construction requirements, pollution of a water body may potentially occur, the Contractor is to ensure adequate measures (e.g. attenuation/ settlement dams / oil absorbent products) are in place to prevent pollution. A method statement is to be provided to this effect (see PZ3 1).

PZ3.12
CONTROL OF FIRE

The Contractor will ensure he has the necessary fire fighting equipment on site in terms of SABS 1200. This will include at least rubber beaters when working in ‘veld’ areas, and at least one fire extinguisher of the appropriate type when welding activities are undertaken, irrespective of the site.

PZ3.13
USE AND MAINTENANCE OF ACCESS FACILITIES

PZ3.13.1
Responsibility

The Project Manager [not the Contractor (SABS 1200 AD 5.3.1)] will be responsible for obtaining permission for temporary and permanent rights of way over all private property affected by project activities. 

The Project Manager will ensure that the Contractor has kept a photographic record of all access facilities and that these are reinstated to a state not worse than upon commencement of the project and to the satisfaction of the landowner (not withstanding that the project’s objective is not to upgrade landowners’ access roads). 

PZ3.13.2
Fencing

Temporary fencing is to consist of 1.2 m bonnox fencing, or similar, suitably tensioned and supported on 1.8 m fencing standards at 3 m intervals, with all necessary straining posts and stays.

All temporary fencing as indicated by the Engineer is removed on completion of the contract.

PZ3.13.3
New Access Roads

Any construction roads created for execution of the project are to be designed to incorporate adequate drainage and water attenuation structures.

Any access roads which incorporate ‘cut and fill’ aspects and/or which are to be surfaced during construction are to be authorised by the Environmental Control Officer and Project Manager. Prior to construction of the road, the Contractor will be required to provide a sketch plan of the road layout (referenced to local topographic, natural and man-made structures). Slope steepness, road width, drainage structures and their frequency will need to be documented and accompany the sketch layout. 

Construction access roads may not be wider than that necessary (maximum width 4 m) for movement of vehicles in one direction only. Should two way traffic be required, points people are to control vehicle movement on the ‘single lane’ road or passing bays are to be used where specified in the project specification or as identified by the Engineer in conjunction with the Environmental Control Officer, unless otherwise stated in the project specification. 

The cut and fill slopes of permanent roads will require grassing, as specified in the project specification or by the Environmental Control Officer, to increase stability and reduce aesthetic impacts. Hard landscaping may be required as per the project specification.

Temporary construction roads will require rehabilitation on completion of construction activities for which they were required. These roads will require rehabilitation as per PZ4 4 or as specified in the project specification. In the case of access ‘tracks’, only ripping to loosen compaction will be required unless otherwise stated by the Environmental Control Officer or project specification. 

Access roads created by the project may only remain unrehabilitated on written request of the landowner, with his acceptance of the state of the road and a clause that the landowner accepts all responsibility for the road and its state.

PZ3.13.4
Maintenance of Existing Access Roads

The Contractor will record, photographically, the state of existing roads which are to be used for access, prior to plant utilising these roads.

During the contract period, the Contractor will ensure that all existing water attenuation and drainage structures are maintained in a state in which they can optimally perform their function.

Upon completion of the construction period, the Contractor will ensure that the access roads are returned to a state not worse than prior to construction commencing. 

PZ3.14
BORROW PITS

Where the Contractor is required to import material this shall be from commercial sources or borrow areas specified in the project specification.

The Contractor may source material from alternative borrow pits provided: the site location; method of winning material and reinstatement and rehabilitation are environmentally acceptable and approved by the Environmental Control Officer.

In this regard, the Contractor shall give the Environmental Control Officer in writing, 30 days prior to opening up alternative borrow pits the following information for acceptance:

· quantities of borrow material required;

· method statement for excavation of material including depth and extent of excavation;

· anticipated ‘active life’ of the borrow area;

· proposal for reinstatement and rehabilitation of borrow area, including final profile;

· written approval from the landowner/ relevant authority that material may be removed from their land subject to their stated conditions, requirements, and royalties, and if the proposal is acceptable to the Environmental Control Officer.

Development and rehabilitation of borrow pit areas are likely to include the following activities (but these must not be regarded as exhaustive):

· Stripping and stockpiling of topsoil as per PZ3 5.3 of this specification;

· Removal (to nominal depth of 500mm) and stockpiling of sub-soil;

· Infill of borrow pit with spoil material;

· Contouring of borrow pit to approximate natural topography and/ or reduce erosion impacts on the site;

· Placement of excavated subsoil over spoil material;

· Placement of stripped topsoil on subsoil;

· Grassing of topsoil in terms of clause PZ4 4 of this specification.

The Contractor is to familiarise himself with the requirements of the Minerals Act No 50 of 1991 in terms of borrow pit development, and the requirements of the EMPR, as applicable. 

PZ3.15
SPOIL SITES

Where the Contractor is required to spoil material, spoil sites must be identified which are environmentally acceptable and approved by the ECO, unless spoil site areas have been identified in the project specification, in which case these will be the designated spoil sites. 

If no spoil sites have been previously identified together with reinstatement and rehabilitation criteria, the Contractor is to provide the following information to the ECO at least 30 days prior to requiring sites to spoil material:

· the location, description of and access to alternative sites identified in order that they may be assessed;

· the quantity of material to be spoiled;

· the type of material to be spoiled (i.e. blast rock/ excavated rock/ soft shale/ subsoil etc.); 

· the proposed method of spoiling;

· the proposed reinstatement and rehabilitation plan including final profile;

· written approval from the landowner/ relevant authority that material may be spoilt on land subject to their stated conditions and requirements and if the proposal is acceptable to the ECO.

Development and rehabilitation of spoil areas are likely to include the following activities (but these must not be regarded as exhaustive):

· Stripping and stockpiling of topsoil as per PZ3 5.3 of this specification;

· Removal (to nominal depth of 500mm) and stockpiling of sub-soil;

· Placement of spoil material;

· Contouring of spoil site to approximate natural topography and/ or reduce erosion impacts on the site;

· Placement of excavated subsoil over spoil material;

· Placement of stripped topsoil on subsoil;

Grassing of topsoil in terms of clause PZ4 4 of this specification.

PZ3.16
NUISANCE

PZ3.16.1
Dust

At all times the Contractor shall control dust on the site, access roads, borrow pits and spoil dumps with water, chemical soil stabilisers or temporary surfacing as specified in the project specification or upon instruction of the Engineer. 

Dust control shall be sufficient so as not to have significant impacts in terms of the biophysical and social environments. These impacts include visual pollution, decreased safety due to reduced visibility, health aspects, and ecological impacts due to dust particle accumulation. 

On gravel or earth roads, vehicle speeds may not exceed 30km per hour.

PZ3.16.2
Noise

The operational layout of the construction site is to be designed to control and reduce noise from source (see clause PZ2 1). 

Machinery and vehicle silencer units are to be maintained in good working order. Offending machinery and /or vehicles will be banned from use on site until they have been repaired. 

Construction activities generating output levels of 85 dB(A) or more (excessively noisy), in residential areas, are to be confined to working hours (08h00 - 17h00) Mondays to Fridays only. 

‘Normal’ or ‘noisy’ working hours may only be extended with the prior written approval of the Project Manager, who has been notified, at least 7 days in advance, of the impending work requiring extension.

The Project Manager will ensure that the neighbours are timeously forewarned of imminent noisy activities.

Should community complaints be received with regard to noise generation, the Contractor will, at the discretion of the Project Manager and Environmental Control Officer, provide an independent and registered noise monitor to undertake a survey of noise output levels from site, and implement measures to reduce noise to legislated levels. 

PZ3.16.3
Visual

All site establishment components, as well as equipment, will be positioned to limit visual intrusion to neighbours (see clause PZ2 1 above).

The type and colour of roofing and cladding materials are to be selected to reduce reflection. 

Security lighting (both temporary and permanent) and lighting required for specific works activities must be placed such that it is not a nuisance to residents and the general public. 

PZ3.16.4
Interference with neighbours and public 


No construction staff may approach site neighbours, for whatever reason, without the knowledge and permission of the Project Manager.

Complaints from neighbours and public with regard to interference from contract staff will be regarded in a serious light, and the offender(s) may be subject to disciplinary action. 

PZ3.16.5
Disruption of Services

Disruption of services, e.g. road access, water and electricity, must be kept to a minimum at all times.

Where service disruption is unavoidable, the Contractor is to advise the Project Manager (at least 7 days in advance), who in turn will timeously warn the affected parties.

PZ3.17
SPECIAL ENVIRONMENTS

PZ3.17.1
Wetlands

Pipeline trenches which traverse wetlands shall be constructed as specified in the project specification. The Contractor will submit a method statement for work in wetland areas as per PZ3 1.1

Construction may not permanently alter the surface or subsurface flow of water through the wetland.

The Contractor shall submit a method statement for review at least 14 days prior to commencing construction in a wetland.

[image: image14.png]FIGHT GERMS BY WASHING YOUR HAND!

~between your fingers.
~under your nalls
~the tops of your hands





The Contractor will remove all wetland vegetation with their root ball intact. This vegetation is to be kept moist at all times. It is to be placed in the shade and covered with moistened hessian cloth until replanting, which is to be undertaken immediately surface reinstatement is complete.

No construction materials may be stockpiled in any wetland areas.

The pre-construction profile of the wetland shall be returned to one similar as before construction, with no created “ridge or channel” features present.

PZ3.17.2
River/ stream courses

The Contractor shall submit a method statement for review 14 days prior to commencing construction. The method statement should highlight (but not be confined to) the following issues:

· detailed plan of crossing including pipe protection works;

· how water flow will be diverted during construction (if applicable);

· containment of contaminated runoff and waste water;

· width of working servitude (if not already detailed in project specification);

· final expected profile of river/ stream banks;

· reinstatement and rehabilitation of river/ stream banks.

The Contractor will remove herbaceous riparian vegetation as indicated in the project specification or by the Environmental Control Officer, with their root ball intact. This vegetation is to be kept moist by means of placing it in the shade, covered with moistened hessian cloth until it is replanted.

The Contractor shall not modify the banks or bed of a water course unless as specified in the project specification. 

Rocks for use in gabion baskets/reno mattresses may not be obtained from a water course. 

The Contractor will not pollute any water body as a result of construction activities (see also PZ3 11).

The Contractor shall not cause any physical damage to any aspects of a water course, other than those necessary to complete the works as specified and in accordance with the accepted method statement

Where a stream or river-crossing requires the diversion of water, a method statement is to be provided to the Environmental Control Officer in this regard for review.

PZ4
REINSTATEMENT AND REHABILITATION

Scope: The intention of this section is to ensure that the condition of the areas disturbed by the project are returned to a state that approximates what they were before the project or better, within reason. The concept of progressive reinstatement is fundamental to cost effective (both financial and environmental) rehabilitation of a site. This concept must be followed at all times. Where landscaping is utilised, the concept is to utilise and restore indigenous plants to the site, in terms of the concept of xeriscaping.

Reinstatement will be required for all areas disturbed by the project. For pipeline projects, this will include the full working servitude, not just the top of actual excavation as per SABS 1200 DB (subclause 5.9.1.1) 

Reinstatement and rehabilitation will ensure that all areas disturbed by the project are returned, within reason, to a state not worse than before the project commenced.

The Contractor will reinstate and rehabilitate all disturbed areas outside of the demarcated working area (as defined in terms of clause PZ3 2 or the project specification) at his own cost and to the satisfaction of the Environmental Control Officer and Project Manager. 

PZ4.1
HOUSEKEEPING 

All areas are to be cleared of rubble associated with construction. This includes the removal of surplus materials, excavation and disposal of consolidated waste concrete and concrete wash water, litter, etc.

All soil contaminated by hydrocarbons, for example from leaking machines, refuelling spills etc., is to be excavated to the depth of contaminant penetration, placed in 200 litre drums and removed to an appropriate landfill site. 

PZ4.2
FINISHING 

PZ4.2.1
Final Grading 

Final levels of all disturbed areas are, where feasible in terms of the project requirement, to be consistent with the natural topography of the area. 

In certain instances, it will be acceptable to reinstate rock onto a works area (e.g. pipeline servitude), provided that that rock does not exceed 250mm in maximum dimension and is placed in a manner consistent with the natural surrounds as indicated by the Environmental Control Officer and Project Manager.

All drainage lines affected by construction are to be reinstated to approximate their original profile. Where this is not feasible due to technical constraints, the profile is to be agreed upon by the Environmental Control Officer and Project Manager.

All compacted (disturbed) areas (including stockpile areas) are to be ripped (along contour) to a depth of 150mm prior to the replacement of topsoil. 

PZ4.2.2
Topsoiling

Topsoil is to be replaced to a minimum depth of 100mm. 

Topsoil is not to be compacted, but once replaced is to be scarified (to a depth of 50mm) consistent with the natural contour. 

If insufficient topsoil is available, subsoil or similar material may be used that may be a suitable substrate after addition of soil improving substances e.g. compost, pH rectifiers (lime or gypsum) etc. Soil testing may be required at an approved facility.

PZ4.3
REINSTATEMENT OF WATER COURSES AND WETLAND AREAS

The Contractor will ensure that water course banks are returned to their original profile unless the project specification states otherwise.

The surface reinstatement of wetland areas is to ensure that no depressions remain which could act as channels for preferential water flow thereby affecting the hydrological regime of the wetland. 

The Contractor will preserve all riparian and wetland vegetation for use in rehabilitation of those environments. This vegetation is to be kept moist at all times. It is to be placed in the shade and covered with moistened hessian cloth until replanting, which is to be undertaken immediately surface reinstatement is complete.

Plants are to be, as nearly as possible, replanted in areas from which they were removed.

PZ4.4
VEGETATION RE-ESTABLISHMENT

The Contractor will ensure that all areas disturbed by contract activities are revegetated to the specified standard.

This standard is deemed to be an 85 % cover with no areas in excess of 0.04 m2 / m2 remaining unvegetated.

Revegetation shall match the vegetation type which previously existed (e.g. kikuyu pastures are to be returned to kikuyu pasture; ‘veld’ grass to ‘veld’ grass, etc.), unless stated otherwise in the project specification.

Prior to re-grassing, and if required: 

· the area is to be scarified or ripped (along contour) to a depth of 50mm to loosen compaction. 

· weeds present on site are to be removed.

Re-grassing, where required, will be either by means of seeding, instant turf (sods), sprigs or plugs as specified in the project specification or as specified by the ECO.

Where sprigs or plugs are utilised, they are to be planted at 200mm centres. The fertiliser shall be applied as per PZ4 5.2. During summer, 25mm of irrigation shall be applied each week until reasonable (60%) ground cover has been obtained. During winter 15mm of irrigation shall be applied each week until reasonable (60%) ground cover has been obtained. The amount of irrigation to be applied will make up the difference between rainfall recorded on site and minimum requirement.

Where instant turf is utilised, it shall be laid as specified in the project specification. The fertiliser shall be applied as per PZ4 5.2. During summer, 25mm of irrigation shall be applied each week until all the turf is visibly growing. During winter 15mm of irrigation shall be applied each week until all the turf is visibly growing. The amount of irrigation to be applied will make up the difference between rainfall recorded on site and minimum requirement.

Grassing shall be undertaken by a specialist grassing Sub-Contractor, unless permission is granted otherwise by the Engineer upon receipt of a written motivation from the Contractor.

The Contractor shall state in writing when the regrassing operation will commence and its expected duration (dates).

Grassing in ‘veld’ areas is to be undertaken as per PZ4 5 below. Cynodon dactylon species may be excluded or substituted from this mixture at the discretion of the Environmental Control Officer, or as specified in the project specification. The seed bulk may be made up with the Eragrostis tef. 

PZ4.5
“VELD GRASS” GRASSING SPECIFICATION

The area to be grassed should be estimated and converted to hectares,

e.g. 100m X 100m = 10 000m2 = 1ha. All fertilizer and seeding rates used in this specification are with respect to hectares.

PZ4.5.1
Regional areas

For re-grassing three distinctive areas exist. These are defined as:

· the Coastal area (a narrow band running from the coast to (15km inland of the coast)

· the Coastal hinterland (a broad band ((50km wide), generally defined as westwards of the coastal belt, and below 800m a.s.l.)

· the area above ( 800m a.s.l. (also called Midlands area). 

PZ4.5.2
Fertiliser 

Standard 2:3:2 (N:P:K) fertiliser shall be used on all sites.

The rate of application will be:

· 200 kg/ha in the Coastal Hinterland areas, and 

· 300 kg/ha in the Midlands and Coastal areas. 

PZ4.5.3
Planting times

Summer (includes Spring) is considered to be between the 1 September and 28 (29) February.

Winter (includes Autumn) is considered to be between 1 March and 31 August. 

Re-grassing will be undertaken (as far as possible) in summer as germination and establishment of grasses is most effective, assuming reasonable spring rains.

Vegetation re-establishment is likely in many cases to be held off until this suitable growing season.

Hydroseeding with a winter mix will only be specified where regrassing is urgently required and cannot wait until the summer season. In this case irrigation will be required as per PZ4 5.4 below.

PZ4.5.4
Establishment and maintenance

During summer, 25mm of irrigation shall be applied each week until reasonable (60%) ground cover has been obtained.

During winter (where annual rye grass is specified) 15mm of irrigation shall be applied each week until reasonable (60%) ground cover has been obtained.

If rapid establishment is required, additional watering may be necessary as specified in the project specification

The amount of irrigation to be applied will make up the difference between rainfall recorded on site and the minimum requirement.

PZ4.5.5
Grass Seed Selection and Application Rates 

The specific seed selection and application rates for each of the defined areas are covered separately, as follows.

PZ4.5.5.1
Coastal area

Summer mix (1 September - 28 February)

	Grass species
	Common name
	General application rate (kg/ha)

	Eragrostis tef
	Teff
	5

	Eragrostis curvula
	Weeping lovegrass
	10

	Chloris gayana
	Rhodes grass
	10

	Digitaria eriantha
	Smuts’ fingergrass
	5

	Total
	
	30


Winter mix (1 March - 31 August)

	Grass species
	Common name
	General application rate (kg/ha)

	Lolium multiflorum cultivar - Midmar
	Annual/Italian rye grass
	10

	Eragrostis curvula
	Weeping lovegrass
	10

	Chloris gayana
	Rhodes grass
	5

	Total
	
	25


PZ4.5.5.2
Coastal hinterland.

Summer mix (1 September - 28 February)

	Grass species
	Common name
	General application rate (kg/ha)

	Eragrostis tef
	Teff
	5

	Eragrostis curvula
	Weeping lovegrass
	10

	Chloris gayana
	Rhodes grass
	10

	Cenchrus ciliarus
	Blue buffalo grass
	2

	Cynodon dactylon
	Couch/KWeek/Star grass
	10

	Total
	
	37


Winter mix (1 March - 31 August)

	Grass species
	Common name
	General application rate (kg/ha)

	Lolium multiflorum cultivar – Midmar
	Annual/Italian rye grass
	10

	Eragrostis curvula
	Weeping lovegrass
	10

	Chloris gayana
	Rhodes grass
	5

	Cenchrus ciliarus
	Blue buffalo grass
	2

	Cynodon dactylon
	Couch/KWeek/Star grass
	3

	Total
	
	30


PZ4.5.5.3
Midlands area

Summer mix (1 September - 28 February)

	Grass species
	Common name
	General application rate (kg/ha)

	Eragrostis tef
	Teff
	4

	Eragrostis curvula
	Weeping lovegrass
	10

	Chloris gayana
	Rhodes grass
	10

	Digitaria eriantha
	Smuts’ fingergrass
	2

	Cynodon dactylon
	Couch/KWeek/Star grass
	2

	Paspalum notatum
	Lawn paspalum
	2

	Total
	
	30


Winter mix (1 March - 31 August)

	Grass species
	Common name
	General application rate (kg/ha)

	Lolium multiflorum cultivar - Midmar
	Annual/Italian rye grass
	10

	Eragrostis curvula
	Weeping lovegrass
	10

	Chloris gayana
	Rhodes grass
	5

	Paspalum notatum
	Lawn paspalum
	2.5

	Total
	
	27.5


PZ4.5.6
Seeding methods

Two methods are recommended, namely hydroseeding and hand-broadcasting. The required method shall be as specified in the project specification. 

All seed supplied should be labelled in accordance with the Government Seed Act No. 20 of 1961 and the Contractor shall be required to produce such certification, if requested by the Engineer. 

PZ4.5.6.1
Hydroseeding

The Grassing Contractor shall be conversant with this method.

Cellulose pulp (consisting of either wood shavings, shredded straw, shredded paper or cotton waste) shall be added to the mix to be applied at a rate of 250 kg/ha.

In addition to the cellulose pulp, compost (consisting of either chicken litter, kraal manure, sugar cane filter cake or mushroom compost) shall be incorporated at a rate of 5m3/ha ((100 X 50kg fertiliser bags/ha). 

PZ4.5.6.2
Hand-broadcasting

Fertiliser, at the appropriate rate, is to be distributed by hand in a manner to ensure that there is an even spread of fertiliser over the site. This is to be done prior to seeding.

The seed mix is to be weighed and made up in an appropriately large container which shall be stirred to ensure no settling out of the grass seed, and a uniform distribution of the different types of seed.

The seed is to distributed by hand in a regular grid broadcasting manner to ensure that there is an even spread of grass over the entire site. 

The area seeded is to be raked over once the seed and fertiliser have been applied to incorporate these elements into the topsoil. 

PZ4.5.7
General

Where there is a possibility of neighbourhood livestock grazing a rehabilitated site these should, as far as is practicable, be excluded for the first 3 months of re-grassing.

PZ4.6
LANDSCAPING

Landscaping of the site may be required as indicated in the project specification.

Compensatory planting of trees or shrubs may be required should the transplantation of such not be successful in terms of PZ3 5.5 or due to plants removed in terms of PZ3 5.4

Planting of trees will be in accordance with the following method:

· All tree holes shall be square in plan;

· Tree holes shall be a minimum of 600mm by 600mm square by 700mm deep;

· Holes are to be backfilled with excavated soil in a ratio of 3:1 with compost. The compost is to be weed free and have been composted at temperatures in the order of 65oC. Where possible, any available topsoil should be placed in the hole at the level where the tree rootball will rest. A handful (half-a-cup) of each Superphosphate and 2.3.2 should be mixed into the soil-compost mix;

· The tree holes are to be backfilled to the point where the tree and its rootball are in the desired position. The tree is to be removed temporarily and the hole filled with water and allowed to drain away. This operation of watering and draining should be repeated at least four times in order that the surrounding ground and hole are thoroughly moist. The tree is then to be replaced and the remaining soil replaced;

· All trees shall be tied (using a tree tie) to a suitable timber stake planted in the ground to a depth of at least 500mm. The stake shall have a minimum diameter of 35mm and shall be at least 300mm higher than the planted tree;

· Water retaining basins of at least 500mm diameters are to be formed around each tree;

· The Contractor is to apply at least 10 litres of water per tree per fortnight for a period of at least 3 months.

The planting of shrubs will be in accordance with the tree planting method with the exception that the holes are to be a minimum of 400mm by 400mm square by 500mm deep, and that the tree stakes and ties are not required.

PZ4.7
ALIEN PLANT CONTROL

All sites disturbed by construction activities will be monitored for colonisation by invasive alien plant species.

The Environmental Control Officer will identify those plants which require removal during both the construction and maintenance period, for the Contractor’s action. 

The Environmental Control Officer will provide advice as to effective methods of removal and control of alien plant species.

PUBLIC COMPLAINTS REGISTER 
	DATE
	COMPLAINANTS NAME
	DESIGNATION/ AFFILIATION
	REASON FOR COMPLAINT
	ACTION TAKEN
	ACTION BY
	ACTION BY DATE
	ACHIEVED BY DATE
	DATE REFERRED TO NW environmental control officer

	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	


MONITORING OF COMPLIANCE WITH ENVIRONMENTAL SPECIFICATIONS

PROJECT NAME: ………………………………………………………………………………………………..
CONTRACT NUMBER: ………………………………………………………………………………………….
PROJECT MANAGER: …………………………………………………………………………………………
ENGINEER’S REPRESENTATIVE / SUPERVISOR: ……………………………………………………….
CONTRACTOR: ………………………………………………………………………………………………….
CONTRACT PERIOD: ……………………………………………………………………………………………
(including start and completion dates):


PERIOD COVERED: ……………………………………………………………………………………………
REPORT PREPARED BY: ………………………………………………………………………………………
------------------------------

Signature

ENVIRONMENTAL CONTROL OFFICER REPORT

PROJECT NAME:




CONTRACT N°

DATE OF SITE INSPECTIONS DURING REPORTING PERIOD: 

___________________________________________________________________________

	Specification Breach
	Spec. No.
	Remedial Action Recommended
	Due Date
	Authority Responsible
	Action Taken

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	


PUBLIC COMPLAINTS

	Complainant
	Designation/ Affiliation
	Date of complaint
	Reason for Complaint
	Action taken 

and date

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	


GOOD PERFORMANCE REPORT

List any aspects of the Contract in which the Contractor is performing well and beyond that which is required in terms of the specification. 

Photographs

Include photographs which illustrate aspects of non-compliance and good performance.

	Photograph 1

Caption


	Photograph 2

Caption




PES: environmental specification

The following guidelines may also be followed:

SECTION 4A: SITE ESTABLISHMENT AND PRELIMINARY ACTIVITIES 

	4A.1   Access to Site 

Sound environmental principles must be followed whilst establishing access to the site. As much as possible, use should be made of the existing roads instead of creating new ones.


	A.1.1 Routing 

a) The contractor must take into account any limitations identified and recommendations made during the environmental duties when deciding on an access route to construction site.

b) The location of all underground services and servitudes must be identified and confirmed.

c) Choice of access routes should take into account minimum disturbance to residents and businesses neighboring the site.

A.1.2 Haulage Roads

a) All roads for construction access must be planned and approved by the Engineer and ECO ahead of construction activities. They should not be created on an ad-hoc basis.

b) Roads must follow natural contours to reduce stormwater erosion.

c) Roads must have as little cut and fill as possible.

d) Road widths and the radii of curves are to be reduced.

e) No trees/shrubs/groundwater may be removed or vegetation stripped without the prior permission of the Engineer/ECO.

f) Agreed turning areas for haulage vehicles are to be formalized and used by the Contractor. No turning maneuvers other than at the designated places shall be permitted.

g) Contractors shall construct formal drainage on all temporary haulage roads in the form of side drains and mitre drains to prevent erosion and point source discharge of run-off.

h) Scour check walls must be constructed in the side drains as follows:

Gradient of Road 

Scour Check Spacing 

<4%

Not required 

5%

20m

8%

10m

10%

5m

i) Scour checks can be constructed from rocks available onsite or using driven wooden pegs. Smaller rocks must be placed on the invert of side drain upstream and downstream of the scour checks.

j) Haulage roads must allow for the natural flow of water 

k) All stream/rivers crossing and temporary bridges shall be built to the Engineer’s approval.

A.1.3 Survey Points 

a) Roads or trails that are cut to provide temporary access for survey work must be minimized.

b) Marking of survey points must be done with the Engineer’s approval.

c) Vegetation clearing must be kept to a minimum during survey operations
	Monitor 

Engineer (E)/ Environmental Control Officer (ECO) 

E

Engineer (E)/ Environmental Control Officer (ECO) 

N/A

Use Existing access roads

N/A

N/A

N/A

E

E/ECO

E

N/A

E

N/A

Monitor

N/A

N/A 

N/A


	Frequency

Prior to moving onto site.

Prior to moving onto site.

Prior to moving onto site

N/A

N/A

N/A

N/A

Prior to moving onto site.

During construction period

Prior to moving onto site.

N/A

N/A

N/A

N/A

Frequency

N/A

N/A

N/A

	4A.2. Setting up Construction Camp

Careful planning of the construction camp can ensure that time and costs associated with environmental management and rehabilitation are reduced


	A.2.1 Layout 

a) Choice of site for the Contractor’s camp requires the Engineer’s permission and must take into account location of local residents and /or ecologically sensitive areas, including flood zones and slip/unstable zones. A site plan must be submitted to the Engineer for approval.

b) The construction camp may not be situated on a floodplain or on slopes greater than 1:3.

c) If the Contactor chooses to locate the campsite on private land, he must get prior written permission from both the Engineer and the landowner.

d) In most cases, on-site accommodation will not be required. The construction camp can thus be comprised of:

· Site office

· Ablution facilities 

· Designated first aid areas

· Eating areas 

· Staff lockers and showers (where water and waterborne are available)

· Storage areas 

· Batching plant (if required)

· Refueling areas (if required)

· Maintenance areas (if required)

· Crushers (if required)

e) Cut and fill must be avoided where possible during the set up of the construction camp.

f) The size of the construction camp should be minimized (especially where natural vegetation or grassland has had to be cleared for its construction).

g) Adequate parking must be provided for site staff and visitors.

h) The constructor must attend to drainage of the campsite to avoid standing water/or sheet erosion.

A.2.2 Ablutions 

a) Temporary chemical toilets must be provided by a company that has been approved by the Engineer. The toilets must be available for all site staff, both at the campsite, and on the site agreed by the Engineer. Toilets should be no closer than 50m from any of the two natural watercourses.

b) The construction of “long drop” toilets is forbidden.

c) Under no circumstances may open areas or the surrounding bush used as a toilet facility.

A.2.3 Provision for Camp Waste Disposal

a) Bins and / or skips shall be provided at convenient intervals for disposal of waste within the construction camp.

b) Bins should have liner bags for efficient control and safe disposal of waste.

c) Recycling and the provision of separate waste receptacles for different types of waste should be encouraged.


	E/ECO

E/ECO

E

E

E

E/ECO

E

ECO

ECO

ECO

Monitor 

ECO

ECO

ECO

ECO


	During surveys and preliminary investigations and prior to moving onto side.

During surveys and preliminary investigations. 

During surveys and preliminary investigations.

During site setup

During site setup.

During site setup.

During site setup.

On a weekly basis.

During site setup.

Ongoing

Frequency

Ongoing.

During site set-up and ongoing.

Ongoing.

During site set-up and ongoing.

	4A.3. Establishing Storage Access 

Storage areas can be hazardous, unsightly and can cause environmental pollution if not designed and managed carefully.
	A.3.1 General Substances and Materials

a) Choice of location for storage areas must take into account prevailing winds, distance to water bodies and general on-site topography.

b) Storage areas must be designated, demarcated and fenced if necessary.

c) Storage areas should be secure so as to minimize the risk of crime. They should also be safe from access by children/animal etc.

d) Fire prevention facilities must be present at all storage facilities.

e) If electrical equipment for substations is stored on site a firebreak will be around the storage area.

f)  Burning of fire breaks is to be carefully planned and managed with the assistance of the nearest Fire Department

A.3.2  Hazardous Substances and Materials

a)  Definition of hazardous substances/materials are those that are potentially: poisonous, flammable, carcinogenic or toxic.

b)  Some examples of hazardous substances/materials: 

· Diesel, petroleum oil, bituminous products 

· Cement 

· Solvent based paints 

· Lubricants 

· Explosives 

· Drilling fluids 

· Pesticides, herbicides 

· LPG

c)  Material Safety Data Sheets (MSDSs) shall be readily available on site for al chemicals and hazardous substances to be used on site. Where possible and available. MSDSs should additionally include information on ecological impacts and measures to minimize negative environment impacts during accidental release or escapes.

d)  Hazardous storage and refueling areas must be bunded with an impermeable liner to protect groundwater quality. The Contractor shall submit a method statement to the Engineer for approval.

e)  Fuel tanks must meet relevant specifications and be elevated so that leaks may be easily detected.

f)  Storage areas containing hazardous substances/ materials must be clearly signed.

g)  It is very important tha the proximity of houses, schools etc is taken into account when deciding on storage areas for hazardous substances.

h)  Residents living adjacent to the construction site must be notified of the existence of the hazardous storage area.

i)  Staff dealing with these materials/substances must be aware of their potential impacts and follow the appropriate safety measures.

j)  Contractors shall submit a method statement and plans for the storage of hazardous materials and emergency procedures.


	Monitor

ECO

ECO

ECO

ECO

N/A

N/A

E/ECO

Monitor

E/ECO

E

ECO

E

ECO

ECO

ECO
	Frequency

During site set-up.

During site set-up.

During site set-up.

During site set-up.

N/A

N/A

Ongoing

Frequency

During site set-up.

During site set-up.

During site set-up.

During surveys and preliminary investigations.

When moving onto site or as the relevant materials arrive onsite.

During staff induction and ongoing as necessary.

Prior to establishment of storage area.



	4A.4.  Materials Management Sourcing 

Materials must be sourced in a legal and sustainable way to prevent off-site environmental degradation.
	A.4.1  Sources of Materials

a) Contractors shall prepare a source statement indicating the sources of all material (including topsoil, sands, natural gravel, crushed stone, asphalt, clay liners etc), and submit these to the Engineer for approval prior to commencement of any work.

b)  Where possible, a signed document from the supplier of natural materials should be obtained confirming that they have been obtained in a sustainable manner and in compliance with relevant legislation.

c)  Where materials are borrowed  (mined), proof must be provided of authorization to utilize these material from the landowner /mineral rights owner and the Department of Mineral and Energy.
	Monitor

E/ECO

ECO

ECO


	Frequency

On award of contract

On receipt of natural materials.

On receipt of borrowed materials.

	4A.5  Education of Site Staff on General an Environmental Conduct 

These points need to be mde clear to all staff on site before the project begins.


	A.5.1  Environmental Education and Awareness

Ensure that all site personnel have a basic level of environmental awareness training. The Contractor must submit a proposal fro this training to the ECO for approval.  Topics covered include:

· What is meant by “environment”.

· Why the environment needs to be protected and conserved.

· How construction activities can impact on the environment.

· What can be done to mitigate against such impacts.

· Awareness of emergency and spills response provisions.

· Social responsibility during construction e.g. being considerate to local residents

It is the Contractor’s responsibility to provide the site foreman with no less than 1 hour’s environmental training and to ensure that the foreman has sufficient understanding to pass this information onto the construction staff. 

a)  Translators are to be used where necessary.

b)  The Engineer/ environmental control officer should be on hand to explain more difficult/ technical issues and to answer questions.

c)  The use of pictures and real-life examples is encouraged as these tend to be more easily remembered.

d) Use should be made of environmental awareness posters on site.

e)  Construction workers should be made aware that they are not to make excessive noise (e.g. Shouting / hooting) when site is near commercial residential areas.

f)  The need for a “clean site” policy also needs  to be explained to the construction workers.

A.5.2 Workers Conduct on Site
A general regard to the social and ecological well-being of the site and adjacent areas is expected of the site staff.  Workers need to be made aware of the following general rules:

a)  No alcohol/drugs to be present on site.

b)  No firearms allowed onsite or in vehicles transporting staff to/ from site, (unless used by security personnel).

c)  Prevent excessive noise.

d)  Prevent unsocial behaviour.

e)  Bringing pets onto the site is forbidden.

f)  No harvesting of firewood from the site or form the areas adjacent to it.

g) Construction staff are to make use of the facilities provided for them, as opposed to ad-hoc alternatives. (e.g. fires for cooking; the use of surroundings bush as a toilet facility are forbidden).

h)  Trespassing on private /commercial properties adjoining the site is forbidden.

i)  Driving under the influence of alcohol is prohibited.

j)  Other than pre-approved security staff, no workers shall be permitted to live on site.


	Monitor

ECO

ECO

ECO

ECO

ECO

ECO

ECO

ECO

ECO
	Frequency

During staff induction and ongoing.

Frequency

Prior to moving onto site.

Ongoing.

Ongoing.

Ongoing.

Ongoing.

During staff induction, followed by ongoing monitoring.

Induction, ongoing monitoring.

During staff induction, followed by ongoing monitoring.



	4A.6.  Dust/ AIR Pollution 

Establishment of the camp site, and related temporary works can reduce air quality 
	a)  Vehicles traveling along the access roads must adhere to speed limits to avoid creating excessive dust.

b)  Camp construction / haulage road construction – areas that have been stripped of vegetation must be dampened periodically to avoid excessive dust.

c)  The Contractor must make alternative arrangements (other than fires) for cooking and /or heating requirements. LPG gas cookers may be used provided that all safety regulations are followed.


	Monitor

ECO

ECO

E
	Frequency

Ongoing.

Ongoing- more frequently during dry and wind conditions.

Ongoing.

	4A.7.  Soil Erosion

The description of vegetation during preliminary activities on site greatly increases the risk of erosion.


	a)  The time that stripped areas are left open to exposure should be minimized wherever possible.  Care should be taken to ensure that lead times are not excessive.

b) Wind screening and stormwater control should be undertaken to prevent soil loss from the site.

c)  Procedures that are in place to conserve topsoil during the construction phase of the project are to be applied to the set up phase i.e. topsoil is to be conserved while providing access to the site and setting up the camp.


	Monitor 

E

E

ECO


	Frequency

During surveys and preliminary investigations.

During site set-up.

During site set-up.

	4A.8.  Stormwater 

Serious financial and environmental impacts can be caused by unmanaged stormwater 


	a)  To prevent stormwater damage, the increase on stormwater run-off resulting from construction activities must be estimated and the drainage system assessed accordingly.  A drainage plan must be submitted to the Engineer for approval and must include the location and design criteria of any temporary stream crossing (sitting and return period etc.)

b)  During site establishment, stormwater culverts and drains are to be located and covered with metal grids to prevent blockages if deemed necessary by the Engineer. (e.g. due to demolition work).


c)  Temporary cut off drains and berms may be required to capture stormwater and promote infiltration.


	E

E

ECO
	During surveys and preliminary investigations.

During site set-up.

During site set-up.

	4A.9.  Water Quality

Incorrect disposal of substances and materials and polluted run-off can have serious negative affects on groundwater quality.
	a) Storage areas that contain hazardous substances must be bunded with an approved impermeable liner.

b)  Spills in bunded areas must be cleaned up, removed and disposed of safely from the bunded area as soon after detection as possible to minimize pollution risk and reduced bunding capacity.

c)  A designated, bunded area is to be set aside for vehicles washing and maintenance. Materials caught in this bunded area must be disposed of to a suitable waste site or as directed by the Engineer.

d)  Provision should be made during site set up for all polluted run off to be treated to the Engineer’s approval before discharged into the stormwater system (This will be required for the duration of the project).
	Monitor

E

E/ECO

E/ECO

E/ECO
	Frequency

During site set-up.

During site set-up and as often as possible on an ongoing basis.

During site set-up.

During site set-up, to be monitored weekly.

	4A.10.  Conservation of the Natural Environment

The  wetland and Indigenous forest in the project area require particular attention


	A.10.1  Fauna and Flora 

a)  No indigenous vegetation/trees may be cleared/removed without prior permission from the ECO.

b)  The forest and wetland in the area need to be protected. The ECO must mark limits around the forest and wetland before the Contractor any work in the vicinity of the forest.

c) Care must be taken to avoid the introduction of alien plant species to the site and surrounding areas.  (Particular attention must be paid to imported material).

d)  Disturbance to birds, animals and reptiles and their habitats should be minimized wherever possible.

A.10.2  Sensitive Habitats

A thirty-meter buffer zone (or a suitable width) from the edges of the wetland should be determined by a wetland ecologist and demarcated by the contractor. No development activity is to occur within the buffer zone. Temporary bonnox type fencing should be used and should be moved in phases as the construction progresses from one area to the next.
	Monitor

N/A

E/ECO

ECO

E/ECO

N/A
	Frequency

N/A.

During site set-up.

Ongoing in campsite, haulage areas.

During surveys and preliminary investigations and ongoing.

N/A`.



	4A.11.  Set up of Waste Management Procedures 
	a) The excavation and use of rubbish pits on site is forbidden.

b) Burning of waste is forbidden.

c)  A fenced area must be allocated for waste sorting an disposal.

d) Individual skips for different types of waste (e.g. “household” type refuse, building rubble, etc) should be provided.
	ECO

ECO

ECO

ECO
	Ongoing.

Ongoing.

During site set-up.

During site set-up.



	4A.12. SOCIAL impacts – Visual & Noise

It is important to take notice of the needs and wishes of those living or working adjacent to the site. Failure to do say can cause disruption to work and increase costs in the form of delays.
	A.12.1  Public Participation

a)  During the set up phase of the project, the Contractor needs to make contact with those people that are Interested or Affected by the development (I&AP’s).

b)  These people will usually have been identified by the environmental consultant that was assigned to the project.  If this wasn’t the case, the I&AP’s can be identified as those who either:

· Live close to the site

· Work close by to the site

· Will have their services /infrastructure affected by the project 

· Have a general interest in the project

· The Councilor for the ward in which the construction is taking place

A.12.2.  Noise Impact 

a)  Construction vehicles are to be fitted with standard silencers prior to the beginning of construction.

b)  Equipment that is fitted with noise reduction facilities (e.g. Side flaps, silencers etc) will be sued as per operating instructions and maintained properly during site operations.

A.12.3  Visual Impacts 

a)  Storage facilities, elevated tanks and other temporary structures onsite should be located such that they have as little impact on local residents as possible.


b)  In areas where the visual environment is particularly important (e.g. along commercial/ tourism routes), the site may require screening in the form of shade cloth or other suitable materials prior to the beginning of construction.

c)  Special attention should given to the screening of highly reflective materials on site.


	Monitor

E

ECO

ECO

ECO

E/ECO

E/ECO

ECO
	Frequency

Prior to moving onto site.

Prior to moving onto site

Prior to moving onto site.

Ongoing.

During surveys and preliminary investigations and site set-up.

During surveys and preliminary investigations and site set-up.

During site set-up.

	4A.13.  Cultural Environment 
	Prior to the commencement of construction, all staff need to know what possible archaeological or historical objects of value may look like, and to notify the Engineer / Contractor should such an item be uncovered
	ECO
	During site set-up and ongoing.


	4A.14.  Security and Safety
	A.14.1  Fencing 

a)  Securing the site in order to reduce the opportunity of criminal activity in the locality of the construction site.

b)  The sites should be fenced and manned to control the access of people.  

c) Potential hazardous areas such as trenches are to be demarcated and clearly marked.

A.14.2  Lighting 

Lighting on site is to be set out to provide maximum security and to enable easier policing of the site, without creating a visual nuisance to local resident or businesses.

A.14.3  Risks Associated with Material on Site

a) Material stockpiles or stacks, such as, pipes must be stable and well secured to avoid collapse and possible injury to site/ local residents.

b) Flammable materials should be stored as far as possible from adjacent residents/b businesses.

c)  Fire fighting equipment should be present onsite at all times as per OHSA.

d)  Obstruction to drivers’ line of site due to stockpiles and stacked materials must be avoided, especially at intersections and sharp corners.

e)  No materials are to be stored in unstable or high risk areas such as in floodplains or on steep slopes.

f)  All I&AP’s should be notified in advance of any known potential risks associated with the construction site and the activities on it.

Examples of these are:

· Stinging of power lines 

· Blasting 

· Earthworks/earthmoving machinery on steep slopes above houses/infrastructure

· Risk to residences along haulage roads/ access routes
	Monitor

E

E

ECO

E/ECO

ECO

ECO

ECO

ECO

ECO

ECO


	Frequency

During site set-up.

During site set-up.

During site set-up.

During site set-up.

Ongoing.

Ongoing.

Ongoing.

Ongoing.

Ongoing.

24hrs prior to the activity in question


SECITON 4B: MANAGEMENT OF CONTRUCTION ACTIVITIES AND WORKFORCE

	4B.1.  Access to Site 
	B.1.1  Haulage Roads 

a)  Contactors shall ensure that all side an mitre drains and scour check walls on access and haul roads are functioning properly and are well maintained.

B.1.2  Maintenance of Access

a) Contractor should ensure that access roads are maintained in good condition by attending to potholes, corrugations and stormwater damage as soon as these develop.

b)  If necessary, staff must be employed to clean surfaced roads adjacent tot construction sites where materials have been split.

c)  Unnecessary compaction of soils by heavy vehicles must be avoided; construction vehicles must be restricted to demarcated access, haulage routes and turning areas.

d)  Cognisance of vehicles weight/ dimensions must be taken when using access constructed our of certain materials. E.g. paved surface/ cobbler entranceways.


	Monitor 

E

E

ECO

ECO

E
	Frequency 

Weekly and after heavy rains

Weekly inspection.

When necessary.

Ongoing.

Ongoing.

	4B.2.   Maintenance of Construction Camp
	B.2.1  Surfaces
a)  The Contractor must monitor and manage drainage of the camp site. To avoid soil erosion.

b) Run-off from the campsite must not discharge into neighbours’ properties.

B.2.2 Ablution

a) Chemical toilets are to be maintained in a clean state and should be moved to ensure that they adequately service the work areas.

b) The Contractor is to ensure that open areas or the surrounding bush are not being used as a toilet facility.

B.2.3 Camp Waste Disposal

a) The Contractor shall ensure that all litter is collected from the work and camp areas daily.

b) Bins and/or skips should be emptied regularly and waste should be disposed of at a registered landfill site.  Waybills for all such disposals are to be kept by the Contractor for review by the Engineer /ECO.

c) A registered chemical waste company is to be used to remove waste from chemical toilet on site.

B.2.4 Eating Areas 

a) Eating areas should be regularly serviced and cleaned to ensure the highest possible standards of hygiene and cleanliness.

b) All litter throughout the site should be picked up and placed in the bins provided.

B.2.5 Housekeeping 

a) The Contractor shall ensure that his camp and working areas are kept clean and tidy at all times 


	Monitor

E

E

ECO

ECO

ECO

ECO

ECO

Monitor

ECO

ECO

E/ECO


	Frequency

Ongoing.

Ongoing.

Weekly inspection.

Weekly inspection.

Ongoing.

Weekly.

Ongoing.

Frequency 

Daily 

Daily.

Weekly monitoring

	4B.3.  Staff Conduct 
	B.3.1 Environmental Education and Awareness

a) The Contractor must monitor the performance of construction workers to ensure that the points relayed during their induction have been properly understood and are being followed.  If necessary, the ECO and /or a translator should be called to the site to further explain aspects of environmental or social behaviour that are unclear.

B.3.2 Worker Conduct on Site

a) The rules explained in the worker conduct section (see section A.5.2 of this EMP), must be followed at all times.


	Monitor

E/ECO

ECO
	Frequency

Ongoing monitoring. 

Ongoing.

	4B.4.   Dust/ Air Pollution

Main causes of air pollution are dust from vehicle movements and stockpiles, vehicle emissions and fires
	a) Vehicles traveling to and from the construction site must adhere to speed limits so as to avoid producing excessive dust.

b) A speed limit of 30km/hr must be adhered to on all dirt roads.

c) Access and other cleared surfaces must be dampened whenever possible and especially in dry and windy conditions to avoid excessive dust.

d) Where dust is unavoidable in residential or commercial areas, screening will be required utilizing wooden supports and shade cloth.

e) Vehicles and machinery are to be kept in good working order and to, meet manufactured specification fro safety, fuel consumption etc.

f) Should excessive emissions be observed, the Contractor is to have the equipments seen to as soon as possible.

g) No fires are allowed on site except for burning of firebreak.

h) Stockpiles may cause dust and so must be managed in by the guidelines in Materials Management in section B.9.1
	Monitor

E

E

E

E

ECO

E

E

E


	Frequency

Ongoing.

Ongoing.

Ongoing.

As directed by Engineer.

Ongoing.

As directed by the Engineer.

Ongoing 

Ongoing.



	4B. 5 Soil Erosion 
	B.5.1 Topsoil Stripping and Stockpiling
Once an area has been cleared of vegetation, the top layer (nominally 150mm) of soil should be removed and stockpiled in a designated area.

B.5.2 Exposed Surfaces 

The full length of the works shall not be stripped of vegetation prior to commencing other activities.  The time that stripped areas are exposed shall be minimized wherever possible.

a) Top-soiling and revegetation shall commence immediately after the completion of an activity and at an agreed distance behind any particular work front.

b) Stormwater control (See B6) and wind screening should be undertaken to prevent soil loss from the site.

c) Side tipping of spoil and excavated materials shall not be permitted – all spoil material shall be disposed of as directed by the Engineer.

d) Battering of all banks shall be such that cut and fill embankments are no steeper than previous natural slopes unless otherwise permitted by the Engineer. Cut and fill embankments steeper than previous ground levels shall be re-vegetated immediately on completion of trimming or shall be protected against erosion using bioengineered stabilization measures.   Deep-rooted vegetation such as Vetiver grass is effective to stabilize steeper embankments,


	Monitor

ECO

E/ECO

ECO

E

E

ECO
	Frequency

Ongoing.

Ongoing.

As each activity is completed.

Ongoing.

Ongoing.

As the cut and fill activity is completed.

	
	e) All embankments, unless otherwise directed by the Engineer, shall be protected by an off drain to prevent from cascading down the face the embankment and causing erosion.


	Monitor

E
	Frequency

Immediately after the creating of the embankment/ stripping of vegetation.




	4B.6.   Stormwater 

Measures in this section are aimed at reducing the erosive potential of stormwater 
	B.6.1 General Principles: 

a) The Contractor shall not in any way modify nor damage the banks or bed of streams, rivers, wetlands, other open water bodies and drainage lines adjacent to or within the designated area, unless required as pert of the construction project specification. Where such disturbance is unavoidable, modification of water bodies should be kept to a minimum in terms of:

· Removal of riparian vegetation

· Opening up of the stream channel

b) Earth, stone and rubble is to be properly disposed of so as not to obstruct natural water pathways over the site. i.e.: these materials must not be placed in stormwater channels, drainage lines or rivers.

c) There should be a periodic checking of the site’s drainage system to ensure that the water flow is unobstructed.

d) The use of high velocity stormwater pipelines should be avoided in favor of open, high friction, semi-permeable channels wherever feasible 

e) A number of smaller stormwater outfall points should be constructed rather than a few large outfall points.

f) Stormwater outfalls should be designed to reduce flow velocity and avoid stream-bank and soil erosion. 
	Monitor

ECO

E

E/ECO

E/ECO

E/ECO

E/ECO
	Frequency

Ongoing.

Monitoring throughout the duration of the project.

Monthly checking

As directed by Engineer

As directed by Engineer



	
	B.6.2 Stormwater Detention Ponds
a) Detention ponds should be vegetated either with wetland vegetation or grass from the Revegetation Specification.  The detention ponds must not block the water flow, but should encourage spreading of the flow over wider areas to reduce velocity and encouraged infiltration.

b) Peak stormwater discharge from the site/area should not be increased with development of the site/area. Stormwater should be detained on site through the use of stormwater detention ponds wherever possible. A series of detention ponds may be required where flow volumes are high.

B6.3  Unchanneled Flow

a) During construction unchanneled flow must be controlled to avoid erosion. Where large areas of soil are left exposed, rows of straw/hay or bundles of cut vegetation should be dug into the soil in contours to slow surface wash and capture eroded soil. The spacing between rows will be dependant on slope.

b) Where surface run-off is contracted (e.g. along exposed roadways/tracks), flow should be slowed by contouring with hay bales or bundled vegetation generated during site clearance operation. If the area must be used for construction vehicles, berms may be used instead.   The berms must at least 30cm high and well compacted. The berms should channel concentrated flow into detention ponds or areas protected with hay bales for flow reduction and sediments capture.


	Monitor 

ECO

E/ECO

E/ECO

Monitor

E/ECO


	Frequency

On completion of detention ponds

As directed by Engineer and ongoing monitoring

As surfaces become exposed 

Frequency

Ongoing

	4B.7. Water  

Quality 

Soil erosion and sediment is detrimental to water quality. Mismanagement of polluted run-off from vehicle and plant washing and wind dispersal of dry materials into rivers and watercourses are detrimental to water quality.
	a) Mixing /decanting of all chemicals and hazardous substances must take place either on a tray or on an impermeable surface. Waste fro these should then be disposed of to a suitable waste site.

b) Every effort should be made to ensure that any chemicals or hazardous substances do not contaminate the soil or ground water on site.

c) Care must be taken to ensure that run-off from vehicle or plant washing does not enter the groundwater. Wash water must be passed through a three-chamber SOG trap prior to being discharged as effluent to a regular municipal sewer.

d) Site staff not be permitted to use any stream, river, other open water body or natural water source adjacent to or within the designated site for the construction or related activities. Municipal water (or another source approved by the Engineer) should instead be used for all activities such as washing of equipment or disposal of any type of waste, dust suppression, concrete mixing, compacting etc.

e) Emergency contact numbers in should be listed and openly displayed in order to speedily deal with spillages and contamination of aquatic environments should it occur.


	Monitor 

ECO

ECO

ECO

ECO

E/ECO
	Frequency

Regular monitoring.

Regular monitoring.

Regular monitoring 

Regular monitoring.

As the need arises

	4B.8.  Conservation of Natural Environment

The patch of forests specifically identified in the EMP should be avoided altogether. The buffer needs to be upheld at all cost.


	B.8.1 Fauna and Flora 

As the work front progresses the Contractor is to check that any vegetation clearing has the prior permission of the ECO.

a) Only trees that have NOT been marked beforehand are to be removed.

b) Gathering of firewood, fruit, medicinal plants, crops, or any other natural material on site or in areas adjacent to the site is prohibited.

c) The hunting of birds and animals on site and in surrounding areas is forbidden.

d) Snares and traps on site and in surrounding areas are forbidden.

e) Immediate revegetation of stripped areas and removal of aliens by weeding must take place.  This significantly reduces the amount of time and money that must be spent on alien plant management during rehabilitation.

f) Alien vegetation encroachment onto the site as a result of construction activities must be controlled during construction.


	Monitor

E

N/A

ECO

ECO

ECO

ECO

ECO


	Frequency

Ongoing.

N/A

Ongoing.

Ongoing.

Ongoing

Ongoing.

Twice – monthly monitoring.



	
	g) Where possible, cleared indigenous vegetation should be kept in a nursery for use at a later stage in the rehabilitation process.


	Monitor 

N/A
	Frequency

N/A

	4B.9.  Materials Management
	B.9.1 Stockpile Management 

a) Stockpiles should not be situated such that they obstruct natural water pathways.

b) Stockpiles should not exceed 2m in height unless otherwise permitted by the Engineer.

c) If stockpiles are exposed to windy conditions or heavy rain, they should be covered either by vegetation or cloth, depending on the duration of the project. Stockpiles may further be protected by the construction of berms or low brick walls around their bases.

d) Stockpiles should be kept clear of weeds and alien vegetation growth by regular weeding.

9.2 Handling of Hazardous Materials

a) All concrete mixing must take place on a designated, impermeable surface.

b) No vehicles transporting concrete to the site may be washed on site.

c) No vehicles transporting, placing or compacting asphalt or any other bituminous product may be washed on site.

d) Lime and other powders must not be mixed during excessively windy conditions.

e) All substances required for vehicle maintenance and repair must be in sealed containers until they can be disposed or /removed from the site.

f) Hazardous substances / material are to be transported in sealed containers or bags.

g) Spraying of herbicides/ pesticides should not take place under windy conditions and must comply with OHSA specs and other chemical handling laws

h) The emergency numbers should be consulted should any accident /spillages of hazardous substances and /or materials take place.  The Contractor is to outline a method statement for the dealing of accidents /spillages of hazardous materials.  This statement must be handed to the Engineer as well as to DWAF should the incident occur near to a body of water.


	Monitor

E/ECO

E

ECO

ECO

ECO

ECO

ECO

ECO

ECO

E/ECO

ECO

ECO
	Frequency

Location as directed by the Engineer.

As this becomes necessary.

Monthly monitoring

Ongoing monitoring.

Ongoing monitoring.

Monthly 

Ongoing monitoring.

Ongoing monitoring.

Ongoing monitoring

Ongoing monitoring

	4B.10.  Waste Management 

Definition: “Refuse” refers to all construction waste (such as rubble, asphalt milling, cement, bags, waste cement, timber, cans, other containers, wire and nails) household and office waste
	B.10.1 On-Site Waste Management
a) Refuse must be placed in the designated skips/ bins, which must be regularly emptied. These should remain within demarcated areas and should be designed to prevent reuse from being blown out by wind.

b) In addition to the waste facilities within the construction camp, provision must be made for waste receptacles to be placed at intervals along the work front.

c) Littering on site is forbidden and the site shall be cleared of litter at the end of each working day.

d) Recycling is to be encouraged by providing separate receptacles for different types of waste and making sure that staff are of their uses.

10.2 Waste disposal

Non-hazardous Waste 

All waste must be removed from the site and transported to a landfill site which must be identified prior to commencement of work.

a) Waybills proving disposal at each shall be provided fro the Engineer’s inspection.

b) Construction rubble shall be disposed off in pre-agreed, demarcated spoil dumps that have been approved by the Engineer, or at disposal sites.

c) Waste from chemical toilets should be disposed of regularly and in a responsible and in a responsible manner by a registered waste contractor.  Care must be taken to avoid contamination of soils and water, pollution and nuisance to adjoining areas.

Hazardous Waste 

a) Hazardous waste disposal must be carried out by an approved waste Contractor.  Waybills for this should be provided.

b) A sump (earth or other) must be created for concrete waste. This is to be de-slugged regularly and the cement waste is to be removed to a tip site as approved by the engineer and ECO.


	Monitor

ECO

ECO

ECO

ECO

ECO

E/ECO

ECO

ECO

E/ECO

ECO
	Frequency

Ongoing monitoring 

Ongoing monitoring

Ongoing monitoring 

Ongoing monitoring.

Checked at each site meeting.

Ongoing monitoring

Monitored weekly and at the start of builders’ holidays.

Ongoing

During establishment and ongoing 

Ongoing

	4B.11.   Social Impacts 

Regular communication between the Contractor and Interested and Affected Parties  (I&AP’s) is important for the duration of the contract
	B.11.1 Disruption of Infrastructure and Services

a) Contractor’s activities and movement of staff to be restricted to designated construction areas.

b) Should the construction staff be approached by members of the public or other stakeholders, they should assist them in locating the Engineer or Contractor, or provide a number on which they may contact the Engineer or Contractor.

c) The conduct of the construction staff when dealing with the public or other stakeholder shall be in a manner that is polite and courteous at all times. Failure to adhere to this requirement may result in the removal of staff from site by the Engineer.

d) Disruption of access for local residents must be minimized and must have the Engineer’s permission.

e) The Contractor is to inform neighbours in writing of disruptive activities at least 24 hours beforehand. This can take place by way of leaflets placed in the postboxes giving the Engineer and Contractor’s details or other methods approved by the Engineer.

B.11.2   Visual Impacts 

a) Lighting on the construction site should be pointed downwards and away form oncoming traffic and nearby houses.

b) The site must be kept clean to minimize the visual impact of the site

c) If screening is being used, this must be moved and re-erected as the work front progresses.

B.11.3 Noise

a) Machinery and vehicles are to be kept in good working order for the duration of the project to minimize noise nuisance to neighbours.

b) Notice of particularly noisy activities must be given to residents/ businesses adjacent to the construction site.

Example of these include:

· Noise generated by jackhammers 

· Blasting 

· Drilling 

· Dewatering pumps

c) Noisy activities must be restricted to the times given in the Project Specification or General Conditions of Contract.


	Monitor 

E

E/ECO

E

E

E/ECO

ECO

ECO

ECO

ECO

E/ECO

E/ECO
	Frequency 

Ongoing.

Ongoing.

Ongoing.

Ongoing.

At least 24 hrs prior to the activity taking place.

Ongoing.

Ongoing- weekly monitoring.

Ongoing.

Ongoing.

At least 24 hrs prior to the activity taking place.

	
	B.11.4 Communication with Interested and Affected Parties (I&AP’s)

a) The Engineer and Contractor are responsible for ongoing communication with those people that are interested in /affected by the project.

b) A complaint register should be housed at the site office. This should be in carbon copy format, with numbered pages. The Contractor must account for any missing pages. This register is to be tabled during monthly site meetings.

c)  I&AP’s need to be made aware of the existence of the complaints book and the methods of communication available to them.

d) Queries and complaints are to be handled by:

· Documenting details of such communications

· Submitting these for inclusion in complaints register.

· Brining issues to Engineer’s attention immediately

· Taking remedial action as per Engineer’s instruction

e) Selected staff are to be made available for formal consultation with I&AP’s in order to:

· Explain construction process

· Answer questions
	Monitor 

E/ECO

ECO

E/ECO


ECO

ECO


	Frequency

Monthly

Monthly

Ongoing.

Ongoing 

Ongoing on a monthly basis and when required

	4B12.  Cultural Environment 
	a) Possible items of historical or archaeological value include old stone foundations, tools, clayware, jewellery, remains, fossils etc.

b) Should something of this nature be uncovered, the Research and Professional Services Division of AMAFA should be contacted and work should be stopped immediately. AMAFA’s head office is in Ulundi and their office in Pietermaritzburg will address any queries within KZN.

The facilitator should be contacted on telephone no. 033-3946543, fax 033-3426097.


	E/ECO
	As required.


SECTION 4C: POST CONSTRUCTION ACTIVITIES

	4C.1.  Construction Camp 
	a) All structures comprising the construction camp are to be removed from site.

b) The area that previously housed the construction camp is to be checked for spills o f substances such as oil, paint etc. and these should be cleaned up.

c) All hardened surfaces within the construction camp area should be ripped, all imported material removed, and the area shall be top-soiled as regressed using the guidelines set out in the revegetation specification that form part of this document.

d) The Contractor must arrange the cancellation of all temporary services.
	Monitor

E

E

E

E
	Frequency

Project completion

Project completion

Project completion

Project completion

	4C.2 Vegetation
	a) All areas that have bee disturbed by construction activities (including the construction camp area) must be cleared of alien vegetation.

b) Open areas are to be re-planted 

c) All vegetation that has been cleared during construction is to be removed from site or used as much as per the revegetation specification, (except for seeding alien vegetation).

d) The Contractor is to water and maintain all planted vegetation until the end of the defects liability period and is to submit a method statement regarding this to the Engineer.
	E

E

E

E
	Project completion

Project completion 

Project completion

Project completion



	4C.3 Land Rehabilitation
	a) All surfaces hardened due to construction activities are to be ripped and imported materials thereon removed.

b) All rubble is to be removed from the site to and approved disposal site or approved by the Engineer.  Burying of rubble onsite is prohibited.

c) The site is to be cleared of all litter.

d) Surfaces are to be checked for waste products form activities such as concreting or asphalting and cleared in a manner approved by the Engineer.

e) All embankments are to be trimmed, shaped and replanted to the satisfaction of the Engineer.

f) Borrow pits are to be closed and rehabilitated in accordance with the DME-approved management plan for each borrow pit. The Contractor shall liaise with the Engineer regarding these requirements.

g) The Contractor is to check that all watercourses are fee from building rubble, spoil materials and waste materials.
	ECO

ECO

ECO

ECO

E/ECO

E

ECO
	Project completion 

Project completion

Project completion

Project completion

Project completion

Project completion

Project completion.

	4C.4 Material and Infrastructure

	a) Fences, barriers and demarcations associated with the construction phase are to be removed form the site unless stipulated otherwise by the Engineer.

b) All residual stockpiles must be removed to spoil or spread onsite as directed by the Engineer.

c) All leftover building materials must be returned to spoil or spread on site as directed by the Engineer.

d) The Contractor must repair any damage that the construction works has caused to neighbouring properties.


	Monitor

E

E

ECO

E


	Frequency

Project completion

Project completion

Project completion

Project completion

	4C.5 General 


	a) The Engineer, ECO and the Contractor need to approve all remediation activities and to ensure that the site has been restored to a condition approved by the Engineer.

b) Temporary roads must be closed and access across these blocked.

c) Access or haulage roads that were built across watercourses must be rehabilitated by removing temporary bridges and any other materials placed in / or near to watercourses.  Revegetation of banks or streambeds must be as necessary to stabilize these and must be approved by the Engineer.

d) All areas where temporary services were installed are to be rehabilitated to the satisfaction of the Engineer.


	E/ECO

E/ECO

E/ECO

E/ECO


	On completion of the construction & maintenance phases

On completion of construction

On completion of construction 

On completion of construction




SECTION 5. CONCLUSIONS AND RECOMMENDATIONS

The sensitive environment along the pipe line route is the patch of indigenous forest located at the start area of the project. This forest need to be avoided by all means. Other construction impacts are minimal and of low significance. Should the EMP be adequately implemented, potential impacts could be further reduced. The concluding recommendations are:

· Contractors need to follow the environmental management plan;

· The development need to benefit the community in a tangible manner, and therefore, attempts need to be made to integrate community needs and aspirations into the implementation processes of the development;

· The contractor need to show concerns for health in general and the health safety of the employees in particular;

· Where appropriate, the contractor must use local labour as much as possible; 

· In terms of the National Environmental Management Act 107 of 1989 every body is required to take reasonable measures to ensure that they do not pollute the environment. Reasonable measures include informing and educating employees about the environmental risks of their work and training them to operate in an environmentally acceptable manner;

· Furthermore in terms of the Nation Environmental Management Act 107 of 1998 the cost of repair for any environmental damage shall be borne by the person responsible for the damage.

	PART C3

ENGINEER’S QUALITY MANAGEMENT SPECIFICATION


1. INTRODUCTION

ZIYANDA Consulting cc subscribes to a Quality Management System accredited by a number of certification bodies including ISO 9001.

This document/specification summarises the Quality Control Procedures used by ZIYANDA Consulting in the Quality Assurance and Control on site works. These procedures are to be used by Engineer’s Representative Staff (i.e. ER and his assistants) and the Contractor’s staff on the following commonly encountered sites;

· Pipelines

· UPVC Pipelines

· Steel Pipelines

· Reservoirs

· Building Works

· Roadworks

The procedures have been developed as “intellectual” property of ZIYANDA Consulting and may only be used on sites managed by ZIYANDA Consulting. Any other use is subject to consent/agreement with ZIYANDA Consulting. 

All references to approval by ER require that the Contractor (via the Site Agent) initiates the necessary request for approval). In addition the Contractor will be required to maintain a copy of all records as required by this Specification. 

The application of the procedures will be agreed as appropriate between the Contractor’s Site Agent and the Engineer (or his Representative) at the commencement of construction activities,.

It will be deemed that the Contractor has incorporated in his completion period and pricing, the necessary requirements to comply with this Specification fully.

1.1
Elements of Site Quality Assurance

The elements of Site Quality Assurance comprise the following:

· general elements that apply to all sites and 

· site specific elements that are specific to sites and may be dependent on the type of construction. 

2. GENERAL ELEMENTS APPLICABLE TO ALL SITES

2.1
Construction Quality Control Organization

This section presents the requirements of key site personnel involved on construction sites, i.e. Engineer’s Representative (ER) staff and Contractor’s staff. The following quality assurance procedures for site quality assurance personnel should be followed:

Engineer’s Quality Assurance Personnel

The following ER staff appointments’ procedure should be followed to ensure the right superintendence on contracts:

	Item
	Activity
	Remarks
	Responsible Party
	Approval by

	1
	Appointment of Engineer for contracts
	Stated in contract data
	Engineer
	Employer

	2
	Supervision staffing arrangements
	Proposed prior to construction work
	Engineer
	Employer

	3
	Site staff 
	Proposal for site personnel including CV’s
	Engineer
	Employer

	4
	Roles
	Delegation of powers by Engineer
	Engineer
	Engineer


The site staff will comprise the Engineer’s Representative (ER) and ER’s assistants (Field Officers):

(a) Engineer’s Representative (ER)

The ER is the primary point of contact for the Engineer on all construction management issues. The ER will monitor and approve each contractor’s quality submittal to ensure that the project is meeting the specifications and requirements. The ER will manage the implementation of the CQAP at the project sites with assistance from Field Officers appointed by the Engineer. 

(b) ER Assistants/Field Officers (FO’s)

Field Officers (FOs) are responsible to the ER and support the ER’s management of the CQAP. The FOs will monitor the day-to-day activities of the contractor. This includes ensuring that contractors comply with the drawings and specifications, applicable SABS standards, good workmanship, and the CQC requirements. As part of this effort, FOs will:

· conduct independent inspections to verify the quality of the work;

· participate in contractor inspections;

· review test and inspection reports; and

· ensure that the required documentation is submitted.

The FOs will be alert to detect, record, and report any deviation from the contract documents, including calling any deficient item to the attention of the ER and the contractors’ Site Agents. The FOs will keep accurate and detailed records of the contractor’s performance and progress, delivery of materials, and other pertinent matters, including the daily inspection report. 

2.2
Contractor’s Quality Assurance Personnel

The contractors are responsible for the quality control of their constructed work product as well as the necessary inspections and tests required to ensure that their work complies with the contract documents. 

2.2.1
Contractor’s  Site Staff

The contractors’ Site Agents are the primary point of contact for the Contractors on all construction management issues. The Site Agents must be full-time on site for the contractors. The Site Agents must have full authority to institute any and all actions necessary for the successful implementation of the CQC program to ensure compliance with the drawings and technical specifications. 

The following procedures apply with respect to appointment of the contractor’s key personnel:

	Aspect
	Remarks
	Approval By
	When

	Appointment of Site Agent
	As per tender for quality based evaluated tenders
	Engineer
	Prior to commencement of construction

	Appointment of Site Forepersons
	As per tender for quality based evaluated tenders
	Engineer
	Prior to commencement of construction


2.3
Site Establishment

The Engineer’s Representative shall inspect and approve/disapprove contractor’s site establishment using Quality Procedure Form QC 01.

2.4
General

For all projects the ER must undertake the following general items as appropriate:

	1
	Confirm “Permission to Occupy” has been received from the relevant authority.

	2
	“Handover of Site” to Contractor to be confirmed in writing.

	3
	Inspect and approve Site Establishment (Form QC 01).

	4
	Setup Site Files/Filing System. 

	5
	Ensure a copy of the Contract Document is retained on Site by the Contractor.

	6
	Ensure a full set/s of approved drawings is/are retained on Site by the Contractor.

	7
	Maintain a Drawing Register.

	8
	Ensure a copy of the latest Contract Program is clearly displayed on Site.

	9
	Establish Quality Assurance Procedures and carry out inspections as and when required.

	10
	Issue Site Instructions as and when required.

	11
	Ensure Safety File, including Dept. of Labour notification, is up to date and on Site and all relevant regulations, including issuing of PPE, are strictly adhered to.

	12
	Ensure all relevant information is recorded in a daily Site Diary and counter signed.

	13
	Hold regular Work Meetings with the Contractor.

	14
	Hold regular Site Meetings with the Client, Professional Team and the Contractor. 

	15
	Maintain a copy of the Environmental Record of Decision on Site


3. SITE SPECIFIC QUALITY ASSURANCE PROCEDURES

Quality assurance inspections and testing will be used to verify the adequacy and effectiveness of the contractor’s quality control program. The Engineer’s Quality Assurance Personnel detailed above will provide inspection and supervision within the scope of work, which includes monitoring of the following construction activities:

· Manufacture of materials

· Transporting and off-loading and storage of construction materials

· Inspection of construction activities, including:

· Pipework

· Steel

· uPVC

· Reinforced Concrete Reservoirs

· Building Works

· Pump stations (mechanical & electrical installations)

· Roadworks

The Contractor will be required to formally request for inspection for any activity which he deems to be complete before proceeding to the next stage of the whole operation. Formal requests must be filled in the  relevant QC Form. 

Contractor Deficiency Correction

When material, performed work or installation is found to be deficient and/or does not meet the project specifications, the Engineer’s QA personnel will assure deficiency correction is implemented. In addition to results of an inspection being recorded on the relevant QC Form, in the event of inspection failure, the Engineer’s QA personnel will fill in Form QC 008 “Failure Report”, to record the deficiencies. A copy of this report will be handed over to the Contractor’s Site Agent. The Contractor will implement corrective actions to remedy work that is not in accordance with the drawings and specifications. The corrective actions will include removal and replacement of deficient work using methods approved by the ER. Removal must be done in a manner that does not disturb work that meets QC/QA criteria; otherwise, the disturbed material must also be removed and replaced. Replacement must be done in accordance with the corresponding technical specifications. Replacement will be subjected to the same scope of QC/QA inspection and testing as the original work. If the replacement work is not in accordance with the drawings and specifications, the replacement work will be removed, replaced, re inspected and re-tested.

Activities which specifically require approval before the next stage can proceed are as detailed in this section. 

3.1
Pipework

The following procedures will be used for pipework quality assurance:

3.1.1
uPVC Pipework

The ER is responsible for ensuring the following quality assurance procedure is followed, as a minimum:

	1
	Inspect & Approve Setting Out (Form QC 001).

	2
	Inspect & Approve Pipeline Trenches (Form QC 002).

	3
	Inspect & Approve Pipeline Bedding (Form QC 003).

	4
	Inspect & Approve Pipe Installation – PVC (Form QC 004B).

	5
	Inspect & Approve Pipeline Pressure Testing (Form QC 006).

	6
	Inspect & Approve Backfilling to Trenches (Form QC 007).


Copies of the ZIYANDA Consulting’s forms are available for inspection at the offices of ZIYANDA Consulting cc. 

3.1.2 Steel Pipework

The ER is responsible for ensuring the following quality assurance procedure is followed, as a minimum:

	1
	Inspect & Approve Setting Out (Form QC 001).

	2
	Inspect & Approve Pipeline Trenches (Form QC 002).

	3
	Inspect & Approve Pipeline Bedding (Form QC 003).

	4
	Inspect & Approve Pipe Installation – Steel (Form QC 004A).

	5
	Inspect & Approve Welding of Pipes (Form QC 005).

	6
	Inspect & Approve Pipeline Pressure Testing (Form QC 006).

	7
	Inspect & Approve Backfilling to Trenches (Form QC 007).


Copies of the ZIYANDA Consulting’s forms are available for inspection at the offices of ZIYANDA Consulting cc. 

3.2
Reinforced Concrete Works

The ER is responsible for ensuring the following quality assurance procedure is followed, as a minimum:

	1
	Inspect & Approve Setting Out (Form QC 001).

	2
	Inspect & Approve Excavations (Form QC 008).

	3
	Inspect & Approve Backfilling to Excavations (Form QC 009).

	4
	Inspect & Approve Excavations prior to Blinding (Form QC 010).

	5
	Inspect & Approve Cast Concrete (Form QC 016).

	6
	Inspect & Approve Structure prior to Concreting (Form QC 015).

	7
	Inspect & Approve Cast Concrete (Form QC 016).

	8
	Inspect & Approve Backfilling to Excavations (Form QC 009).


Copies of the ZIYANDA Consulting’s forms are available for inspection at the offices of ZIYANDA Consulting cc. 

3.3
Building Works

The ER is responsible for ensuring the following quality assurance procedure is followed, as a minimum:

	1
	Inspect & Approve Setting Out (Form QC 001).

	2
	Inspect & Approve Excavations (Form QC 008).

	3
	Inspect & Approve Backfilling to Excavations (Form QC 009).

	4
	Inspect & Approve Excavations prior to Blinding (Form QC 010).

	5
	Inspect & Approve Cast Concrete (Form QC 016).

	6
	Inspect & Approve Foundations prior to Concreting (Form QC 011).

	7
	Inspect & Approve Cast Concrete (Form QC 016).

	8
	Inspect & Approve Sub Structure Brickwork (Form QC 012).

	9
	Inspect & Approve Foundations prior to Surface Bed Concreting (Form QC 013).

	10
	Inspect & Approve Cast Concrete (Form QC 016).

	11
	Inspect & Approve Superstructure Brickwork (Form QC 014).

	12
	Ensure relevant Certificates are received/issued for the roof structure.


Copies of the ZIYANDA Consulting’s forms are available for inspection at the offices of ZIYANDA Consulting cc. 

3.4
Roadworks

The ER is responsible for ensuring the following quality assurance procedure is followed, as a minimum:

	1
	Inspect & Approve Setting Out (Form QC 001).

	2
	Inspect & Approve Excavations (Form QC 008).

	3
	Inspect & Approve Backfilling to Excavations (Form QC 009).

	4
	Inspect & Approve Excavations prior to Blinding (Form QC 010).

	5
	Inspect & Approve Earthworks (Form QC 017).

	6
	Inspect & Approve Subgrade Construction (Form QC 018).

	7
	Inspect & Approve Pavement Layerworks/Subbase (Form QC 019).

	8
	Inspect & Approve Base Construction (Form QC 020).

	9
	Inspect & Approve Culvert Construction (Form QC 021).

	10
	Inspect & Approve Headwalls and Wi8ng Walls (Form QC 022).

	11
	Inspect & Approve Subsoil Drainage (Form QC 023).

	12
	Record Site Measurement (Form QC 025)


Copies of the ZIYANDA Consulting’s forms are available for inspection at the offices of ZIYANDA Consulting cc. 

4
DOCUMENTATION

4.1
Overview

An effective CQA Plan depends largely on recognition of all construction activities that should be monitored and on assigning responsibilities for the monitoring of each activity. This is most effectively accomplished and verified by the documentation of quality assurance activities. The ER will document that quality assurance requirements have been addressed and satisfied. The ER will provide the Engineer with signed descriptive remarks, data sheets, and inspection reports to verify that monitoring activities have been carried out. The ER will also maintain, at the job site, a complete file of Drawings and Technical Specifications, a CQA Plan, test procedures, daily diaries, and other pertinent documents.

4.2
Daily Site Diary

A daily construction site diary will be prepared and signed by each Site Agent and the ER. The diary will include a summary of the contractor’s daily construction activities. At a minimum, the daily construction diary will include the following information:

· Date, project name, location, and other identification

· Description of weather conditions, including temperature, cloud cover, and rainfall

· Reports on any meetings held and their results

· Record of visitors to site

· Locations of construction underway during that day

· Equipment and personnel working in each activity, including subcontractors

· Descriptions of work being inspected

· Decisions made regarding approval of units of material or of work, and corrective actions to be taken

· Description of problems or delays and resolution

· Communications with contractor staff

· Construction activities completed and/or in progress

· Signature of the diary preparer

The daily site diary will be routed on a daily basis to the project QC/QA files and will be maintained as part of the permanent project record. 

4.3
Control of Quality Records

The ER verifies QA record accuracy and maintains copies of all quality-related documentation. This includes, but may not be limited to:

· Daily construction QA records;

· Inspection reports;

· Non-conformance (Failure) reports;

· Material receiving reports; and

· Monitoring and test data.

These records will be stored in files maintained in the project document control files. All original documents pertaining to QC information will be maintained in the project file located at the site. All records shall be available for inspection and audit, at any time, by the Engineer and the Employer. 

PROJECT SPECIFIC OCCUPATIONAL HEALTH AND SAFETY SPECIFICATION 

FOR

COVID-19 SITE CONDITIONS

KEY ROLE PLAYERS

	EMPLOYER


	

	Principal Agent:


	

	Civil Engineer


	

	Environmental Control Officer


	

	Health and Safety Agent


	

	PRINCIPAL CONTRACTOR


	

	Contracts Manager


	

	Site Agent


	

	H&S Officer


	

	Other:
	

	
	


TABLE OF CONTENTS

1271.
LIST OF ABBREVIATIONS


1292.
DEFINITIONS


1303.
KEY REFERENCES


1314.
INTRODUCTION


1314.1
PURPOSE


1314.2
IMPLEMENTATION OF THE PROJECT SPECIFIC COVID-19 OCCUPATIONAL HEALTH AND SAFETY SPECIFICATIONS


1314.2.1
Roles And Responsibilities of Health and Safety Officers


1335.
BASELINE RISK ASSESSMENT


1335.1
SUMMARY OF RISKS IDENTIFIED DURING DESIGN AND IMPLEMENTATION


1346.
SITE SPECIFIC HEALTH AND SAFETY PROCEDURES


1346.1
DEMOGRAPHICS


1346.1.1
Age of Employee


1346.1.2
Health status


1346.1.3
Socio economic status / Unskilled labour


1346.1.4
Accommodation


1356.2
ORIGIN OF LABOUR AND TRANSPORTATION


1356.2.1
Public Transportation across borders/towns/cities


1356.2.2
Contractor provided transportation across borders/towns/cities


1366.3
SOCIAL DISTANCING


1366.3.1
Tasks that require more than 1 person to complete


1366.3.2
Access/Egress of Site, Welfare Facilities, Meeting Areas


1376.4
ALCOHOL AND DRUG TESTING


1376.5
MEDICAL SURVEILLANCE


1386.6
ABLUTION FACILITIES


1386.7
SECURITY ACCESS


1386.7.1
Staggered access to site;


1396.8
PROCUREMENT AND STORAGE FOR COVID-19 PPE AND GENERAL SUPPLIES


1396.9
WASTE MANAGEMENT FOR COVID-19 WASTE


1396.9.1
Disposal of any gloves, masks


1406.9.2
Paper towels


1406.9.3
Disinfectant solution


1406.9.4
Wastewater


1406.10
SIGNAGE


1406.10.1
Access rules


1406.10.2
Notices/Posters with protocols


1416.11
EMERGENCY PLANNING


1416.11.1
First aid


1416.11.2
Evacuation plans


1416.11.3
Isolation of potentially infected workers


1416.12
PERSONAL PROTECTIVE EQUIPMENT (PPE)


1416.12.1
Masks


1426.12.2
Face Shields


1426.12.3
Overalls


1426.12.4
Hand Gloves


1426.13
CONSEQUENCE MANAGEMENT


1426.13.1
Change Management


1436.13.2
Succession Planning


1436.13.3
Consequences


1446.14
WELFARE FACILITIES


1446.14.1
Clean, storage for food and personal belongings


1446.14.2
No personal belongings to be kept on site


1446.14.3
No communal drinking facilities (shared cups etc.)


1446.14.4
Larger meeting areas/ preferably use technology (Skype, Zoom, Microsoft teams):


1446.14.5
Eating areas


1456.15
ADEQUATE RESOURCING OF PROJECTS


1467.
CONTRACTUAL CONSIDERATIONS


1467.1
GENERAL CONSIDERATIONS


1467.2
APPLICABLE GENERAL CONDITIONS OF CONTRACT


1467.2.1
GCC 2015




ANNEXURES

(c) ANNEXURE A:  
BASIC RISK ASSESSMENT 

(d) ANNEXURE B:

TYPICAL BILL OF QUANTITIES
(e) ANNEXURE C:  
PPE ISSUE REGISTER

(f) ANNEXURE D:  
COVID-19 QUESTIONNARE & DECLARATION

1. LIST OF ABBREVIATIONS

BRA 

Baseline Risk Assessments 

BEPs

Built Environment Professionals 

BoQ 

Bill of Quantities 

PSHSS

Project Specific Health and Safety Specifications
COIDA 

Compensation of Injuries and Diseases Act 

CR

Construction Regulations 

DEL 

Department of Employment and Labour 

H&S

Health and Safety
OHSA

Occupational Health and Safety Act No. 85 of 1993 (as amended)
PPE

Personal Protective Equipment 

PC

Principal Contractors 

SSHSS

Site Specific H&S Specification 
2. DEFINITIONS

The Employer:
The UMKHANYAKUDE DISTRICT MUNICIPALITY

The Act:
Means, unless the context indicates otherwise, the Occupational Health and 
Safety Act, No. 85 of 1993 and Regulations promulgated thereunder, as amended

COVID-19:
Means, the Novel Coronavirus (2019-n Cov2) which is an infectious disease caused by a virus that has previously not been scientifically identified in humans which emerged in 2019 and was declared a global pandemic by WHO in 2020

WHO:

Means, The World Health Organisation 

3. KEY REFERENCES

The following key references apply to the specifications:

· Occupational Health and Safety Act No. 85 of 1993 and Regulations (as amended)

· Government Gazette No. 43257 dated 29 April 2020 titled COVID-19 Occupational Health and Safety Measures in Workplaces COVID-19 (C19 OHS), 2020

· Regulation 10 (8) of the Regulations issued in Terms of Section 27 (2) of The Disaster Management Act, 2002 (ACT No. 57 of 2002).
· The Disaster Management Act, 2002 (Act No. 57 of 2002), as amended
4. INTRODUCTION

The Regulations promulgated under the National Disaster Management Act, as a result of the Covid-19 pandemic has catapulted the role of health and safety (H&S) into the forefront of all construction activities. 

Construction projects range in size and complexity, occur in rural communities and cities, where the population is dense, or there is very little activity. Irrespective of the nature of the work, workers remain exposed to the typical risks and hazards that are typical of construction. Working at heights, confined spaces, breaking, cutting and grinding to name a few. High levels of hard physical labour and long hours of work are typical, over and above the risk of contracting Covid-19. As such the Occupational Health and Safety Act No 85 of 1993 and its Regulations require to be complied with. More specifically, the Construction Regulations of 2014 remain applicable and must be adhered to in order to protect the workers. 

The Construction Regulations are very specific regarding the roles of stakeholders, namely the employer, designers and contractors. Each of these categories have very specific roles and responsibilities and cover both the built environment professionals (BEPs) and contractors. Each have roles in terms of H&S as per the existing arrangements over and above their contractual and monitoring duties on a project. 

This H&S specification is based on Annexure 2 (Guideline for the Construction Sector Relating to Health and Safety and COVID-19) of the Construction Sector Reactivation Protocols prepared by the Construction COVID-19 Rapid Response Task Team and dated 26 April 2020. 

4.1 PURPOSE 

The purpose of this specifications is to specifically manage the operations of Construction work projects during the confirmed 2020 Covid1-19 Novel Corona Virus to ensure that employees are well informed and equipped to take all possible measures to prevent the spread and contain the virus as far as possible and reasonably practicable when performing their duties on site.

4.2 IMPLEMENTATION OF THE PROJECT SPECIFIC COVID-19 OCCUPATIONAL HEALTH AND SAFETY SPECIFICATIONS 

These H&S specifications will form an integral part of the Contract and are in addition to Project Specific Health and Safety Specifications (PSHSS) already included in the document.  Where there is conflict of interpretation between the specifications, the Covid-19 specifications shall take precedence.  

No work may commence without written approval of the revised H&S plan by the H&S Agent, or the responsible person in the MISA. Subsequent to approval, the contractor’s activities on site will be monitored through regular H&S audits and Non-conformances will be issued and penalties or work stoppage will be issued where appropriate.  
4.2.1 Roles And Responsibilities of Health and Safety Officers

The PC’s Health and Safety Officer (HSO) will be required to undertaken the following amongst other activities:

· HSO officers will ensure that they carry out the COVID 19 awareness and ensure that all employees receive the message and understand what to do and how to do it. The training awareness will include training of Security officers on what to do when receiving employees to the premises. 

· HSO officers must ensure that before letting any employees inside the premises/site camp, they issue them with face masks and sanitise their hands before passing through the gate. 

· Screening questionnaire will be completed before employees can be allowed to gain access to the premises. 

· The Employer specifications and requirements will be implemented accordingly. 

· Ensure hand sanitizer and hand soap is available at all times and issued to all including training on proper usage. 

· Undertake employee awareness campaigns on how the virus is spread from one person to another and also train them on how to prevent the spreading of the virus. 

· Conduct regular toolbox talks to ensure that employees are always reminded of correct behaviour and handling of PPE provided. 

· Ensure that employees who are suspected to have the symptoms are isolated immediately and the Department of Health immediately notified of such. While waiting the HSO officer must ensure that the isolated victim is entirely kept away from other employees, this will help to lessen to spread the virus. 

5. BASELINE RISK ASSESSMENT 

5.1 SUMMARY OF RISKS IDENTIFIED DURING DESIGN AND IMPLEMENTATION

The existing Baseline Risk Assessment (BRA) will require to be amended to take into account risks related to the potential spread of the Covid-19 virus. A typical risk assessment schedule is provided in ANNEXURE A for use by the Contractor.

Examples of risk factors include but are not limited to the following: 

· Lack of financial resources by Employer; 

· Employer not enforcing financial resources for projects; 

· Transportation, to, from and on sites; 

· Manual labour for physical tasks and tasks that will not allow for social distancing; 

· Workers arriving at work with a temperature or other symptoms of Covid-19; 

· Management of isolating potentially infected workers, and tracing of family/contacts; 

· The lack of clean ablution facilities; 

· The lack of clean welfare facilities where workers congregate for lunch break; 

· Lack of cleaning and hand washing facilities; 

· Confined working areas; 

· Too few emergency supplies, first aiders and first aid boxes; 

· Sanitization of frequently used environments throughout the working day; 

· The need to continually monitor site activities; 

· Underlying chronic diseases and age of workers (experienced workers); 

· Specialised contractors having older workers, or need to cross borders, and 

· Rural projects, or small/private projects ignoring the current legislation. 

6. SITE SPECIFIC HEALTH AND SAFETY PROCEDURES

6.1 DEMOGRAPHICS

It will be incumbent upon the PC to establish a suitable and sufficient procedures for the identification of potentially infected employees and workers, the management of exposure to the corona virus on the project, including visitors and suppliers. Including a response plan for persons suspected of being infected with or exposed the virus. The procedure is to be applicable to all levels of management and supervision, employees and local labour.

As part of this procedure, the contractor is to maintain a register of all employees and workers on the project, including sub-contractor employees and workers, keeping records of the following information as a minimum (note the NIOH document that is currently available):

6.1.1 Age of Employee

The procedure is to take cognizance of the vulnerability of older workers and make provision for additional or more frequent screening of workers above a specified age. A certificate of fitness should be available to make the worker fit for duty, and should be available on site at all times.

6.1.2 Health status

A detailed record of all current and previous health conditions, specifically those identified as creating a higher risk for contracting Covid-19, to be kept for all workers. The procedure is to make provision for stringent testing procedures and management of exposure to the virus for workers with higher vulnerability due to underlying health conditions. Such records are confidential and will remain with the Occupational Health facility. A certificate of fitness must be available for each worker on site, including management and contractors.

6.1.3 Socio economic status / Unskilled labour

The procedure is to consider the socio-economic status and skill level of workers, taking cognizance of the fact that these may have an impact on the worker’s level of exposure to the virus outside of the workplace and the risk of being asymptomatic carriers of the virus to the project/site.

6.1.4 Accommodation

Where accommodation is provided by the contractor/sub-contractor, factors to be considered in the procedure include, inter alia:

· Density of occupants to allow for adequate social distancing (minimum 1.5m) in sleeping and dining quarters;

· Restriction on the number of persons using the same sanitary/hygiene facilities;

· Provision of dedicated crockery and cutlery for each occupant, together with a procedure for effective cleaning and safe storage of same and a prohibition on the sharing of utensils;

· Dedicated facilities for safekeeping of personal belongings and abovementioned utensils for each person. Such facilities are to allow for total segregation of belongings and must be easy to sanitize. Provision of such facilities for safekeeping to be accompanied with a procedure for the use and sanitizing of the storage facility to reduce the risk of cross-contamination;

· Facilities for accommodation provided by the contractor to have in place stringent procedures for personal hygiene, ongoing maintenance of sanitizing and social distancing, and

· Additional rules to include a prohibition on the sharing of clothing, towels and other personal belongings, as well as the laundering of clothing for multiple persons at the same time. 

6.2 ORIGIN OF LABOUR AND TRANSPORTATION 

Where a return to work will necessitate travel between provinces and cities for employees and workers to return to the project, the PC is to have a procedure for, or provide transport for the return of workers to minimize the risk of exposure to the virus while in transit. While this is difficult to control by the PC, induction training needs to include such information so workers can protect themselves. Where on-site transportation is done, a policy needs to be available for how such transportation will be made safe and limit any opportunity for cross infection. If possible the PC could provide their own transportation for their workers. 

Parking areas for public and private vehicles need to be considered. Hand cleaning facilities when entering gates, doors, and security entrances. 

6.2.1 Public Transportation across borders/towns/cities 

The contractor to source/recommend a transport service provider that complies with all travel restrictions and requirements as gazetted by the government, inter alia: 

· Maximum occupancy of vehicles to allow for social distancing; 

· Vehicle sanitized before passengers board; 

· Passengers provided with hand sanitizer and face masks prior to boarding; 

· Vehicle sanitized before boarding, and hand sanitizer provided to passengers prior to boarding, after each stop where passengers leave the vehicle for comfort breaks, and 

· Frequent hand sanitizing is recommended during transit. 

6.2.2 Contractor provided transportation across borders/towns/cities 

Where the contractor provides transportation across borders/towns/cities to assist workers to return to work, provision is to be made for an adequate number of vehicles to comply with the maximum occupancy as in (a) above, and all such vehicles provided will be subject to the same requirements as abovementioned. 

Since it will not practicable to separate belongings and luggage in either instance mentioned above, the contractor’s procedures must make provision for the sanitizing of personal belongings and luggage on arrival at the final destination.

6.3 SOCIAL DISTANCING
Social distancing has been shown to be an effective method to slow down the spread of the corona virus. It will be incumbent on the contractor to ensure that the construction site and facilities are set up in such a way that it will be possible as far as is practicable to maintain the required social distancing of a minimum of 1 metre between persons when at work.

6.3.1 Tasks that require more than 1 person to complete

Where it is not possible to maintain the required distance between workers due to the nature of the work activity, e.g. curb laying, confined working areas, rebar tying, preparing wire cages, the contractor will be required to implement, maintain and enforce a procedure to adequately protect such workers against potential infection with the corona virus. This includes but is not limited to:

· Providing adequate supplies of suitable PPE such as face masks, task specific gloves, safety glasses, disposable/additional coveralls;

· PPE used during multi-person activities to be exchanged immediately after the task is completed;

· Sealed bins to be provided for disposable PPE such as masks, disposable coveralls, disposable gloves, etc.;

· Sealable bags provided to each person for keeping PPE requiring laundering, such as gloves and overalls, and

· Sanitising/washing facilities provided for immediate sanitizing of hard hats, safety glasses, shoes, safety harnesses etc. on completion of multi-person tasks.

All the above to be utilized when breaking for lunch or leaving the site, and before commencing with the next or new work activity.

6.3.2 Access/Egress of Site, Welfare Facilities, Meeting Areas

The PC is to ensure there is suitable and adequate provision to minimize the risk of persons who may be infected with Covid-19 entering the site, the spread of the virus between persons who work on or visit the site and the risk of potentially contaminated persons leaving the site and accessing public spaces or going home to their families. To achieve this, the contractor is required to implement, inter alia the following measures:

· Persons accessing the site in groups to maintain social distancing of at least 1 metre while waiting to access the site;

· Persons waiting to access the site to be segregated from the public where required by the provision of dedicated, prominently identified public pedestrian walkways situated in such a way that social distancing is maintained between site personnel and the public;

· Screening of each person who enters the site with a no-touch infrared thermometer;

· Means of (fully) sanitizing each person and their belongings, who access and leave the site;

· Dedicated facilities for safekeeping of personal for each person. Such facilities are to allow for total segregation of belongings and must be easy to sanitize. Provision of such facilities for safekeeping to be accompanied with a procedure for the use and sanitizing of the storage facility to reduce the risk of cross-contamination;

· Toolbox talks to be conducted outdoors when possible in order for persons to maintain social distancing. Where inclement weather does not allow for this, toolbox talks to be conducted with smaller groupings of workers in a sheltered area large enough to maintain social distancing, and

· Eating areas to be set up in such a way that the maximum number of persons who will use the area at any one time are able to maintain the required social distancing of 1 metre. Should this not be practicable, meal times are to be staggered on a rotational basis to avoid contact between persons.

*This guideline is not an exhaustive list and the contractor is encouraged to develop rigorous control measures and procedures to safeguard all persons accessing or working on the site against the risk of Covid-19.

Where possible remote means of monitoring such as use of drones or security cameras to monitor site conditions and to do site inspections could be considered.

6.4 ALCOHOL AND DRUG TESTING

Alcohol testing may only be done using single use test units, and must be disposed of in the appropriate contaminated waste. Drug testing will only be done by an occupational health facility either using urine or blood sampling. A protocol will be drawn up by the PC to manage this with the occupational health service being used.

6.5 MEDICAL SURVEILLANCE

The normal requirements of pre-placement, periodic and exit medicals will remain, with the Occupational health service providing a methodology of how they will be including factors relating to Covid-19. No lung functions or peak flows will be done until deemed safe to do so by the South African Thoracic Society.

It is preferable that occupational health service providers use a cloud-based record keeping service to ensure easy tracking and tracing. Free apps such as Square 1 is such an example.

Any person who contracts the virus may need to be reported to the Compensation Commissioner as an occupational disease where their work is to monitor and in contact with others. Such details are provided in the Compensation for Injuries and Diseases Act (COIDA).

Isolation of workers who have a temperature or any symptoms, and removal to the closest facility for testing and treatment, through the numbers provided. The PC is to ensure their policy on this includes such information.

Workers will be required to complete COVID-19 questionnaires prior to returning to site. Any worker with any symptoms is not to return to work, or notify the PC of same.

6.6 ABLUTION FACILITIES

Ablution facilities are an essential facility that must be available for workers across a site. Facilities are a high risk area and increased cleaning regimes are required to be introduced. A policy on how this will be done is required, that will cover both portable and permanent facilities. The following are considerations, which include, inter alia:

· Portable toilets to be provided at a 1:10 ratio

· Cleaners to continually clean and have a formal cleaning regime

· Hand washing facilities (soap and water, paper towel) to be available where possible, and if not, to provide hand sanitizer

· Induction training to educate to ensure all users are hand washing correctly

· Flush toilets preferably 1:15 unless increased cleaning regime present;

· Restrict the number of people using toilet facilities at any one time e.g. use a welfare attendant;

· Wash hands before and after using the facilities;

· Enhance the cleaning regimes for toilet facilities particularly door handles, locks and the toilet flush;

· Portable toilets should be avoided wherever possible, but where in use these should be cleaned and emptied more frequently;

· Provide suitable and sufficient rubbish bins for hand towels with regular removal and disposal that need to be managed as hazardous waste;

· Introduce staggered start and finish times to reduce congestion and contact at all times;

· Consider increasing the number or size of facilities available on site if possible, and

· Provide suitable and sufficient rubbish bins in these areas with regular removal and disposal.

6.7 SECURITY ACCESS

Public access to site is to be limited at all times, and non-essential visitors are not to be allowed entry. There is required to be staggered access at all times. The following aspects are to be included in a policy document as to how such issues will be managed, inter alia:

6.7.1 Staggered access to site;

The PC should consider the following:

· Introduce staggered start and finish times to reduce congestion and contact at all times;

· Monitor site access points to enable social distancing – consideration for the number of access points, either increase to reduce congestion or decrease to enable monitoring;

· 50-100mm deep trough to be placed at entrances to site. Disinfectant is to be placed in the trough and all shoes coming onto site or leaving site will be disinfected, without wetting shoes themselves;

· Remove or disable entry systems that require skin contact e.g. fingerprint scanners or biometric system;

· Require all workers to wash or clean their hands before entering or leaving the site;

· Ensure social distancing between people waiting to enter site;

· Regularly clean common contact surfaces in reception, office, access control and delivery areas e.g. scanners, turnstiles, screens, telephone handsets, desks, particularly during peak times;

· Reduce the number of people in attendance at site inductions and consider holding them outdoors wherever possible, and

· Drivers should remain in their vehicles if the load will allow it and must wash or clean their hands before unloading goods and materials.

6.8 PROCUREMENT AND STORAGE FOR COVID-19 PPE AND GENERAL SUPPLIES

The following is to be implemented by PC:

· Availability of personal protective equipment PPE is an imperative and should be available at all times. Where this is not so, the work related to the activity will be stopped until adequate supplies are available.

· Storage of PPE is to be tightly controlled, with records of issue. Damaged PPE is to be managed in the usual way, but all to be disposed of as if contaminated.

6.9 WASTE MANAGEMENT FOR COVID-19 WASTE

Waste management arrangements to be updated to include provision for the disposal of additional waste generated due to preventative measures implemented. All waste to be managed as hazardous waste.

6.9.1 Disposal of any gloves, masks

The contractor shall dispose of all used gloves and masks as hazardous waste and provide sealable bags and containers for the safe disposal of this waste.

6.9.2 Paper towels

The contractor shall provide adequate supplies of paper towels on site. At points where these towels are provided lined waste bins to be placed in order to collect all used towels and then to be disposed of in hazardous waste.

6.9.3 Disinfectant solution

The contractor to provide adequate supplies of disinfectant on site where the use of water and soap for cleaning is not practical. If disinfectant dispensers are not refilled it should be disposed with other hazardous waste.

6.9.4 Wastewater

Wastewater at washing points, toilets, and bathrooms to be contained in a drainage system that prevent surface spills. If wastewater is contained in waste buckets it must be sealed when removed and disinfected after it is cleaned.

6.10 SIGNAGE

The PC is to review all current signs and notices displayed on site. The PC is to avoid conflicting messages/notices that have been in place prior to lockdown and review according. Typical signage that can be displayed on site is shown in Figure 1

[image: image15.png]


Figure 1: Typical Signage

6.10.1 Access rules

The contractor shall install additional signage with site rules specific to the prevention of spreading the COVID-19 virus at the access control points of the site.

6.10.2 Notices/Posters with protocols

Notices and posters shall be placed and installed to raise awareness and regarding protocols to be followed on site. These notices and posters shall be placed conspicuously at various points on the site including the following places:

· Entrance

· Site notice board

· Site Office

· Eating areas

· Next to toilets and bathrooms

· Hand washing stations

· Storerooms

6.11 EMERGENCY PLANNING

An updated emergency plan is to be completed that is in line with the current Regulations of the National Disaster Management Act.

6.11.1  First aid

Extra gloves, and disinfectants are to be available, first aiders are to be issued with at least FFPT2 masks should they be required to respond

6.11.2 Evacuation plans

Evacuation plans should consider social distancing.

6.11.3 Isolation of potentially infected workers

The emergency plan is to consider how anyone who arrives on site and displays any of the symptoms, or has a raised temperature.

6.12 PERSONAL PROTECTIVE EQUIPMENT (PPE)

The hierarchy of control applies with the use of PPE. Specific regard for the type and usage, training and control is to be outlined in the policies and procedures.

6.12.1 Masks

Masks are compulsory for all employees; personnel and professional team members, reducing the potential of inhaled COVID-19 droplets. For general administration purposes, for essential staff on site only, cloth masks may be worn. N95 masks are only to be worn by first aiders or high risk workers, due to the national shortage thereof.

All employees to have access to N95 or FFPT2 masks when required, only in instances of HIGH RISK OF EXPOSURE

All N95 and FFPT2 masks to be disposed with or after 1 day’s use. Induction is to include training on the correct use of face masks.

Cloth face masks to be used on entering and leaving the site. It is advised that each worker is supplied with at least 3 cloth face masks. This would assist ensuring that the masks are hygienic (1 on the face; 1 in the wash and 1 as a backup).

The PC must ensure that sufficient stock is at all-time available on site. This will also have depended on the type of mask being issued.

All disposable masks are biological waste and must be properly disposed of. This must be disposed in container (locked) or in bags to be either removed as medical biological waste by registered service provider.

CLEARLY IDENTIFIABLE BINS INDICATING BIOLOGICAL WASTE TO BE PROVIDED

6.12.2 Face Shields

The principal contractor could also look at options such as full face shields for preventing spreading of virus through eyes. This would assist the employee who is doing hard physical work to breathe more easily but still protecting the mouth, eyes and nose.

Face shields should be cleaned daily before the shift and at the end of the shift. Proper cleaning agents/disinfectant must be used. Face shields should be issued to employees and no sharing is allowed.

6.12.3 Overalls

All employees must be issued with 3 overalls (1 overall wearing; 1 overall in the wash and one as the backup). This will ensure that the employee will be able to wear clean hygienic overalls. This must form part of the COVID-19 training for all employees.

6.12.4 Hand Gloves

It is preferable that surgical gloves are not worn unless indicated and workers trained in the proper use thereof. Gloves must only be used when the activity demand the wearing of specific type of hand gloves. This will be directed by the PC risk assessment.

Site office personnel need to be made aware of the risks in the office environment, this include to handling of documents and plans. These employees could be issued with the appropriate hand gloves or sufficient hand wash / sanitising facilities must be available in the site office.

6.13 CONSEQUENCE MANAGEMENT

6.13.1 Change Management

Each Principal contractor / contractors to ensure that regular information pertaining to COVID 19 and or any Health and Safety matters is distributed to ensure that required measures / controls is timeously addressed. There are various information platforms available to the Principal Contractor and or employee that can assist in keeping them informed.  These include inter alia:

· Local Authority / Legislation

· World Health Organizations

· Health Care Departments / Health Care Professional’s / Centre’s / Hospitals

· Public Service Announcements – National News

Each contactractor is responsible and required to keep his or her employees informed by means but not limited by conducting the following;

· Awareness campaigns -i.e. posters within work places

· Daily site task Inspections (DSTIs)

· Toolbox talks / Daily briefings

· Meetings

· Company policies / procedures / Employee Wellbeing interaction

· Company newsletters

· Telecommunications – Cell phones Apps / e-mail

6.13.2 Succession Planning

Employees who is performing specialize work/activities (including plant operators) must be identified. These positions must have alternative employees that could perform these activities. This could mean additional training for these employees.

Key personnel on site should also have competent alternative employees that could perform these functions when needed. Where possible administrative staff should be working from home to limit any opportunistic exposure.

It is very important to understand that the availability of certain essential products and material may not always be available and thus proper planning must be in place to ensure that the activities on site are not interrupted.

Proactive planning must be in place to ensure that the following are ordered and available:

· PPE (cloth face masks, face shields, overalls)

· Hand sanitizers with at least 60% alcohol content

· Disinfectants and cleaning materials

6.13.3 Consequences

When non-compliance activities are noted, that activity will be stopped. Should the remedial actions not take place the site will be shut down till the corrective actions have been implemented.

Employees that do not work according to the SSHSS and SSHSP must be disciplined according to the company’s disciplinary codes and practices.

Supervisory employees on site must ensure compliance, and when non-conformances are noted disciplinary actions should also be followed.

PCs should note that they could be fined and even according to the Disaster Management Act, arrested.

6.14 WELFARE FACILITIES

The PC shall adapt arrangements regarding the provision of welfare facilities to be in line with Government guidelines and requirements.

6.14.1 Clean, storage for food and personal belongings

The PC to provide lockable storage for all employees on site, which shall be disinfected daily. Training and awareness to address procedures and the importance of good hygiene practice.

6.14.2 No personal belongings to be kept on site

Apart from extra clean personal clothing no other personal belongings allowed on site accept if kept in locker provided by the PC.

6.14.3 No communal drinking facilities (shared cups etc.)

The PC to provide adequate supplies of bottled water to all employees on site. Empty bottles to be disposed of as normal waste. Training and awareness to address procedures and the importance of good hygiene practice.

6.14.4 Larger meeting areas/ preferably use technology (Skype, Zoom, Microsoft teams):

The PC is to limit the number of employees at all activities to the minimum required to do the work in a safe manner. Where possible meetings must be held in open areas limited to essential personnel. Technological alternatives to be exploited for meeting attendance if possible. Training and awareness to address procedures and the importance of social distancing.

6.14.5 Eating areas

The PC is to limit the number of employees at all activities to the minimum. Stagger lunchbreaks and resting periods for work teams. Training and awareness to address procedures and the importance of good hygiene practice and social distancing.

Workers are required to stay on site once they have entered it and not use local shops.

Dedicated eating areas should be identified on site to reduce food waste and contamination.

· Break times should be staggered to reduce congestion and contact at all times.

· Hand cleaning facilities or hand sanitiser should be available at the entrance of any room where people eat and should be used by workers when entering and leaving the area;

· Workers should be asked to bring pre-prepared meals and refillable drinking bottles from home;

· Social distancing to be applied whilst eating and avoid all contact;

· Where catering is provided on site, it should provide pre-prepared and wrapped food only;

· Payments should be taken by contactless card wherever possible;

· Crockery, eating utensils, cups etc. should be disposable if supplied;

· Drinking water should be provided with enhanced cleaning measures of the tap mechanism introduced;

· Tables should be cleaned and disinfected between each use;

· All rubbish should be put straight in the bin and not left for someone else to clear up;

· All areas used for eating must be thoroughly cleaned at the end of each break and shift, including chairs, door handles, vending machines and payment devices.

6.15 ADEQUATE RESOURCING OF PROJECTS 

The PC will be required to price for the additional H&S related items that have arisen as a result of the Covid-19 pandemic and the regulations promulgated under the Disaster Management Act 2002 (Act No. 57 of 2002), as amended. The Bill of Quantities (BoQ) provided to the PC needs to take into account the requirements that have been identified in the BRA and the SSHSS. Contractors need to be able to price for the requirements and the appropriate BEP to assess the suitability of the items and pricing thereof. 

A typical example of a H&S BoQ that would be adapted is included as Annexure B.  The BoQ is not exhaustive and is dependent much on the amended BRA as approved by the Employer or his Principal agent. Should risk factors change, amendments will need to be made to the BoQ.

7. CONTRACTUAL CONSIDERATIONS

7.1  
GENERAL CONSIDERATIONS 
Before considering the provisions of the common construction contracts in detail, the following general recommendations are made: 

1. Should payment certificates not have been issued during the period of lockdown, they should be issued as soon as possible after recommencement of works, but no later than the end of May 2020. 

2. The lockdown period will give rise to various typical force majeure claims and contractors will be entitled to submit extension of time claims for the period of the lockdown. These will be evaluated by the Principal Agent in accordance with the situation/conditions on site during the lockdown. 

3. The Covid-19 epidemic and the continued lockdown regulations may have a further and continued impact to contractors after site re-opening. Those impacts will have to be assessed by the contractors and further claims for resulting delays to the project programmes may need to be considered. 

4. Where time limits are applicable to claims and claim notifications, such time period should only be calculated from, at the earliest, the date on which the relevant construction site re-opens. 

5. It is recommended that all claims arising from the lockdown be submitted and resolved as soon as possible after recommencement and well before any applicable time limits. 

6. Any disputes emerging in regard to claims should be resolved expeditiously in accordance with the provisions in the contract. 

7.2  
APPLICABLE GENERAL CONDITIONS OF CONTRACT

The following clauses in the General condition of contract are noted which are considered applicable to Covid-19 Lockdown should this occur:

7.2.1 GCC 2015

1. Clause 5.12.1 provides that the contractor is entitled to an extension of time for the completion of the works if “circumstances of any kind whatsoever” will delay the achievement of practical completion of the works.

2. Clause 5.12.2.4 specifically lists “any disruption which is entirely beyond the contractor’s control” as a circumstance entitling the contractor to an extension of time. A contractor will accordingly be entitled to an extension of time for delays caused by the lockdown and other circumstances resulting from Covid-19.

3. In terms of clause 5.12.3, if an extension of time is granted the contractor shall be paid such additional time-related general items as are appropriate.

4. Clause 5.12.4 provides that instead of granting an extension of time, if feasible, the contractor may be requested to accelerate the rate of progress to achieve practical completion and will be paid for the costs of such acceleration.

5. A contractor may also be entitled to a claim for extension of time with adjusted value in terms of clause 5.4.3 if an instruction to commence work was issued to the contractor but the employer was unable to fulfil its obligation to give the contractor access and possession of site due to the limitations imposed during lockdown.

6. However, once the contractor has been given possession of the site, a claim under clause 5.4.3 would not be applicable.

7. Covid-19 may also fall within the definition of “excepted risk” and in particular the reference to “epidemic plague” set out in clause 8.3.1.7.

8. In terms of clause 8.3.2, the contractor is entitled to an extension of time and can recover additional costs where the contractor suffers a delay or loss directly or indirectly caused by an “excepted risk”.

9. Clause 9.1.2 read with clause 9.1.4 provides that the contractor is entitled to claim additional costs, which are not covered by the additional time-related general items, caused by “a state of emergency, riot, commotion politically motivated sabotaged acts of terrorism or disorder” and “any such event beyond the control of the contractor” that materially affects the execution of the works.

10. Clause 9.1.4 requires the contractor to notify the engineer within 14 days of becoming aware of such increase in cost.

11. In terms of clause 6.8.4 the contractor is entitled to any additional costs, which are not covered by the additional time-related general items, if at any time within 28 days before the closing of tender or thereafter, any act, ordinance, regulation or by-law is amended and this results in additional cost to the contractor.

12. In terms of clause 10, the contractor is required to submit its claim for any extension of time or additional payment as follows:

(a) the contractor must submit its claim to the engineer in accordance with the specified requirements, within 28 days after the circumstance or event giving rise to such claim; and

(b) if the event giving rise to a claim is of an ongoing nature, the contractor is additionally required to deliver updated monthly claims to the engineer and submit its final claim within 28 days after the end of the event or circumstance.

13. The parties may deliver a written notice of dispute to each other and the engineer of any dispute provided that the dispute arises from a rejected claim and it is delivered within 28 days of the event giving rise to the dispute.

14. The dispute shall be referred to adjudication unless an amicable settlement is contemplated. The parties may agree to settle any claim or any dispute amicably with the help of an impartial third party. If the other party rejects amicable settlement in writing or does not respond to the invitation within 14 days or if the amicable settlement is unsuccessful the dispute shall be referred to adjudication.

15. Either party is entitled to disagree with any decision of the Adjudication Board and refer the matter to arbitration or court proceedings, whichever is applicable in terms of the contract provided that a party disputes the adjudicator’s decision not before 28 days or after 56 days from receipt of the decision.

ANNEXURE A

BASIC RISK ASSESSMENT

[image: image1.emf]LOW MED HIGH

1 4 12

2 6 18

3 8 27

LEGAL REF 

LIKELY CONSEQUENCES OF AN ACCIDENT

FREQUENCY OF EXPOSURE

PROBABILITY OF HARM

RISK RATING AND RISK CATEGORY

LIKELY CONSEQUENCES OF AN ACCIDENT

FREQUENCY OF EXPOSURE

PROBABILITY OF HARM

RISK RATING AND RISK CATEGORY

Note: This is a broad overview of the activities expected and available during the design stage of the project. Key issues will be addressed during the construction stage, and may be updated during 

this time. Consolidation of activities where overlap or applicable throughout the project (plant, material or other common activities). Compliance with all the applicable legislation is required. 

Penalties for non-compliances will be applied where issues not addressed as per the H&S Specification (as amended).

BASELINE  RISK ASSESSMENT

Risk Rating multiplier: Low = 1; Medium = 2; High = 3 PREPARED BY:



REFERENCES/ABBREVIATIONS: OHSA Occupational Health and Safety Act (applies overall); GAR = General Administration Regulations; GSR = General Safety Regulations; HBR = Hazardous Biological 

Regulations; CR = Construction Regulations; HCSR = Hazardous Chemical Substances Regulations; FR = Facilities Regulations; EIR = Electrical Installation Regulations; DMR = Driven Machinery 

Regulations; PER = Pressure Equipment Regulations; RTA = Road Traffic Safety Act; SANS = 1200 (unless stated) SANS 10085 = Access Scaffolding; SANS 10083 = Audiometry standards; SANS 1300, 

10142,10400 & 2001 = Building & Electrical Standards; SARTSM = South African Roads and Traffic Signs Manual; PC = Principal Contractor;

Baseline design: RAW RISK

Baseline Design: Residual 

risk

DESIGN ASPECTS 

PRESENT

DESCRIBE THE METHODS AND 

ACTIVITIES USUALLY 

PROVIDED BY THE PC AND 

CONTRACTOR

CATEGORYEXTRA CONTROL MEASURES NECESSARY TO 

REDUCE RISK/ REDESIGNLIKELY


ANNEXURE B

TYPICAL TO COVID-19 RELATED OCCUPATIONAL HEALTH AND SAFETY BILL OF QUANTITIES 

SECTION A: PRELIMINARY AND GENERAL ITEMS

	ITEM No
	DESCRIPTION
	UNIT
	QUANTITY
	RATE
	TOTAL

	 
	SECTION A
	 
	 
	 
	

	
	OHS Act and Construction Regulations (2014)
	
	
	
	

	A1
	Preparation of the Contractor's site specific Health and Safety Plan
	
	 
	 
	

	A1.1
	 Review of OHS Plan for each assignment. Rate to include for risk assessment specific to the COVID-19 Epidemic and other adjustments to ensure compliance for the Regulations 
	Sum
	 
	 
	

	A1.2
	Principal Contractor's initial obligations in respect of the Occupational Health and Safety Act and Construction Regulations
	
	 
	 
	

	 
	 Signage- COVID-19 Related
	 Sum 
	 
	 
	

	A1.3
	Provision of Personal Protective Equipment (PPE) related to COVID-19 virus
	 
	 
	 
	

	A1.3.1 
	Face Mask for COVID-19 (respiratory protection (as required)
	No
	 
	 
	

	 A1.3.2
	Surgical Gloves ( for security and cleaning team)
	No
	 
	 
	

	A1.3.3
	Safety Goggles for Screening Person
	No
	 
	 
	

	A1.4
	Cost of medical certificates and medical surveillance
	 
	 
	 
	

	 A1.4.1
	Initial (baseline) medical examinations
	
	
	 
	

	 
	Screenings for Employees with COVID-19 Symptoms
	Sum 
	 
	 
	

	A1.4.2
	Periodic and exit examinations
	
	
	 
	

	 
	Screenings for Employees with COVID-19 Symptoms
	No
	 
	 
	

	 
	Contractor's charges to allow for handling costs and profit in respect of A1.4.1 and A.4.2
	%
	 
	 
	

	A1.5
	Induction training
	
	 
	 
	

	 A1.5.1
	 Re-induction for Covid-19
	Sum
	 
	 
	

	A1.6
	Provision of First Aid Boxes to GSR requirements
	
	 
	 
	

	 
	 Non-contact thermometers for Covid-19
	 No
	 
	 
	

	
	
	
	
	 
	

	SUBTOTAL CARRIED FORWARD
	
	
	
	

	SUBTOTAL BROUGHT FORWARD
	

	A2
	Fixed Charge Items
	
	
	
	

	A2.1
	Facilities for Contractor including offices, storage sheds, workshops, laboratories, living accommodation, ablution and latrine facilities, tools and equipment, water supplies, electric power, communications, setting out of Works, security and dealing with water, traffic and access. Made COVID-19 Safe
	Sum 
	
	 
	

	A2.2
	Other fixed-charge obligations for COVID-19
	
	
	 
	

	A2.2.1
	Hand Sanitiser - 500ml
	No
	
	 
	

	A2.2.2
	Cleaning and detergents for cleaning everyday
	No
	
	 
	

	A2.2.3
	Daily Logbook for usage of the above accessories
	No
	
	 
	

	A2.2.4
	Extra cleaning staff
	No
	
	 
	

	A2.2.5
	Maintenance of a register for workers contacts including Civid-19 screening status 
	Sum
	
	
	

	A3
	Waste management for COVID-19
	
	
	
	

	A3.1
	Waste Bins
	No 
	
	
	

	A3.2
	Waste disposal considered to hazardous in terms of Covid-19
	Sum 
	
	
	

	A4
	Transportation
	
	
	
	

	A4.1
	Transport to Construction Site Safety for COVID-19
	Sum 
	
	
	

	
	
	
	
	
	

	A5
	Time Related Items
	
	
	
	

	
	Principal Contractor's time related obligations in respect of the Occupational Health and Safety Act and Construction Regulations
	
	
	
	

	A5.1
	 COVID-19 Related
	weeks
	
	
	

	A6
	Removal of Site establishment on completion
	
	
	
	

	TOTAL (Excluding VAT)
	


ANNEXURE C

PPE ISSUE REGISTER

LOCATION / SITE NAME: .............................................................................................   COMPANY NAME: ...........................................................

ISSUED BY:..........................................................................................................................................................................................................

	
	
	
	
	
	
	
	
	
	
	
	
	

	[image: image2.png]



	[image: image3.jpg]



	[image: image4.jpg]



	[image: image5.png]



	[image: image6.jpg]



	[image: image7.jpg]



	[image: image8.jpg]



	[image: image9.jpg]



	[image: image10.jpg]



	[image: image11.png]



	[image: image12.jpg]



	[image: image13.jpg]



	ENTER NAME AND SURNAME & SIGN BELOW EACH ITEM RECEIVED

	    Gloves
	Hard Hat
	   Overhaul
	   Safety 

    Boots
	Reflective

     Vest
	    Safety 

    Glasses
	    Dust 

    Mask
	Earplugs


	    Safety 

   Harness
	  Welding

    Gloves
	Welding Helmet/ Glasses
	Welding

   Apron
	 ENTER NAME AND SURNAME

	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	
	
	
	


ANNEXURE D

COVID-19 QUESTIONNARE & DECLARATION

Contractor Name: __________________________________________________________

Important : Please note that this is an individual Questionnaire.

Site/Work Area: __________________________________________________

Employee Name and Surname: ______________________________________

Date: ____________________________

Line Manager: ___________________________________

	Symptomatic Screening Questionnaire
	Yes 
	No

	Have you experienced symptoms of flu or had flu in the past two weeks?
	
	

	Have you experienced any coughing or breathing abnormalities lately?
	
	

	Do you currently have a fever or have you been experiencing symptoms of a fever? ( Red eyes, burning sensation )
	
	

	In the last 14 days, have you come into contact with any person that has displayed symptoms or tested positive for COVID 19?
	
	

	Have you travelled outside the borders of South- Africa lately?
	
	

	Have you been tested for COVID 19?
	
	


Personal Commitment 

1. I Will further to the above , declare any immediate changes in my health to my line manager

2. I will Adhere to all the guidelines set out by Thermaire & Ampair in the COVID 19 management plan 

3. I will maintain good hygiene practices 

4. I will maintain social distance from employees at all times 

5. I will utilize ppe and sanitizer provided at all times.

6. I will ensure that shared equipment, as far as reasonably practicable , has been sanitized before handover to other employees.

I ,_________________________________________ Declare that the document is a true statement of my current health and hereby will adhere to all guidelines set out. 

Employee Signature   __________________________

	Temperature reading If available (Refer to health practioner if above 38 degrees Celsius
	

	Employee Cleared for entrance ( Circle )
	Yes
	No


	Questionnaire reviewed by :
	


MHLATHUZE WATER
CONTRACT MW/61/2/2022/2023: CONSTRUCTION OF 25-75KL PREFABRICATED ELEVATED STEEL RESERVOIRS, BULK AND RETICULATION PIPELINES AND BOREHOLE DRILLING IN WARDS 7 AND 14 UNDER THE UMHLABUYALINGANA MUNICIPALITY
PART C4: SITE INFORMATION

INDEX

2PART C4: SITE INFORMATION
SI 

2C4.1
 LOCALITY PLAN
SI 

2C4.1.1 
Access
SI 

2C4.2 
 CONDITIONS ON SITE
SI 

2C4.2.1
Nature of Ground and Subsoil Conditions
SI 

2C4.2.2
Weather Conditions
SI 

2C4.2.3
Limitations
SI 



PART C4: SITE INFORMATION

C4.1

LOCALITY PLAN

The Locality of the site is as per the attached Locality Plan.

C4.2 

CONDITIONS ON SITE 
A brief description of the site conditions is given under this section.

C4.2.1
Nature of Ground and Subsoil Conditions
No subsoil investigations have been undertaken along the pipeline route. No responsibility is accepted for any conclusions drawn by Tenderers from the results and information supplied (if any) and Tenderers must satisfy themselves as to the nature of materials to be excavated under this contract. 

Geotechnical investigations will be undertaken during construction and after completion of bulk earthworks.  The Tenderer must allow a period of 2 weeks from the date of completion of bulk earthworks for these investigations and the production of a geotechnical report by the appointed geotechnical Engineer.

C4.2.2
Weather Conditions

The following general weather conditions are prevalent on site

	Site Conditions
	Specific Details 

	Altitude above sea level
	Maximum 230 m

	Ambient temperatures
	Maximum : 
30ºC

Minimum  :  
4ºC

24 hour Average Max : 30ºC

	Maximum relative humidity
	100%

	Environmental atmosphere
	Humid with high salt content, severely corrosive.

	Lightning
	Severe


C4.2.3
Limitations 

The following limitations characterise the site of the pipeline construction:

· Where the pipeline transverses privately owned land, the contractor’s activities will be limited to a 15m wide strip along the pipeline route. Any additional space utilisation is to be agreed with the Engineer during construction.
· The Mhlathuze Water will arrange for the right to access the site on privately owned land.
· The contractor will be required to compensate for land and crop damage, prior to commencement of work.
· The pipeline is to be laid in close proximity to existing residences. The contractor’s methodology for constructing the new pipeline should therefore ensure that no  (or minimum) disruption of the activities of residents result from his construction  activities.

· It maybe imperative that the contractor constructs access tracks during the construction period, which will be rehabilitated after the contract. The costs of provision of the access tracks will be deemed to be included in the rates of scheduled items. 
Insert Locality Plan

MHLATHUZE WATER
CONTRACT MW/DDD: CONSTRUCTION OF 25-75KL PREFABRICATED ELEVATED STEEL RESERVOIRS, BULK AND RETICULATION PIPELINES AND BOREHOLE DRILLING IN WARDS 7 AND 14 UNDER THE UMHLABUYALINGANA MUNICIPALITY
PART C5: DRAWINGS

INDEX

21
PART C5: DRAWINGS
D



PART C5: DRAWINGS
The drawings issued to tenders as part of the tender documents must be regarded as provisional and preliminary for the tenderer’s benefit to generally assess the scope of work. The drawings are issued as a separate book of drawings. 

The work shall be carried out in accordance with the latest available revision of the drawings approved for construction (AFC)

At commencement of the contract, the Engineer shall deliver to the Contractor copies of the AFC drawings and any instructions required for the commencement of the works. From time to time thereafter during the progress of the works, the Engineer may issue further drawings for construction purposes as may be necessary for adequate construction, completion and defects correction of the works. 

All drawings and specifications and copies thereof remain the property of the Employer, and the Contractor shall return all drawings and copies thereof to the Employer at the completion of the contract.

Tender drawings are issued separately and are listed hereunder:

LIST OF DRAWINGS
	DRAWING DETAILS 



	TITLE

	Element of Contract
	Drawing N⁰
	Description

	Contract MW/DDD
	J094-L1
	Locality Map

	
	J094-P01
	Project  Layout Plan 

	
	J094(02)-D02
	Details of Valve Chambers

	
	J094(02)-D03


	Pipeline Standard Details(Sheet 1 of 3)

	
	
	Pipeline Standard Details(Sheet 2 of 3)

	
	
	Pipeline Standard Details(Sheet 3 of 3)

	
	J094(02)-D04
	Name Board Details

	
	
	

	
	
	

	
	
	

	
	
	











Page SW 223
	Scope of Works 
	Part C3

	Reference: MW/61/2/2022/2023
	



