[image: image1.jpg]ETHEKWINI
MUNICIPALITY



SAFETY & SECURITY CLUSTER
Fire and Rescue Service

25 Centenary Boulevard, Umhlanga Ridge, Umhlanga, 4320
PO Box 625, Durban, 4000

Tel: +27 [0]31 5840400/1, Fax +27 [0]31 5840408
E-mail: jojoi@durban.co.za 

www.durban.gov.za 
Date

:
04 July 2014
To

:
Peter Gilmore / Municipal health & safety officer
Locations

:
Gandhi Interpretation Centre, Gandhi House and Gandhi Printing Press House.



Dube Museum at Ohlanga School School and Ohlanga Renaissance Library

Address

:
Inanda Township
Subject

:
Fire Safety Inspection report and order to comply


Fire safety compliance inspection conducted in above mentioned premises by  fire safety officer MW Chiliza on the 03 July 2014. 

Inspection revealed the following:-

	OBSERVATIONS / FINDINGS
	FOR COMPLIANCE

	GANDHI INTERPRETATION CENTRE
1. No fire extinguishers.
2. No fire hose reels.
3. No illuminated exit light or emergency light.
4. No fire equipment & escape signage.
5. Insufficient escapes or exit doors.
6. No emergency locks.
7. No manual alarm.
	GANDHI INTERPRETATION CENTRE
1. Have sabs approved and serviced 4,5 kg fire extinguishers mounted between 3cm and 1,5m off the floor with signage.

2. Have one fire hose reel installed with the minimum diameter of 25mm outside the main entrance with signage

3. Have illuminated exit light above exit doors or emergency light installed by a competent person.

4. Have fire equipment signage mounted to indicate its location and escape signs to indicate direction of escape.

5. Have additional exit or escape door installed at least 5m apart.
6. Have emergency locks installed in escape doors. (panic/push bar, thumb turn or red lam bolt) preferably push bar.

7. Have manual alarm installed by a competent person to warn people of any incident or emergency in order to evacuate.

	GANDHI HOUSE

1. No fire extinguishers

2. No manual alarm
	GANDHI HOUSE
1. Have sabs approved and serviced 4,5 kg fire extinguishers mounted between 3cm and 1,5m off the floor with signage.

2. Have manual alarm installed by a competent person to warn people of any incident or emergency in order to evacuate.

	GANDHI PRINTING PRESS

1. No fire extinguishers
	GANDHI  PRINTING PRESS
1. Have sabs approved and serviced 4,5 kg fire extinguishers mounted between 3cm and 1,5m off the floor with signage.

	MAHATMA GANDHI SETTLEMENT (COMPLEX)

1. No street fire hydrants close by.
2. No assembly point signage.
	MAHATMA GANDHI SETTLEMENT ( COMPLEX)
1. For your information

2. Have assembly point signage mounted to indicate gathering point in the event of an emergency.

	J.L. DUBE HERITAGE SITE ( Complex)

1.   No assembly point signage
2.   No street fire hydrants close by

	J.L. DUBE HERITAGE SITE (Complex)

1.   Have assembly point signage mounted to indicate gathering point in      the event of an emergency.
2.   For your information

	DUBE MUSEUM

1. No fire extinguishers.

1. No manual alarm.
	DUBE MUSEUM

1. Have sabs approved and serviced 4,5 kg fire extinguishers mounted between 3cm and 1,5m off the floor with signage.
2. Have manual alarm installed by a competent person to warn people of any incident or emergency in order to evacuate.

	OHLANGA RENAISSANCE LIBRARY

1. Insufficient escapes.
2. No manual alarm.

3. No emergency locks.

	OHLANGA RENAISSANCE LIBRARY
1. Have one additional escape door on ground level and must be 5m apart from existing one.
2. Have manual alarm installed by a competent person to warn people of any incident or emergency in order to evacuate.
3. Have emergency locks installed in escape doors. (panic/push bar, thumb turn or red lam bolt) 


NB: Fire department is responsible for inspections and technical advice only not for rectifying the problems, service providers relevant to the contraventions must be contacted for quote and action once procured.
 Health and safety officer for the municipality must be appointed to co ordinate compliance with these issues.
For any queries regarding follow up and advice on above comments, don’t hesitate to contact Innocent Jojo.

“Consultation and co-operation without compromising safety”

Yours faithfully

	Innocent Jojo

Fire Safety Officer & Law Enforcement Officer
Tel:  (031) 584 409
Cell: (071) 838 462

	


