{"text_format":"3","workbook":"xlsx","n_sheets":1,"sheets":["ADSS Table A3.1"],"read":"whole","date_system":"1900"}

{"sheet":"ADSS Table A3.1","index":0,"n_rows":27,"n_cols":7,"rows_kept":27,"merged":[[0,1,0,6],[1,1,1,6]]}
[null,"Table A3.1 Mandatory Criteria - A/B Schedule"]
[null,"ADSS A/B Schedule as per NRS 078-1 "]
[null,"Item"," Subclause","Description ",null,"Schedule A ","Schedule B"]
[]
[null,"B.1",4.1,"Number of fibres ",null,"48 cores"]
[null,"B.2",4.1,"Type of fibre ",null,"As in NRS 081 "]
[null,"B.3 ","4.2.2"," Mass per length of cable  ","kg/km ","< 200"]
[null,"B.4 ","4.2.2 ","Cable diameter ","mm"," ≤ 15"]
[null,"B.5 ","4.2.2 ","Maximum bending radius ",null,"250 mm"]
[null,"B.6 ","4.2.6 ","Cabled cut-off wavelength  ","nm"," ≤  1 260 nm"]
[null,"B.7 ","4.2.7 ","Details of measures taken and tests performed for UV",null,"XXXXXXXXXX"]
[null,null,"4.2.8","Cable markings on outer layer",null,"None"]
[null,null,"8.1.2","Cable markings on bedding layer",null,"Yes"]
[null,"B.8 ","4.2.8"," Anti-tracking sheath ",null,"Yes"]
[null,"B.9 ","4.2.8 ","Sheath tracking performance (maximum permitted leakage current under heavy pollution conditions, 100 kΩ/m longitudinal resistance). As given in IEEE 1222  ","mA","XXXXXXXXXX"]
[null,"B.10 ","4.2.9 ","Details of measures against water penetration",null,"XXXXXXXXXX"]
[null,"B.11"," 4.2.10 ","Details to minimize fibre hydrogen absorption",null,"XXXXXXXXXX"]
[null,"B.12 ","4.2.11 ","Maximum design span length  ","m","400 (or as otherwise agreed)"]
[null,"B.13"," 4.2.11"," Ultimate tensile strength (UTS) ","kN","≥ 35,0 (or as specified for specific application)"]
[null,"B.14 ","4.2.11"," Maximum working load (where fibre strain does not exceed 0,2 % in the fibres) (MAT)  ","kN","XXXXXXXXXX"]
[null,"B.15 ","4.2.11 ","Maximum continuous load (fibre under no strain) (MOT) ","kN","XXXXXXXXXX"]
[null,"B.16 ","4.2.18 ","Long-term creep ",null,"XXXXXXXXXX"]
[null,"B.17",5,"Compliance with environmental requirements ",null,"Yes"]
[null,"B.18 ","6.2.1 ","Type test reports available. ",null,"Comply"]
[null,"B.19","6.2.12","Details of electrical design tests performed to prove withstand capability of cable",null,"XXXXXXXXXX"]
[null,"B.20 ","8.2.1 ","Wound length"," m ","XXXXXXXXXX"]
[null,"B.21 ",9.1,"All documentation as listed in 9.1 to be supplied ",null,"Comply"]