Annexure 1: Bid Specification:

RFB 3287-2026: PROVISION OF HEATING, VENTILATION, AND AIR CONDITIONING (HVAC) EQUIPMENT MAINTENANCE CONTRACT FOR SITA PIETERMARITZBURG DATA CENTRE FOR A PERIOD OF THIRTY-SIX (36) MONTHS.

TECHNICAL, PRICING AND PREFERENCE POINTS REQUIREMENTS

# Contents

1.	Introduction	4

1.1	Purpose	4

1.2	Background	4

2.	Scope of Bid	4

2.1	Scope of Work	4

2.2	Delivery address	4

3.	Requirements	4

3.1	Product / Service / Solution Requirements	4

3.2	Service Elements	5

3.2.1	Full-Service Agreement	5

3.2.2	Response time and distance	5

3.3	Special Requirements	6

4.	Bid Evaluation Stages	6

4.1	Mandatory Administrative Responsiveness (Stage 1)	6

4.1.1	Attendance of briefing session	6

4.1.2	Registered Supplier	6

4.2	Technical returnable documents	7

4.2.1	Instruction and evaluation criteria	7

4.3	Technical mandatory requirements (Stage 2)	7

4.4	Special Conditions of Contract Verification (Stage 3)	8

4.4.1	Special Conditions of Contract	9

4.4.2	Declaration of compliance and acceptance SCC	15

4.5	Price and Preference Points Evaluation (Stage 4)	15

4.5.1	Costing and Preference Evaluation	15

4.5.2	Costing and Pricing Conditions	15

4.5.3	Bid Pricing Schedule	16

4.6	Declaration of Acceptance	16

4.7	Preference Requirements	16

Annex A: Bidder Substantiating Evidence	22

5.	Technical Mandatory Requirement Evidence	22

5.1	Bidder Accreditation/Affiliation Requirements	22

5.2	Bidder Experience and Capability Requirements	22

5.3	Construction Industry Development Board (CIDB) Registration Requirements	23

5.4	Special Conditions of Contract Verification	23

5.5	Preference Points Preferential Goals Evidence	23

Annex B: CIDB Registration Requirements	24

Annex C: Planned Maintenance for the HVAC system	25

6.	Detailed Scope of Work	25

6.1	High Level Scope of Work	25

6.1.1	Preventative maintenance servicing contract specifications:	25

6.1.2	Corrective Maintenance	25

6.1.3	Emergency Maintenance / Call Outs	26

6.2	Sita Change Control	26

6.3	Root Cause Analysis	27

6.4	Performance Management Meetings	27

6.5	Performance Management Reporting	27

6.6	Subcontracting	28

6.7	Equipment to be serviced	28

6.8	Building Management System (BMS)	28

6.8.1	Preventive Maintenance	28

6.8.2	Corrective Maintenance	28

Annex D: List of Equipment to be serviced	30

# Introduction

## Purpose

The purpose of this request for bid (RFB) is to invite suppliers (hereinafter referred to as “bidders”) to submit bids for the provision of HVAC equipment maintenance at SITA Pietermaritzburg data centre for a period of 36 months.

## Background

HVAC maintenance is essential for comprehensive climate control in the data centre. It is imperative that a maintenance contract be in place to prevent the disruption of operability within this SITA Data centre. This is imperative to avert the breakdown of Air Conditioning that is crucial to the computer environment. The building was designed for the functionality of providing IT services to the Government in such a way that security and risk is mitigated. Air Conditioning is therefore a critical aspect in creating an environment conducive to such operability

# Scope of Bid

## Scope of Work

The business requirement is to appoint a service provider to provide HVAC component preventive, corrective and call-out maintenance services for a period of 36 months. This service is required at the SITA Pietermaritzburg Data Centre.

The Maintenance Scope consists of these three primary activities:

- Preventive/ Routine/ Scheduled Maintenance.

- Corrective/ Remedial Maintenance.

- Emergency Maintenance/ Call Outs.

The maintenance service will include the provision of all labour, material, tools, equipment, supplies, transportation, storage utilities, supervision and services necessary to maintain the HVAC systems at the SITA Pietermaritzburg. The Bidder must have a qualified artisan to attend to HVAC incidents.

The detailed scope of work is provided in Annex C.

## Delivery address

The goods or services must be supplied or provided at the following physical address:

| No | Site Name | Physical Address |
| --- | --- | --- |
| 1 | SITA Pietermaritzburg | Natalia Building, 333 Jabu Ndlovu Street, Pietermaritzburg. |

# Requirements

## Product / Service / Solution Requirements

List of the existing equipment

| No. | Description | Quantities |
| --- | --- | --- |
| 1. | Cooling towers | 2 |
| 2. | Cooling tower fans | 2 |
| 3. | Down-blow air conditioning unit | 13 |
| 4. | Compressors | 13 |
| 5. | Sump pumps | 2 |
| 6. | Condenser water pumps and motors | 2 |
| 7. | Heat elements | 13 |
| 8. | Water Condensers | 13 |
| 9. | Humidifiers | 13 |
| 10. | Coils | 13 sets |
| 11. | Filters | 13 sets |
| 12. | Supply Fan | 13 |
| 13. | Water treatments to cooling towers | 2 |
| 14. | Sludge system | 2 |
| 15. | Isolation damper Co2 | 2 |
| 16. | Fire damper | 8 |
| 17. | Exhaust - Gas suppression | 2 |
| 18. | Fresh Air fan | 2 |
| 19. | Ceiling void exhaust (5 Service rooms) | 5 |
| 20 | Air Exhaust Systems and supply (5 service rooms) | 5 |
| 21 | Booster pumps | 2 |
| 22 | HVAC Electrical panel | 1 |

## Service Elements

### Full-Service Agreement

- This is a 36-month contract; and

- Throughout the term of the agreement, the service provider will respond to reported faults, preventive, corrective and scheduled maintenance.

### Response time and distance

Response time shall be measured as the time taken from reporting the call, to the time taken by the qualified artisan to arrive at the relevant site.

The response to call outs shall be categorised according to the need for urgency in attending to the call. All breakdowns during and after working hours shall be responded to as follows:

- Emergency response

This event/incident requires immediate action to prevent/mitigate against equipment damage, harm/injury to persons/property or service interruption. The Bidder shall respond to an emergency call-out within ninety (90) minutes.

- Urgent response

This event/incident refers to failure/repairs required that could affect services or impose danger if left unattended for a lengthy period.  The Bidder shall respond to an urgent call-out within four (4) hours.

- Routine response

This refers to any other event/incident, other than those mentioned above. These calls shall be dealt with as unscheduled additional work items as requested by SITA KZN Office Facilities and the time-frame will be agreed up in the contract.

Any breakdown impacting on services shall be attended to until restored to good reliable condition.  The Bidder will be liable for any costs incurred as a result of negligence, poor performance or excessive time taken to effect repairs.

## Special Requirements

- HVAC maintenance often comes with special requirements to ensure safety, compliance, and effectiveness. The service provider shall observe the following; Safety Procedures: HVAC maintenance requires strict adherence to safety procedures to prevent HVAC hazards, shocks, fires, and other accidents. This includes using personal protective equipment (PPE), following lockout/tagout (LOTO) procedures.

- Compliance with Standards: HVAC maintenance activities must comply with industry standards, codes, and regulations, Occupational Safety and Health Administration (OSHA) requirements, and local building codes.

- Documentation and Record-Keeping: Proper documentation of maintenance activities, inspections, tests, repairs must be kept and filed, this includes maintaining maintenance logs, equipment manuals, test reports, compliance certificates.

# Bid Evaluation Stages

The bid evaluation process consists of Four stages, according to the nature of the bid. A bidder must qualify for each stage to be eligible to proceed to the next stage of the evaluation. The stages are:

Table 1: Bid Evaluation Stages

| Stage | Description | Applicable for this bid YES/NO |
| --- | --- | --- |
| Stage 1 | Mandatory Administrative Responsiveness | YES |
| Stage 2 | Technical Mandatory Responsiveness | YES |
| Stage 3 | Special Conditions of Contract verification | YES |
| Stage 4 | Price and Preference Points Evaluation | YES |

## Mandatory Administrative Responsiveness (Stage 1)

### Attendance of briefing session

- A Compulsory physical briefing session will be held. The bidder must sign the briefing session attendance register using the same information (bidder company name, bidder representative person name and contact details) as submitted in the bidder’s response document. Any bidder who fails to attend the compulsory briefing session will be disqualified.

### Registered Supplier

- Only responses from bidders who are registered as a Supplier on National Treasury’s Central Supplier Database (CSD) in terms of National Treasury’s Instruction Note 4A of 2016/17 will be considered for award on this RFB.

## Technical returnable documents

### Instruction and evaluation criteria

- The bidder must comply with ALL the requirements as per the Technical Mandatory Requirements below by providing substantiating evidence in the form of documentation or information, failing which it will be regarded as “NOT COMPLY”.

- The bidder must provide a unique reference number (e.g. binder/folio, chapter, section, page) to locate substantiating evidence in the bid response.

- The bidder must comply with ALL the TECHNICAL MANDATORY REQUIREMENTS in order for the bid response to proceed to the next stage of the evaluation.

## Technical mandatory requirements (Stage 2)

Table 2: Technical Mandatory Requirements

| Technical Mandatory Requirements | Substantiating evidence of compliance (used to evaluate bid) | Evidence reference (to be completed by bidder) |
| --- | --- | --- |
| 1. Bidder Accreditation/Affiliation Requirements |  |  |
| The Bidder must have at least one qualified Artisan -Refrigeration Mechanic. | The Bidder to provide to ANNEX A, a copy of a valid Trade Test Certificate (Refrigeration Mechanic) for the Artisan. NOTE (1): SITA reserves the right to verify all information provided. | <provide unique reference to locate substantiating evidence in the bid response – see Annex A. par 5.1.> |
| 2. Bidder Experience and Capability Requirements |  |  |
| The Bidder must have executed an HVAC maintenance contract for at least Two (02) Customers in the past Five (05) years. | Provide to ANNEX A, reference details and/or reference letters for Two (02) customers to whom maintenance of HVAC equipment were delivered in the last Five (05) years from publication date of this bid. NOTE (1): The Bidder must provide all the following information when completing Table 6 - Company Name; and - Contact person’s, telephone number and/or email address; - Project or Service scope of work (i.e. HVAC maintenance); and - Project Start and End Date. NOTE (2): The reference letter/s should be on a company letterhead (signed and dated) and include all of the following information: - Company Name; and - Contact person, telephone and/or e-mail address; and - Project Scope of Work; and - Project Start and End date. NOTE (3): Failure to complete Table 6 fully and/or to submit reference letters as indicated will result in disqualification. NOTE (4): SITA reserves the right to verify the information provided. | <provide unique reference to locate substantiating evidence in the bid response – see Annex A. par 5.2> |
| 3. Construction Industry Development Board (CIDB) Registration Requirements |  |  |
| The Bidder must be registered with Construction Industry Development Board (CIDB) rating of 4 ME or Higher. | The Bidder needs to complete and sign Annex B as evidence that the Bidder is registered with the CIDB with a minimum rating of 4ME or higher and attach this to ANNEX A. NOTE 1: SITA reserves the right to verify the information provided. NOTE 2: SITA reserves the right to validate the certificate of registration prior to the award of the bid. | <provide unique reference to locate substantiating evidence in the bid response – see Annex A. par 5.3> |
| 4. Special Conditions of Contract Verification |  |  |
| The Bidder must accept ALL the Special Conditions of Contract. | The Bidder must accept ALL the Special Conditions of Contract by completing and signing the declaration of Acceptance in Declaration of compliance and acceptance under the Special Conditions (Section 4.4.2). NOTE (1): Failure to accept ALL the Special Conditions of Contract will result in disqualification. | <Provide unique reference to locate substantiating evidence in the bid response – see Annex A, par 5.4> |

## Special Conditions of Contract Verification (Stage 3)

- The successful supplier will be bound by Government Procurement: General Conditions of Contract (GCC) as well as this Special Conditions of Contract (SCC), which will form part of the signed contract with the successful Supplier. However, SITA reserves the right to include or waive the condition in the signed contract.

- SITA reserves the right to:

  - Negotiate the conditions; or

  - Automatically disqualify a bidder for not accepting these conditions; or

- In the event that the bidder qualifies the proposal with own conditions and does not specifically withdraw such own conditions when called upon to do so, SITA will invoke the rights reserved in accordance with subsection 4.4. (b) above.

### Special Conditions of Contract

#### Contracting Conditions

- Formal Contract - The supplier must enter into a formal written contract (agreement) with SITA.

- Right to Audit - SITA reserves the right, before entering into a contract, to conduct or commission an external service provider to conduct a financial audit or probity to ascertain whether a qualifying bidder has the financial wherewithal or technical capability to provide the goods and services as required by this tender.

#### Delivery Address

- The supplier must deliver the required products or services at as indicated in Section 2.2, Delivery Address:

SITA Pietermaritzburg, Natalia Building, 333 Jabu Ndlovu Street;

#### Services and Performance Metrics

- The bidder is responsible to provide the following services as specified in the Service Breakdown Structure (SBS);

- Operational MTTResolve: Response and Repair Times:

- The Bidder must perform HVAC faults within predefined response and repair times. Maximum Time to Repair in all cases (Full-Service Agreement) will be sixteen (16) working hours for all HVAC faults.

- Mission Critical MTTResolve: Response and Repair Times - The Bidder must perform corrective maintenance within predefined response and repair times. Maximum Time to Repair in all mission critical cases (Full-Service Agreement) will be (90 minutes) 1.5 hours working hour for the emergency call outs.

#### Supplier Performance Reporting

- Reports need to be provided immediately after the fault has been resolved for emergency call outs to communicate the findings.

- Bidder is required to compile monthly reports detailing all the other maintenance completed.

- SITA will note the:

- The % defect free deliveries made;

- The % of complete service delivery and on time, based on agreed standards; and adherence to agreed response times.

#### Certification, Expertise and Qualification

- The bidder certifies that:

- it has the necessary expertise, skill, qualifications and ability to undertake the work required in terms of the Statement of Work or Service Definition.

- it is committed to provide the Products or Services;

- perform all obligations detailed herein without any interruption to the Customer; and

- it has been certified for the Products and Services required

- is responsible for its staff and they must be equipped with adequate individual safety equipment and personal protective equipment when executing the task.

- The bidder must perform the Services in the most cost-effective manner consistent with the level of quality and performance as defined in Scope of Work or Service Definition;

- HVAC Work: The Supplier must ensure that HVAC Work is performed as prescribed by the Occupation Health and Safety Act (Act 85 of 1993 as amended).

- Any HVAC installation or alteration is certified after completion of work by means of a Certificate of completion

#### Logistical Conditions

- Hours of Work

  - Office hours are defined as business working hours of the customer and is Mondays to Fridays between 07:30 and 16:00.

  - After hours of the customer during weekdays are from 16:00 to 07:30.

  - All mission critical sites will be managed on a 24 x 7 x 365 basis.

- Tools of Trade

- The bidder is expected to use its own resources (cell phone, laptops etc) to communicate with its own offices or outside of the SITA/Client buildings, including all tools and equipment to render the services effectively.

#### Regulatory, Quality and Standards

- The contractor must adhere to the provisions within the following minimum Standards and Acts during the full period of this contract. It is taken that the contractor is familiar and conversant with these Standards and Acts:

- Occupational Health and Safety Act, inclusive of the Regulations contained within this Act, with specific reference to the Lead Regulations, Environmental Regulations, Driven Machinery Regulations, Machinery Regulations, Electrical Installation Regulations and SANS 10142, and Pressure Equipment Regulations;

- Environmental Conservation Act 1989 as amended;

- SITA’s Health and Safety Policy;

- SITA’s site access and security policy; and

- SITA’s Change Control Policy.

#### Security screening and security clearance requirements

- Company security screening: The supplier may be required to undergo a company security screening conducted by the State Security Agency (SSA). Should the SSA find the supplier not suitable after the conduct of the security screening, the business relationship will be terminated. The following documentation will be required for the company security screening process to be conducted:

- Copy of company registration documentation;

- Copy(ies) of identity documentation of Director(s), Member(s) or Trustee(s);

- Copy of valid tax clearance certificate.

- Security suitability check for individuals: SITA may, at its own discretion and in line with its policies and procedures, require employees of the supplier to be subjected to a security suitability check before commencement of a project or delivering of a service. The security suitability check is conducted by SITA in order to ensure that individuals meet the minimum-security requirements and also to verify personal information. The supplier will be required to replace any employee(s) who is found to be not suitable after the conduct of the security screening. The following documentation will be required for the security suitability check:

- Copy of identity document;

- Copy(ies) of qualification(s) if SITA requires verification thereof;

- Fingerprints – will be taken electronically;

- Signed consent form for the conduct of background checks.

Security clearance: A security clearance, issued by either the SSA or Defence Intelligence (DI) is required if any employee of the supplier will have or may gain access to classified information throughout the duration of the project or in the process of delivering a service. The level of security clearance required – Confidential, Secret or Top Secret, will be determined at the sole discretion of SITA. The supplier will have to replace any employee who do not qualify for a security clearance or is found not suitable by the SSA or DI. The following documentation will be required for the security clearance process:

- Completed Z204 or DD1057 security clearance application form;

- Fingerprints;

- Personal documentation of the applicant, including but not limited to, identity document, passport, marriage certificate (if applicable), divorce order (if applicable), qualifications, salary advice and bank statements.

#### Confidentiality and non -disclosure conditions

- The Supplier, including its management and staff, must before commencement of the Contract, sign a non-disclosure agreement regarding Confidential Information.

- Confidential Information means any information or data, irrespective of the form or medium in which it may be stored, which is not in the public domain and which becomes available or accessible to a Party as a consequence of this Contract, including information or data which is prohibited from disclosure by virtue of:

  - the Promotion of Access to Information Act, 2000 (Act no. 2 of 2000);

  - being clearly marked "Confidential" and which is provided by one Party to another Party in terms of this Contract;

  - being information or data, which one Party provides to another Party or to which a Party has access because of Services provided in terms of this Contract and in which a Party would have a reasonable expectation of confidentiality;

  - being information provided by one Party to another Party in the course of contractual or other negotiations, which could reasonably be expected to prejudice the right of the non-disclosing Party;

  - being information, the disclosure of which could reasonably be expected to endanger a life or physical security of a person;

  - being technical, scientific, commercial, financial and market-related information, know-how and trade secrets of a Party;

  - being financial, commercial, scientific or technical information, other than trade secrets, of a Party, the disclosure of which would be likely to cause harm to the commercial or financial interests of a non-disclosing Party; and

  - being information supplied by a Party in confidence, the disclosure of which could reasonably be expected either to put the Party at a disadvantage in contractual or other negotiations or to prejudice the Party in commercial competition; or

  - information the disclosure of which would be likely to prejudice or impair the safety and security of a building, structure or system, including, but not limited to, a computer or communication system; a means of transport; or any other property; or a person; methods, systems, plans or procedures for the protection of an individual in accordance with a witness protection scheme; the safety of the public or any part of the public; or the security of property; information the disclosure of which could reasonably be expected to cause prejudice to the defence of the Republic; security of the Republic; or international relations of the Republic; or plans, designs, drawings, functional and technical requirements and specifications of a Party, but must not include information which has been made automatically available, in terms of the Promotion of Access to Information Act, 2000; and information which a Party has a statutory or common law duty to disclose or in respect of which there is no reasonable expectation of privacy or confidentiality;

- Notwithstanding the provisions of this Contract, no Party is entitled to disclose Confidential Information, except where required to do so in terms of a law, without the prior written consent of any other Party having an interest in the disclosure;

- Where a Party discloses Confidential Information which materially damages or could materially damage another Party, the disclosing Party must submit all facts related to the disclosure in writing to the other Party, who must submit information related to such actual or potential material damage to be resolved as a dispute;

- Parties may not, except to the extent that a Party is legally required to make a public statement, make any public statement or issue a press release which could affect another Party, without first submitting a written copy of the proposed public statement or press release to the other Party and obtaining the other Party's prior written approval for such public statement or press release, which consent must not unreasonably be withheld.

#### Guarantee and warranties

- The supplier confirms that:

  - The warranty of goods supplied under this contract remains valid for the duration of the contract after the goods were delivered, installed and commissioned with a sign off, including the client’s signature

  - as at Commencement Date, it has the rights, title and interest in and to the Product or Services to deliver such Product or Services in terms of the Contract and that such rights are free from any encumbrances whatsoever;

  - the Product is in good working order, free from Defects in material and workmanship, and substantially conforms to the Specifications, for the duration of the Warranty period;

  - during the Warranty period any defective item or part component of the Product be repaired or replaced within 3 (three) hours after receiving a written notice from SITA;

  - the Products is maintained during its Warranty Period at no expense to SITA;

  - The Product or solution possesses all material functions and features required for SITA’s Operational Requirements;

  - the Service is continued during the term of the Contract;

  - all third-party warranties that the Supplier receives in connection with the Products including the corresponding software and the benefits of all such warranties are ceded to SITA without reducing or limiting the Supplier’s obligations under the Contract;

  - no actions, suits, or proceedings, pending or threatened against it or any of its third-party suppliers or sub-contractors that have a material adverse effect on the Supplier’s ability to fulfil its obligations under the Contract exist;

  - SITA is notified immediately if it becomes aware of any action, suit, or proceeding, pending or threatened to have a material adverse effect on the Supplier’s ability to fulfil the obligations under the Contract;

  - any Product sold to SITA after the Commencement Date of the Contract remains free from any lien, pledge, encumbrance or security interest;

  - SITA’s use of the Product and Manuals supplied in connection with the Contract does not infringe any Intellectual Property Rights of any third party;

  - the information disclosed to SITA does not contain any trade secrets of any third party, unless disclosure is permitted by such third party;

  - it is financially capable of fulfilling all requirements of the Contract and that the Supplier is a validly organized entity that has the authority to enter into the Contract;

  - it is not prohibited by any loan, contract, financing arrangement, trade covenant, or similar restriction from entering into the Contract;

  - the prices, charges and fees to SITA as contained in the Contract are at least as favourable as those offered by the Supplier to any of its other customers that are of the same or similar standing and situation as SITA; and

  - any misrepresentation by the Supplier amounts to a breach of Contract.

#### Intellectual Property Rights

- SITA retains all Intellectual Property Rights in and to SITA's Intellectual Property. As of the Effective Date, the Supplier is granted a non-exclusive license, for the continued duration of this Contract, to perform any lawful act including the right to use, copy, maintain, modify, enhance and create derivative works of SITA's Intellectual Property for the sole purpose of providing the Products or Services to SITA pursuant to this Contract; provided that the Supplier must not be permitted to use SITA's Intellectual Property for the benefit of any entities other than SITA without the written consent of SITA, which consent may be withheld in SITA's sole and absolute discretion. Except as otherwise requested or approved by SITA, which approval is in SITA's sole and absolute discretion, the Supplier must cease all use of SITA's Intellectual Property, at of the earliest of:

  - termination or expiration date of this Contract;

  - the date of completion of the Services; and

  - the date of rendering of the last of the Deliverables

- If so required by SITA, the Supplier must certify in writing to SITA that it has either returned all SITA Intellectual Property to SITA or destroyed or deleted all other SITA Intellectual Property in its possession or under its control

- SITA, at all times, owns all Intellectual Property Rights in and to all Bespoke Intellectual Property.

- Save for the license granted in terms of this Contract, the Supplier retains all Intellectual Property Rights in and to the Supplier’s pre-existing Intellectual Property that is used or supplied in connection with the Products or Services

- Provide SITA with the compliant Occupational Health and Safety File (required on site for period of installation and proof of compliance).

#### General

- The supplier will be bound by Government Procurement: General Conditions of Contract.

- (GCC) as well as this Special Conditions of Contract (SCC), which will form part of the signed contract with the Supplier. However, SITA reserves the right to include or waive the condition in the signed contract.

- SITA reserves the right to:

  - Negotiate the conditions, or

  - Automatically disqualify a bidder for not accepting these conditions, or

  - Before entering into a contract, conduct or commission an external service provider to audit or conduct probity to ascertain whether a qualifying bidder has the technical capability to provide the goods and services as required by this tender.

- The parties in the agreement agree that the offer price of all the equipment shall be at the wholesale price or below wholesale price as agreed with the OEM. Should, at any time during the existence of the agreement that the offered price which is higher than the wholesale price or as agreed with the OEM, SITA client shall be entitled to such wholesale price with the exclusion of the mark-up which the reseller may have charged.

#### Counter Conditions

- Bidders’ attention is drawn to the fact that amendments to any of the Bid Conditions or setting of counter conditions by bidders may result in the invalidation of such bids.

#### Fronting

- The SITA supports the spirit of Broad Based Black Economic Empowerment and recognizes that real empowerment can only be achieved through individuals and businesses conducting themselves in accordance with the Constitution and in an honest, fair, equitable, transparent and legally compliant manner. Against this background the SITA will not condone any form of fronting.

- The SITA, in ensuring that bidders conduct themselves in an honest manner will, as part of the bid evaluation processes, conduct or initiate the necessary enquiries/investigations to determine the accuracy of the representation made in bid documents. Should any of the fronting indicators as contained in the Guidelines on Complex Structures and Transactions and Fronting, issued by the Department of Trade and Industry, be established during such enquiry/investigation, the onus will be on the bidder / contractor to prove that fronting does not exist. Failure to do so within a period of 14 days from date of notification may invalidate the bid / contract and may also result in the restriction of the bidder/contractor to conduct business with the public sector for a period not exceeding ten (10) years, in addition to any other remedies SITA may have against the bidder/contractor concerned.

#### Business Continuity and Disaster Recovery Plans

- The bidder confirms that they have written business continuity and disaster recovery plans that define the roles, responsibilities and procedures necessary to ensure that the required services under this bid specification is in place and will be maintained continuously in the event of a disruption to the bidder’s operations, regardless of the cause of the disruption.

#### Supplier Due Diligence

- SITA reserves the right to conduct supplier due diligence prior to final award or at any time during the Contract period and this may include pre-announced / non-announced site visits. During the due diligence process the information submitted by the bidder will be verified and any misrepresentation thereof may disqualify the bid or Contract in whole or parts thereof.

#### Preference Goal Requirements Conditions

- The Bidder’s commitment for the Preference Goal Requirements in this tender will be legally binding and the Bidder needs to perform against their commitment for the duration of the contract which will form part of the Contractual Agreement.

- The Bidder must sustain or improve the company’s BBBEE Level for the duration of the contact which will form part of the Contractual Agreement.

- Performance of Preference Goal Requirements will be determined annually. Bidders must submit their Preference status report indicating progress against the Bidder’s Preferential commitments within 30 days of the yearly anniversary of the contract.

- Bidders need to keep auditable substantive records / evidence and upon request by SITA must be made available for audit and, or due diligence purposes.

- SITA reserves the right to require from a Bidder, either before a bid is adjudicated or at any time subsequently, to substantiate any claim with regards to preferences, in any manner required by SITA.

- SITA reserves the right to verify information / evidence provided by the Bidder.

- SITA reserves the right to introduce a penalty of 1% of the overall annual year spent by SITA for the prior year if the Bidder fails to comply to paragraphs (a), (b) and (c) above.

### Declaration of compliance and acceptance SCC

I (we), the bidder hereby declare that I (we) accept ALL the Special Conditions of Contract as specified in par 4.4.1 above and shall comply with all stated obligations:

Name of Bidder:_____________________________	Signature: _________________________

Date:______________

## Price and Preference Points Evaluation (Stage 4)

### Costing and Preference Evaluation

- In terms of the SITA Preferential Procurement Policy (PPP), the following preference point system is applicable to all Bids:

  - the 80/20 system (80 Price, 20 Specific Goals) for requirements with a Rand value of up to R50 000 000 (all applicable taxes included); or

- The Applicable Preference Point system for this tender is the 80/20 preference point system.

- Points for this tender shall be awarded for:

  - Price; and

  - Preference points for specific goals.

- The maximum points for this tender will be allocated as follows, subject to par.2.

Table 3: Points Allocation

| Description | Points |
| --- | --- |
| Price | 80 |
| Preference points for specific goals | 20 |
| Total points for Price and preference points for specific goals | 100 |

### Costing and Pricing Conditions

- South African Pricing - The total price must be VAT inclusive and be quoted in South African Rand (ZAR).

- Total Price

  - All quoted prices are the total price for the entire scope of required services and deliverables to be provided by the bidder.

  - All additional costs as well as cost of delivery, labour, S&T, overtime, etc. must be included in this bid.

  - All services, accessories, upgrades and options required by the solution or specified by the client must be included in the quoted price. If not included, suppliers will be required to supply these accessories at no cost to the client.

  - SITA reserves the right to negotiate pricing with the successful bidder prior to the award as well as envisaged quantities

- The bidder must complete the declaration of acceptance as per par 4.6 below by marking with an “X” either “ACCEPT ALL”, or “DO NOT ACCEPT ALL”, failing which the declaration will be regarded as “DO NOT ACCEPT ALL” and the bid will be disqualified.

### Bid Pricing Schedule

  - Bidders must complete the bid pricing schedule in the Excel spreadsheet format provided and upload this as part of their submission.

## Declaration of Acceptance

|  | ACCEPT ALL | DO NOT ACCEPT ALL |
| --- | --- | --- |
| - The bidder declares to ACCEPT ALL the Costing and Pricing conditions as specified in par 4.5.2 above by indicating with an “X” in the “ACCEPT ALL” column, or - The bidder declares to NOT ACCEPT ALL the Costing and Pricing Conditions as specified in par 4.5.2 above by - - Indicating with an “X” in the “DO NOT ACCEPT ALL” column, and; - Provide reason and proposal for each of the condition not accepted. |  |  |
| Comments by bidder: Provide the condition reference, the reasons for not accepting the condition. |  |  |

## Preference Requirements

- The bidder must complete in full all the PREFERENCE requirements.

- Allocation of points per requirements: The points allocation of bidders’ responses to the requirements will be determined by the completeness, relevance and accuracy of substantiating evidence.

- Points will be allocated for each PREFERENCE requirement as per the criteria set in each section in the table below.

- The bidder must provide a unique reference number (e.g. binder/folio, chapter, section, page) to locate substantiating evidence in the bid response. During evaluation, SITA reserves the right to treat substantiation evidence that cannot be located in the bid response, as “NOT COMPLY”. The evidence needs to be attached to ANNEX A

- Preference Goal Requirements

  - The applicable Preference Point system for this tender and points claimed is 80/20.

  - The specific Preferential Goal Requirements for this tender is indicated in the table below.

  - Failure on the part of a bidder to complete the 80/20 preference point systems and submit proof or documentation required in terms of this tender to claim preference points for the Preference Goal Requirements, will be interpreted to mean that preference points for specific goals are not claimed.

  - The Bidder must indicate how they claim points for each of the preference points by signing at par 4.5 in the Invitation to Bid document.

  - The Bidder must provide a Preferential Goals Plan (narrative document) as well as an Activity Plan with clear milestones indicating the commitment by the Bidder for each of the Presential Goals identified for this tender for the duration of the contact set in each section in Annexure A table below.

  - Failure on the part of a bidder to submit proof or documentation required in terms of this tender to claim preference points for the Preference Goal Requirements for this tender, will be interpreted to mean that preference points are not claimed.

  - The Bidder’s commitment for the Preference Goal Requirements in this tender will be legally binding and the Bidder needs to perform against their commitment for the duration of the contract which will form part of the Contractual Agreement.

  - The Bidder must sustain or improve the company’s BBBEE Level for the duration of the contact which will form part of the Contractual Agreement.

  - Performance of Preference Goal Requirements will be determined annually. Bidders must submit their Preference status report indicating progress against the Bidder’s Preferential commitments within 30 days of the yearly anniversary of the contract.

  - Bidders need to keep auditable substantive records / evidence and upon request by SITA must be made available for audit and, or due diligence purposes.

  - SITA reserves the right to require from a Bidder, either before a bid is adjudicated or at any time subsequently, to substantiate any claim with regards to preferences, in any manner required by SITA.

  - SITA reserves the right to verify information / evidence provided by the Bidder.

  - SITA reserves the right to introduce a penalty of 1% of the overall annual year spent by SITA for the prior year if the Bidder fails to comply to paragraphs (g), (h) and (i) above.

Table 4: Preference Goal Requirements (Specific Goals)

| Preference Goal Requirement # | Preferential Goal Requirements | Preferential Goal Requirements |  |
| --- | --- | --- | --- |
|  | Preferential Goal Requirements allocated for this tender | Substantiating evidence and evidence reference to be completed by bidder. Evaluation per requirement: Each requirement indicated in the table below must be completed and points will be allocated based on the evidence required below | Evidence Reference |
|  | B-BBEE Requirements |  |  |
| 1) | B-BBEE Requirements Promotion of Transformational Objectives. | Evidence: The Bidder must provide a copy of the following relevant evidence for the Preferential Goal points which the Bidder qualifies for: - Columns A, B, C and D in table 5 # Copy of relevant proof of the following to confirm the B-BBEE status of the contributor as defined in the Broad-Based Black Economic Empowerment Act: - B-BBEE certificate (from a SANAS Accredited Agency); # or # Sworn affidavit in the format provided by CIPC - Applicable to EMEs and QSEs only; # and/ or - Column D in table 5 # Copy of South African Identification Document (ID); and/ or - Column E in table 5 # Copy of Medical Certificate clearly indicating the disability in line with the B-BBEE status claimed as defined in the Broad-Based Black Economic Empowerment Act. Points allocation: Points will be allocated for bidders that meets the requirements as indicated in table 5. | <provide unique reference to locate substantiating evidence in the bid response – Annex A, par 5.5> |

Table 5: B-BBEE Points as part of the Preference Goal requirements (Preferential Goal Requirements for (80/20) system)

Note: Bidder to select the section for points they wish to claim (Mark as Y=Yes) in the table below.

|  |  |  |  | Ownership |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Reference # | Contributor Level as defined in the Broad-Based Black Economic Empowerment Act | EME/QSEs | Black Owned (BO) (51% or more) | Black Woman Owned (BWO) (More than 30%) | Youth Owned | Owned by People living with disabilities | Score | Bidder to select the section for points they wish to claim (Mark as Y= Yes) |  |
|  |  |  | (A) | (B) | (C) | (D) | (E) | (F) |  |  |
|  | 1 | Level 1 | 6 | 6 | 4 | 2 | 2 | 20 |  |  |
|  | 2 | Level 1 | 6 | 4 | 2 | 2 | 0 | 14 |  |  |
|  | 3 | Level 1 | 6 | 4 | 2 | 0 | 0 | 12 |  |  |
|  | 4 | Level 1 | 6 | 4 | 0 | 0 | 0 | 10 |  |  |
|  | 5 | Level 2 and 3 | 4 | 2 | 1 | 1 | 1 | 9 |  |  |
|  | 6 | Level 2 and 3 | 4 | 2 | 1 | 1 | 0 | 8 |  |  |
|  | 7 | Level 2 and 3 | 4 | 2 | 1 | 0 | 0 | 7 |  |  |
|  | 8 | Level 2 and 3 | 4 | 2 | 0 | 0 | 0 | 6 |  |  |
|  | 9 | Level 4 and 5 | 2 | 1 | 0,5 | 0,5 | 0,5 | 4,5 |  |  |
|  | 10 | Level 4 and 5 | 2 | 0,5 | 0,5 | 0,5 | 0 | 3,5 |  |  |
|  | 11 | Level 4 and 5 | 2 | 0,5 | 0,5 | 0 | 0 | 3 |  |  |
|  | 12 | Level 4 and 5 | 2 | 0,5 | 0 | 0 | 0 | 2,5 |  |  |
|  | 13 | Level 6 | 0 |  | 0 | 0 | 0 | 0 |  |  |
|  | 14 | Level 7 | 0 |  | 0 | 0 | 0 | 0 |  |  |
|  | 15 | Level 8 | 0 |  | 0 | 0 | 0 | 0 |  |  |
|  | 16 | Non-Contributor | 0 |  | 0 | 0 | 0 | 0 |  |  |
|  | Total Maximum Score Allocation: |  | 20 |  |  |  |  |  |  |  |

- Bidder Substantiating Evidence

# Technical Mandatory Requirement Evidence

## Bidder Accreditation/Affiliation Requirements

Provide a copy of a valid Trade Test Certificate (Refrigeration Mechanic) for the Artisan.

NOTE (1):

SITA reserves the right to verify all information provided.

## Bidder Experience and Capability Requirements

Provide reference details and/or reference letters for Two (02) customers to whom maintenance of HVAC equipment were delivered in the last Five (05) years from publication date of this bid.

NOTE (1):

The Bidder must provide all the following information when completing Table 6

- Company Name; and

- Contact person’s, telephone number and/or email address;

- Project or Service scope of work (i.e. HVAC maintenance); and

- Project Start and End Date.

NOTE (2):

The reference letter/s should be on a company letterhead (signed and dated) and include all of the following information:

- Company Name; and

- Contact person, telephone and/or e-mail address; and

- Project scope of Work; and

- Project start and End date.

NOTE (3):

Failure to complete Table 6 fully and/or to submit reference letters as indicated will result in disqualification.

NOTE (4):

SITA reserves the right to verify the information provided.

Table 6: References

| No | Company Name | Reference person name, contact details | Project Scope of Work | Project start and end date |
| --- | --- | --- | --- | --- |
| 1 | <Company name> | <Person Name> <Tel> <email> | < Provide scope of work from Two (02) customers to whom maintenance of HVAC equipment were delivered in the last Five (05) years from publication date of this bid>. | Start Date: End Date: |

## Construction Industry Development Board (CIDB) Registration Requirements

The Bidder needs to complete and sign Annex B as evidence that the Bidder is registered with the CIDB with a minimum rating of 4ME or higher and attach this here.

NOTE 1:

SITA reserves the right to verify the information provided.

NOTE 2:

SITA reserves the right to validate the certificate of registration prior to the award of the bid.

## Special Conditions of Contract Verification

The Bidder must accept ALL the Special Conditions of Contract by completing and signing the declaration of Acceptance in Declaration of compliance and acceptance under the Special Conditions (Section 4.4.2).

NOTE (1):

Failure to accept ALL the Special Conditions of Contract will result in disqualification.

## Preference Points Preferential Goals Evidence

The Bidder must provide a copy of the following relevant evidence for the Preferential Goal points which the Bidder qualifies for:

- Columns A, B, C and D in table 5

# Copy of relevant proof of the following to confirm the B-BBEE status of the contributor as defined in the Broad-Based Black Economic Empowerment Act:

# B-BBEE certificate (from a SANAS Accredited Agency);

# or

# Sworn affidavit in the format provided by CIPC - Applicable to EMEs and QSEs only;

# and/ or

- Column D in table 5

# Copy of South African Identification Document (ID); and/ or

- Column E in table 5

# Copy of Medical Certificate clearly indicating the disability in line with the B-BBEE status claimed as defined in the Broad-Based Black Economic Empowerment Act.

Points allocation:
Points will be allocated for bidders that meets the requirements as indicated in table 5.

- CIDB Registration Requirements

The Bidder needs to complete and sign to confirm that the bidder is registered with the Construction Industry Development Board (CIDB) with a minimum rating or higher of 4ME or higher.

      - The Bidder needs to indicate the Bidder, CIDB rating by ticking next to the relevant CIDB rating in the table below:

| Service and Support (Milestones) | CIDB Rating | Bidder to Indicate the Bidder CIDB rating here | CRS Number |
| --- | --- | --- | --- |
| CIDB Rating | 4ME |  |  |
|  | Higher |  |  |

      - The Bidder confirms and will ensure compliance to the CIDB Basic Guide General Conditions of Contract for Construction Works (GCC 2004).

NOTE 1:

SITA reserves the right to verify the information.

I, the Supplier (Full names) …………………………………………………. Representing (company name) …………………………………………………………….. hereby confirm that the Bidder is registered with Construction Industry Development Board (CIDB) and understand that it will form part of the contract and is legally binding.

Thus, done and signed at ……………………………………. On this………day of……………….20….

__________________

Signature

Designation:

- Planned Maintenance for the HVAC system

# Detailed Scope of Work

## High Level Scope of Work

The Maintenance Scope consists of these three primary activities:

- Preventive/Routine /Scheduled Maintenance

- Corrective/ Remedial Maintenance

- Call outs

### Preventative maintenance servicing contract specifications:

In terms of this maintenance contract the Contractor will regularly and systematically inspect the systems and perform such service and maintenance work as is described in the Schedule of Equipment and Maintenance Schedules attached hereto, and which forms part of this agreement. A report on the monthly service is required. Should a problem be identified during the course of the monthly maintenance, this must be identified and brought to the attention of SITA in this monthly report. Should it be found that during the scheduled inspections that repairs and/or replacements are required; these will be reported to SITA. The contractor must then provide SITA with a written quotation to rectify/repair the identified problem. SITA will then follow the procurement process for the repairs subjected to SITA’s procurement policies and procedures. Outstanding problems must be carried forward in monthly service reports.

  - The Supplier will be required to support and fully co-operate with other vendors who perform any corrective repairs.

  - The Supplier will be required to quality check and pass all work done by other vendors and sign-off the job card as complete.

  - A monthly maintenance service must be carried out to the equipment as stipulated on annex C

  - Details of actual maintenance that is to be performed, and the associated frequency, i.e. monthly, quarterly and annually, is identified in Annexure C.

  - The maintenance service must also make provision for the water treatment for the cooling towers

  - A Technician to be on standby after-hours including weekends and public holidays 24/7/365 days.

  - All callouts 24/7/365 days irrespective of the cause of the fault must be included in the costing.

  - Technicians must be Trade Tested and must have at least three (3) years’ experience on central plants, chillers and air handling systems.

  - Provide a consultant and advisory service to SITA KZN.

### Corrective Maintenance

- Corrective Maintenance is carried out to repair, replace, fix or adjust significant equipment and defects and failures, including the required replacement of significant units, parts, modules and components that are attributable to the Maintenance Contractor and within the scope of its responsibilities. The need for Corrective Maintenance can be identified by either the Maintenance Contractor during a site inspection or during Preventive Maintenance or identified by SITA (or one of its contractors).

- Where the Maintenance Contractor identifies the need for Corrective Maintenance that does not form part of the standard Preventive Maintenance repair requirements, the contractor shall notify the SITA Electrical Technologist / Technician within 6 hours in detail of such identification. SITA shall then decide on appropriate further action and indicate to the Maintenance Contractor that he may close the case or provide SITA with a non-obligatory quotation. SITA may also obtain quotations from other service providers. SITA may then decide to proceed with the corrective repair according to the written quotation provided. The repairs will be done on an ad-hoc time and material basis. Permission for the maintenance contractor to proceed with the corrective repair will be issued in writing.  Where SITA identifies the need for Corrective Maintenance, the process shall be the same as (a) above.

- SITA may award work for corrective maintenance or new installations to a different supplier other than the Maintenance contractor. The Maintenance contractor will be required to support and fully co-operate with the other supplier/s. The Maintenance contractor will be required to quality check and pass all work done by other suppliers and provide SITA with written confirmation of completion of the corrective maintenance or new installation.

- Where purchase orders have been issued to the maintenance contractor for Corrective Maintenance, but the maintenance contractor is not performing or providing the quoted works within the agreed timeline, SITA shall have the right to cancel the purchase order, or part thereof.

### Emergency Maintenance / Call Outs

- The activity involved with restoring, repairing or replacing on a non-scheduled maintenance basis. This maintenance activity would be a result of a service affecting or possible service affecting defect resulting in the loss of operation or potential imminent loss of operation of any part or component of any site. The nature of the defect component is such that it was not identified or known previously (for which the corrective maintenance process could have been followed).

- The contractor shall have a 24/365 call out facility. The maximum response time which the contractor must respond to a call must be as follows:

  - Critical (HVAC breakdown) – Within 90 minutes from notification;

  - Non-Critical (HVAC breakdown) – within four (4) hours from notification;

  - If the above response times are not adhered to it may attract a penalty as set out below; and

  - Spares required for ad hoc requests must be quoted for and approved by SITA KZN before the service is rendered.

- Emergency Maintenance action shall be required at any time day or night including weekends and holidays. The Maintenance Contractor shall have a sufficient number of available staff to react on a 24x7x365 basis. The Emergency maintenance response times shall meet or exceed the Service Level Agreements timelines set within this document.

- During Emergency Maintenance action the maintenance contractor’s objective shall always be to prevent a site failure or service failure by any means possible.

- The labour cost (which includes travel cost, overhead cost, etc.) for Call Outs are deemed included in the Scheduled Maintenance rate per site. The rationale is that the maintenance contractor is responsible for the site maintenance and should ensure that the site doesn’t experience any risk. Components that could lead to failure, or that could place the site under risk should thus have been identified during the scheduled maintenance work and visits.

- The component replacement cost under Emergency Maintenance shall be based on the contractual unit rates. Where no unit rates exist for that item, the contractor shall provide a cost based on the item’s cost plus the unit rate markup. Should the Maintenance Contractor have the need to subcontract the work to a third party, the subcontractor’s cost (inclusive of the subcontractor’s supporting documents) shall be presented with the Maintenance Contractor’s unit rate markup. The Maintenance Contractor shall however procure expensive components directly from the subcontractor’s supplier, to prevent multiple layer markup cost to SITA. The sub-contractor is not allowed to subcontract any portion of his work assignment to another party. Where the Maintenance Contractor receives trade discounts, these discounts shall be made visible to SITA and be passed on to SITA.

- Call out costs for labour that is not directly related to preventive maintenance, such as power tests over and above the specified monthly tests (or the like) shall be based on the contractual unit rates.

## Sita Change Control

- The contractor must not undertake any work on any of the major HVAC components or switch off any of the major HVAC components without an approved SITA change request;

- The dates for the Change Control requests will depend on SITA suitability. A number of factors influence the Change Control request dates and could be amongst other reasons other high impact SITA Change request work having a higher priority, SITA client approval, anticipated Grid power interruptions, and freeze periods.

## Root Cause Analysis

- The Reason for any Outage (RFO) for failures must be issued within 12hours of equipment failure, by the contractor.

- A detailed HVAC Root Cause Analysis (RCA) must be issued within 36-hours of the equipment/HVAC failure. The following minimum points must be addressed in the RCA:

- Background leading to the failure

- HVAC reason for failure, which is supported by the Original Equipment Manufacturer.

- If a component failure, why it hasn’t been detected and repaired during Preventive Maintenance.

- If its’s a SLA failure, why the SLA has been breached.

- Moneys that shall be credited by the contractor to SITA as penalty for failure.

- How similar failures shall be prevented for this site and other sites under the contractor’s responsibility.

- Time required for permanent repairs.

- How the restored system (and other similar systems) shall be tested to make sure similar failures shall not occur.

- How lessons learned shall be incorporated into the Preventive Maintenance, Standard Operating Procedures during the remainder of the contract.

- Upon SITA’s prior approval, and nature of the component failure, the 36-hour SLA may be extended by SITA to cater for detailed analysis.

- Technically poor and sub-standard RCAs shall not be accepted and shall be referred back to the maintenance contractor, with the 36-hour SLA still intact.

- Technically acceptable RCAs requiring further explanation shall be referred back to the maintenance contractor, after which another 12hour window shall be allowed for elaboration on the requested areas.

## Performance Management Meetings

- The contractor must meet with SITA at least once per month during the contract period, during which the progress of the contract and issues under this contract must be discussed.

- The reports under discussion must be released to SITA at least four (4) business days in advance.

## Performance Management Reporting

- The contractor must provide the following monthly reports during the warranty period.

  - Mechanical/Technical Concern list;

  - Equipment at end of life in the following 3 months, 6 months, 12 months;

  - List of high frequency incident / call outs;

  - List of open calls still in progress with targeted completion dates;

  - List of RFOs and RCAs and submission dates;

  - Component / module repair report;

  - Areas of risk where SITA is exposed to Occupational Health and Safety risks;

  - Areas of risk where SITA is exposed to site failure risks;

  - Capacity Report;

  - Unavailable critical spares and stock report of critical spares, as at report date;

  - Carbon Footprint information;

  - Invoices not paid by SITA;

  - Outstanding Purchase Orders from SITA;

  - Schedule of quotes submitted to SITA under this contract; and

  - Warrantee report on components repaired / replaced.

## Subcontracting

- The contractor / service provider must obtain SITA’s permission for any sub-contracting of work

- Where work is subcontracted to a specialist third party contractor / service provider, the Contractor / Service provider must supervise the work continuously on site to ensure acceptable quality and to ensure that no risk exist to SITA and ensure no service interruptions to SITA or its clients. The Contractor / Service provider remain fully responsible for the subcontractor’s actions or omission of actions. Penalties or claims for damages caused by the sub-contractor shall be applied to the Contractor / Service provider in full.

## Equipment to be serviced

- All equipment to be inspected cleaned, painted, lubricated and adjustments made as per schedule.

- Supply and refill refrigerant gas when necessary.

- The BMS Software upgrade and maintenance of the system.

## Building Management System (BMS)

### Preventive Maintenance

- System Health Checks

- Verify communication between devices (sensors, controllers, actuators).

- Test network connections and address any latency or errors.

- Update firmware and software to the latest versions.

- Sensor Calibration

- Regularly calibrate temperature, humidity, pressure, and CO2 sensors for accurate readings.

- Check sensor placement and cleanliness.

- Controller Inspections

- Confirm correct operation of controllers and control loops.

- Check programming logic for outdated or inefficient algorithms.

- Replace worn-out batteries in backup power for controllers (if applicable).

- Actuator and Valve Maintenance

- Inspect and lubricate dampers, valves, and actuators.

- Test operation to ensure proper response to control signals.

- HVAC and Equipment Monitoring

- Verify HVAC components are controlled as expected.

- Check setpoints, schedules, and overrides for accuracy

- System integration.

- Integrate the system with UPS and generator.

### Corrective Maintenance

- Fault Diagnosis and Repair

- Identify and resolve system errors or communication faults.

- Repair or replace faulty sensors, controllers, or actuators.

- Configuration Adjustments

- Update schedules, setpoints, and programming logic to align with building usage patterns or occupant feedback.

- Component Replacement

- Replace aging hardware that is no longer efficient or reliable.

- Trend Analysis

- Analyse historical data for anomalies in temperature, pressure, energy use, or other parameters.

- Alerts and Notifications

- Configure the BMS to send alerts for components nearing failure based on usage trends.

- List of Equipment to be serviced

| No. | Description of Equipment | Frequency |
| --- | --- | --- |
| 1. | 2 x Cooling Towers - Check frames for corrosion - Check structure and mountings - Check water levels - Check ball operation - Inspect cold water basin - Drain and clean sump and strainer - Check water treatment system operation - Check automatic bleed valve operation - Check chemical levels - Water sample test - Check spray nozzle, branch grommets, wet deck and eliminators - Check inlet louvers- remove any dirt or debris - Clean piping and equipment - Check and service water temperature in and out - Check and record plantroom temperature and humidity | Monthly |
| 2. | 2 x Cooling Tower Fans - Visual inspection - Check bearings - Oil the bearings - Lubricate motor base adjusting screws - Check all mountings on the fan and motor - Clean fan blades and check condition - Check the V-belts and the condition of pulleys - Check fan for rotation without obstruction - Check the electrical connection and tighten - Clean the equipment - Adjust belt tensions - Check drive alignment - Check fan for uniform pitch - De-sludge cooling tower - Check fan for uniform pitch | Monthly |
| 3. | HVAC Electrical Panels Visual Inspection: - Check for any signs of damage (burn marks, rust, corrosion). - Ensure panel cover and door are intact and securely attached. - Inspect for loose or frayed wiring. - Verify that all labels are clear and legible (circuit labels, safety labels, etc.) - Look for any unusual smells, which could indicate overheating or burning Cleanliness: - Remove dust and debris from inside the panel. - Ensure no foreign objects (like screws or tools) are left in the panel. - Check ventilation openings for blockages Circuit Breakers and Fuses: - Confirm that all breakers are properly labelled and functional. - Test breakers by toggling them off and on to ensure smooth operation. - Check for any signs of wear, overheating, or corrosion. - Verify that all fuses are of the correct rating and replace any blown fuses. Measure and record the Current (A) and the Voltage (V) | Monthly |
| 4. | 2 x Booster Pumps General Visual Inspection - Check for any visible leaks (water or lubricant) around the pump and piping. - Inspect for signs of corrosion or rust on the pump body and connections. - Look for any unusual wear, damage, or cracks in the pump casing. Electrical Checks - Verify that power supply cables and connections are connected. | Monthly |
| 5. | 2 x Sump Pumps - Check all mountings - Check bearings - Check operation of both pumps - Check and confirm operation of level switched and alarms - Check for leaks and blockages - Clean the sump - Check for foreign objects in the sump - Check general status of motor/ pumps and couplings - Clean the equipment - Check the pumps alignment - Prime pump motors - Measure and record current and voltage | Quarterly |
| 6. | 2 x Condenser water pumps and motors - Check alarms - Check all mountings - Check frames/ panel for corrosion - Visual inspection - Check mounting - Check for noisy bearings - Grease and oil bearings - Check for leaks and blockages - Check mechanical seals - Check operation of all gauges - Clean strainers installed before pumps - Check motor and pump alignment - Check general status of motors - Check electrical connection and tighten - Check operation of by-pass control valves in condenser water system - Clean equipment - Replace packing - Remove packing and inspect sleeves - Realign coupled pumps and record - Measure the current and the voltage | Monthly |
| 7. | 13 x down-blow air conditioning unit - Check alarms - Check all mountings - Check frames/panels for corrosion - Check for excess vibration from rotating equipment - Clean strainers on condenser water at the units - Check and confirm operation of water control valve - Measure and record room temperature and humidity in each are served by down blow unit | Monthly |
| 8. | 13 x Compressors - Visual inspection - Check mounting - Visual check all components - Check pipe work and lagging - Simulate and record LP &HP cut out - Check for gas leaks - Measure and record refrigerant suction - Measure and record running amps - Measure and record line voltage - Measure and record refrigerant discharge - Record superheat and subcooling temperatures - Check oil levels and oil pressure - Check each circuit sight glass for dryness and bubble for indication of leaks - Check for refrigerant leaks in critical areas - Check electrical connection and tighten - Check wiring - Flush oil- - Check all safety switches and settings - Check general operation - Clean equipment | Monthly |
| 9. | 13 x Heat Elements - Check element mounting - Check operation - Check wiring and connection, tighten if necessary - Measure and record, current and Voltage | Monthly |
| 10. | 13 x Condensers - Check for water leaks - Check pressure drop of condenser - Clean and flush condenser | Monthly |
| 11. | 13x Humidifiers - Check water levels - Check for scale build up - Check for leaks - Check general operation and tighten - Clean equipment | Monthly |
| 12. | 13 sets x Coils - Visual check the surface and general status - Spray clean with water (if required) - Spray clean clear drain pan - Check and clear drain pan - Check, clean drainpipe and flush | Monthly |
| 13. | Filters - Visual check of filters - Measure pressure drop across filters and record - Replace or clean filters, if pressure is higher than 120Pa | Monthly |
| 14. | 13 x Supply Fans - Visual inspection for vibration - Check bearing - Check fan blades direction - Clean fan blades and check condition - Check all mountings on fan and motor - Check insulation and for leakages - Check general operation of unit - Clean the equipment - Check drive alignment | Monthly |
| 15. | Water Treatments - Water Quality Checks - Test pH - Test conductivity - Check TDS levels - Verify chemical dosing | Monthly |
| 16 | Sludge system - Inspect sludge accumulation - Verify sludge removal process - Check drain operation | Monthly |
| 17 | Isolation Dampers CO₂ (2 - Verify damper movement - Inspect linkage and actuators - Check seals | Monthly |
| 18 | Fire Dampers (8) - Inspect fusible links - Verify damper operation - Check blade condition | Monthly |
| 19 | Exhaust - Gas suppression - Inspect exhaust fans - Check ductwork condition - Verify extraction operation - Test controls and interlocks | Monthly |
| 20 | Fresh Air fan - Inspect fan blades - Check bearings - Inspect coupling/belts - Measure airflow - Check vibration - Measure motor current | Monthly |
| 21 | Ceiling void exhaust (5 Service rooms) - Inspect fans - Check ductwork integrity - Inspect dampers - Operational Checks - Verify airflow rates - Check room pressure | Monthly |
| 22 | Air Exhaust Systems and supply (5 service rooms) - Verify airflow - Check filters - Inspect fan operation - Measure exhaust airflow - Verify room air change | Monthly |