APPENDIX E -   Tender Technical Schedule A&B (Returnable)

# CONTENTS

Page

1. General	4

2. Experiences and eligibility	5

2.1 EPC Contractor	5

2.2 plant Designer and Trainers	6

3. plant configuration design	7

4. Guarantee on Performance and Availability	9

5. Equipment Warranty	11

6. Technical datasheets -  Components	12

6.1 Civil Works	12

6.2 Electrical Works	13

6.2.1 PV Modules	13

6.2.2 DC Combiner box (Primary and Secondary)	13

6.2.3 DC Cabling and Connectors	14

6.2.4 String Inverters	14

6.2.5 Hybrid System (BESS)	15

6.2.5.1 AC Cabling	16

6.2.5.2 AC Distribution Boards	17

6.2.5.3 Protection	18

6.2.6 Weather Stations	19

6.3 Control and monitoring system	19

6.4 Safety and security	20

6.5 INspection, testing and maintenance	20

6.6 Spare Parts	21

7. Project IMPLEMENTATION Schedule	22

8. document management	23

Table 2-1: General Information about EPC Contractor	5

Table 2-2: Specific EPC Project Experience	5

Table 2-3: Engineering Experience Requirements	6

Table 3-1: Kriel Carport PV System Design	7

Table 3-2: Admin Carport PV/BESS Hybrid System Design	8

Table 4-1: Kriel PV Plant Performance Guarantee – From the Contractor	9

Table 4-2: Monthly Breakdown of First Year Guaranteed PR for Kriel PV plant	9

Table 4-3: Admin PV Plant Performance Guarantee – From the Contractor	10

Table 4-4: Monthly Breakdown of First Year Guaranteed PR for Admin PV plant	10

Table 5-1: Equipment warranty for Kriel PV Plant	11

Table 5-2: Equipment warranty for Admin PV/BESS Plant	11

Table 6-1: Civil Works Technical Specification per Carport	12

Table 6-2: PV Module Specific Requirement	13

Table 6-3: DC Combiner Box Requirement	13

Table 6-4: DC Cabling and Connectors Requirement	14

Table 6-5: Kriel Carport String Inverter Requirements	14

Table 6-6: Admin Carport BESS Requirements	15

Table 6-7: AC Cabling Requirements	16

Table 6-8: Kriel Carport AC Distribution Board Requirements	17

Table 6-9: Admin Carport AC Distribution Board Requirements	18

Table 6-10: Earthing, Lightning and Surge Protection Requirements	18

Table 6-11: Weather Station Requirements per Carport	19

Table 6-12: CMS Requirements	19

Table 6-13: Fire Protection Specific Requirements	20

Table 6-14: Inspection, Testing and Maintenance Requirements	20

Table 6-15: Minimum Spare Parts Requirement	21

Table 7-1: Project Implementation Schedule Key Milestones - Requirements	22

# General

- This document provides the specific technical requirement and schedules for the Tenderer to complete and return during the Tender phase.

- The Tenderer completes this document with the clear understanding of technical information presented in the Works Information document (Technical Specification 474-13557).

- The Employer has completed the column “Required – Schedule A” in all Tables in this document with minimum requirements for the Tenderer to respond to.

- The Tenderer fills in the column “Tendered – Schedule B” in all Tables in this document electronically before printing. An Empty column is considered non-responsive.

- The technical information provided by the successful Tenderer forms part of the contract data and is binding.

- The technical datasheets, reports, diagrams and drawings are supporting document that are necessary to verify the information completed by the Tenderer in Schedule B. Failure to attach supporting information is considered non-responsive.

- Failure to submit this document leads to technical disqualification.

# Experiences and eligibility

## EPC Contractor

Table 2-1: General Information about EPC Contractor

| No. | Description | Tendered – Schedule B |
| --- | --- | --- |
| 1 | Name of EPC Contractor |  |
| 2 | Office Address |  |
| 3 | Name of Contact Person |  |
| 4 | Position and Title of Contact Person |  |
| 5 | Contact Details |  |

Table 2-2: Specific EPC Project Experience

| Item No. | Description | Unit | Required Schedule A | Tendered Schedule B |
| --- | --- | --- | --- | --- |
| 1 | Contractor Experience |  |  |  |
| 1.1 | Compliance to Section 2.2 of the Technical Specification. | Yes/No | Tenderer to indicate Yes or No |  |
| 1.2 | Solar PV DC capacity and Battery capacity of one PV-Battery hybrid project completed by EPC Contractor. | kWp/kWh | ≥ 50/100 |  |
| 2 | Project Details from Experience Presented in 1.2 |  |  |  |
| 2.1 | Name of the hybrid project | Name | Tenderer to provide |  |
| 2.2 | Location of the hybrid project | Name | Tenderer to provide |  |
| 2.3 | Photographs | Photos | Tenderer to attach |  |
| 2.4 | Customer contact number | Number | To be provided |  |

## plant Designer and Trainers

- The Contractor ensures that only qualified personnel are included in design, construction, commissioning, operation and maintenance of the Project. The minimum requirements of key personnel for the Project are presented in Table 2-3.

- The Tenderer provides detailed CV of each personnel’s responsible for the works mentioned in Table 2-3.

- If any replacement is required during the Construction and Operation, the Contractor ensures that the replacement has equivalent or higher experience than replaced one.

Table 2-3: Engineering Experience Requirements

| Item No. | Description | Unit | Required Schedule A | Tendered Schedule B |
| --- | --- | --- | --- | --- |
| 1 | Engineering Designers |  |  |  |
| 1.1 | Compliance to Section 3.1.4 of the Technical Specification. | Yes/No | Tenderer to indicate Yes or No |  |
| 1.2 | Civil Engineer work experience | Years | ≥ 3 |  |
| 1.3 | Detailed CV and ECSA certificate of a Professional Civil Engineer | Years | Tenderer to attach |  |
| 1.4 | Electrical Engineer work experience | Years | ≥ 3 |  |
| 1.5 | Detailed CV and ECSA certificate of a Professional Electrical Engineer | Years | Tenderer to attach |  |
| 2 | Trainer – Design, Construction, commissioning and O&M |  |  |  |
| 2.1 | Compliance to Section 2.8 of the Technical Specification. | Yes/No | Tenderer to indicate Yes or No |  |
| 2.2 | Trainer for design, construction and commissioning, operating and Maintenance of PV system | Years | ≥ 2 |  |
| 2.3 | Detailed CV of the Trainer | Years | Tenderer to attach |  |

# plant configuration design

- The Tenderer ensures that the Kriel Solar Carport PV Plant is designed according to all relevant standards, best industry practice and according to the site condition. The design complies to the technical specification requirements.

Table 3-1: Kriel Carport PV System Design

| Item No. | Description | Unit | Required Schedule A | Tendered Schedule B |
| --- | --- | --- | --- | --- |
| 1 | Basic Design Conditions |  |  |  |
| 1.1 | Compliance to Section 3.1.6.2 and Section 3.1.6.3 of the Technical Specification. | Yes/No | Tenderer to indicate Yes or No |  |
| 1.2 | Design lifetime of the Plant | Years | ≥ 25 |  |
| 2 | PV Capacity and Energy Yield |  |  |  |
| 2.1 | DC capacity | kWp | ≥ 577 |  |
| 2.2 | Nominal AC capacity | kWac | 500 |  |
| 2.3 | Inverter clipping losses | % | ≤ 1 |  |
| 2.4 | Annual Energy yield | GWh | ≥ 1.1GWh |  |
| 3 | Major Components – General Information |  |  |  |
| 3.1 | Total number of PV modules | Number | Tenderer to provide |  |
| 3.2 | Total number of String Inverters | Number | ≤ 5 |  |
| 3.3 | Total number of PV DC-DB | Number | Tenderer to provide |  |
| 3.4 | Number of Lighting fixtures | Number | Tenderer to provide |  |
| 4 | Diagrams and Drawings |  |  |  |
| 4.1 | PV Module Site Layout | Drawing | Tenderer to attach |  |
| 4.2 | PV Simulation Report with Energy yield, System losses and Bill of Material | Report | Tenderer to attach |  |
| 4.3 | Single line diagram | Diagram | Tenderer to attach |  |

- The Tenderer ensures that the Admin Solar Carport PV and BESS Hybrid Plant is designed according to all relevant standards, best industry practice and according to the site condition. The design complies to the technical specification requirements.

Table 3-2: Admin Carport PV/BESS Hybrid System Design

| Item No. | Description | Unit | Required Schedule A | Tendered Schedule B |
| --- | --- | --- | --- | --- |
| 1 | Basic Design Conditions |  |  |  |
| 1.1 | Compliance to Section 3.1.7.3 and Section 3.1.7.4 of the Technical Specification. | Yes/No | Tenderer to indicate Yes or No |  |
| 1.2 | Design lifetime of the plant | Years | ≥ 25 |  |
| 2 | Total PV/Battery Capacity for Admin Building Boards (Board A and Board B) |  |  |  |
| 2.1 | Total PV DC capacity | kWp | ≥ 1334 (2x667kWp) |  |
| 2.2 | Total Nominal Inverter AC capacity | kWac | ≥ 1200 (2x600kWac) |  |
| 2.3 | Inverter clipping losses | % | 0-3% |  |
| 2.4 | Total Annual Energy yield | GWh | ≥ 2.2 GWh |  |
| 2.5 | Total Battery capacity | kWh | ≥ 2400 (2x1200kWh) |  |
| 3 | PV/Battery Capacity per Board |  |  |  |
| 3.1 | PV DC capacity | kWp | ≥ 667 |  |
| 3.2 | Nominal hybrid Inverter AC capacity | kWac | ≥ 600 |  |
| 3.3 | Battery capacity | kWh | ≥ 1200 |  |
| 3.4 | Number of Battery | Number | Tenderer to provide |  |
| 3.5 | Number of DC cabinet - MBMS | Number | 1 |  |
| 3.5 | Number of Hybrid Inverter (1x preferred) | Number | ≤ 4 |  |
| 3.6 | Number of PV Modules | Number | Tenderer to provide |  |
| 3.7 | Number of Lighting fixtures | Number | Tenderer to provide |  |
| 4 | Diagrams and Drawings |  |  |  |
| 4.1 | PV Module Site Layout | Drawing | Tenderer to attach |  |
| 4.2 | PV Simulation Report with Energy yield, System losses and Bill of Material | Report | Tenderer to attach |  |
| 4.3 | Single line diagram | Diagram | Tenderer to attach |  |

# Guarantee on Performance and Availability

- The Contractor provides guarantee on Plant Performance Ratio (PR) and Availability during Provisional Acceptance Test (PAT) and Maintenance Period (FAT) for the Kriel PV Plant.

Table 4-1: Kriel PV Plant Performance Guarantee – From the Contractor

| Item No. | Description | Unit | Required Schedule A | Tendered Schedule B |
| --- | --- | --- | --- | --- |
| 1 | Product information and Compliance |  |  |  |
| 1.1 | Compliance to Section 3.8 of the Technical Specification | Yes/No | Tenderer to indicate Yes or No |  |
| 1.2 | First year guaranteed annual average Performance Ratio | % | ≥ 80 |  |
| 1.3 | Guaranteed pant availability during PAT | % | ≥ 99.5 |  |
| 1.4 | Guaranteed annual average plant availability during maintenance period - FAT | % | ≥ 98 |  |

- Monthly breakdown of First Year Guaranteed Performance Ratio and estimated solar irradiation on module plane is provided in the following table.

Table 4-2: Monthly Breakdown of First Year Guaranteed PR for Kriel PV plant

| Month | Breakdown of first year annual guaranteed PR (%) | Estimated Solar Irradiation on Module Plane (kWh/m2) |
| --- | --- | --- |
| January |  |  |
| February |  |  |
| March |  |  |
| April |  |  |
| May |  |  |
| June |  |  |
| July |  |  |
| August |  |  |
| September |  |  |
| October |  |  |
| November |  |  |
| December |  |  |
| Annual Average |  |  |

- The Contractor provides guarantee on Plant Performance Ratio (PR) and Availability during Provisional Acceptance Test (PAT) and Maintenance Period (FAT) for the Admin PV Plant.

Table 4-3: Admin PV Plant Performance Guarantee – From the Contractor

| Item No. | Description | Unit | Required Schedule A | Tendered Schedule B |
| --- | --- | --- | --- | --- |
| 1 | Product information and Compliance |  |  |  |
| 1.1 | Compliance to Section 3.8 of the Technical Specification | Yes/No | Tenderer to indicate Yes or No |  |
| 1.2 | First year guaranteed annual average Performance Ratio | % | ≥ 80 |  |
| 1.3 | Guaranteed pant availability during PAT | % | ≥ 99.5 |  |
| 1.4 | Guaranteed annual average plant availability during maintenance period - FAT | % | ≥ 98 |  |

- Monthly breakdown of First Year Guaranteed Performance Ratio and estimated solar irradiation on module plane is provided in the following table.

Table 4-4: Monthly Breakdown of First Year Guaranteed PR for Admin PV plant

| Month | Breakdown of first year annual guaranteed PR (%) | Estimated Solar Irradiation on Module Plane (kWh/m2) |
| --- | --- | --- |
| January |  |  |
| February |  |  |
| March |  |  |
| April |  |  |
| May |  |  |
| June |  |  |
| July |  |  |
| August |  |  |
| September |  |  |
| October |  |  |
| November |  |  |
| December |  |  |
| Annual Average |  |  |

# Equipment Warranty

- The Contractor provides equipment warranty according to minimum requirement set in table below.

- The Contractor transfers the ownership of all manufacturer equipment warranties to the Employer during the Substantial Completion of the Project.

Table 5-1: Equipment warranty for Kriel PV Plant

| Equipment | Minimum Warranty Period in Years | Tendered Warranty Period in Years |
| --- | --- | --- |
| PV Module - Product Warranty against Manufacturing defects | 10 |  |
| PV Modules – Performance | 25 |  |
| Mounting structures Duration of warranty (materials) | 10 |  |
| Mounting structures Lifetime design warranty | 25 |  |
| String Inverter | 10 |  |
| Batteries | 10 |  |
| Switchgear | 1 |  |
| CMS Datalogger | 1 |  |

Table 5-2: Equipment warranty for Admin PV/BESS Plant

| Equipment | Minimum Warranty Period in Years | Tendered Warranty Period in Years |
| --- | --- | --- |
| PV Module - Product Warranty against Manufacturing defects | 10 |  |
| PV Modules – Performance | 25 |  |
| Mounting structures Duration of warranty (materials) | 10 |  |
| Mounting structures Lifetime design warranty | 25 |  |
| Hybrid Inverter | 5 |  |
| Batteries | 10 |  |
| Container product warranty | 10 |  |
| Switchgear | 1 |  |
| CMS Datalogger | 1 |  |

# Technical datasheets -  Components

## Civil Works

Table 6-1: Civil Works Technical Specification per Carport

| Item No. | Description | Unit | Required Schedule A | Tendered Schedule B |
| --- | --- | --- | --- | --- |
| 1 | Foundations and Mounting Structure |  |  |  |
| 1.1 | Compliance to Section 3.2 of the Technical Specification | Yes/No | Tenderer to indicate Yes or No |  |
| 2 | Kriel Carport - Mounting Structure requirement |  |  |  |
| 2.1 | Mounting Type (NE and NW) | Type | Cantilever Carport |  |
| 2.2 | Mounting Orientation | ° | 7 - 10° tilt |  |
| 2.3 | Prefabricated Solar Carport | Yes/No | Tenderer to indicate Yes or No |  |
| 2.4 | Structure Material | Steel/Aluminium | Tenderer to provide |  |
| 2.5 | Module mounting (landscape/portrait) | Side | Portrait |  |
| 2.6 | Module Structure waterproofing required | Yes/No | Tenderer to indicate Yes or No |  |
| 2.7 | Single Carport overhang space for EV charger cover/shading | m | ≥ 1.2 |  |
| 2.8 | Mounting structure specification and high-level drawings | - | Tenderer attach |  |
| 2.9 | Detailed Method Statement for execution of civil scope (Site investigations, design steps, construction works, etc.) | Report | Tenderer to attach |  |
| 3 | Admin Carport - Mounting Structure requirement |  |  |  |
| 3.1 | Mounting Type (East-West) | Type | Cantilever Carport |  |
| 3.2 | Mounting Orientation | ° | 7 - 10° tilt |  |
| 3.3 | Prefabricated Solar Carport | Yes/No | Tenderer to indicate Yes or No |  |
| 3.4 | Structure Material | Steel/Aluminium | Tenderer to provide |  |
| 3.5 | # Module mounting (landscape/portrait) | Side | Portrait |  |
| 3.6 | # Module Structure waterproofing required | Yes/No | Tenderer to indicate Yes or No |  |
| 3.7 | # Single Carport overhang space for EV charger cover/shading | m | ≥ 1.2 |  |
| 3.8 | # Mounting structure specification and high-level drawings | - | Tenderer attach |  |

## Electrical Works

### PV Modules

Table 6-2: PV Module Specific Requirement

| Item No. | Description | Unit | Required Schedule A | Tendered Schedule B |
| --- | --- | --- | --- | --- |
| 1 | Product information and Compliance |  |  |  |
| 1.1 | Compliance to Section 3.3.1.1 of the Technical Specification | Yes/No | Tenderer to indicate Yes or No |  |
| 1.2 | Tier 1 Manufacturer (Q3/Q4 2024) | Name | Tenderer to provide |  |
| 1.3 | PV Module technology | Name | Crystalline Silicon technology (mono or poly) |  |
| 1.4 | PV Module Rated Power at STC | Wp | ≥ 545 |  |
| 1.5 | Technical Datasheet of PV Module | Datasheet | Tenderer to attach |  |
| 1.6 | PV Module Installation manual to verify PV Plant module layout | Manual | Tenderer to attach |  |
| 1.7 | PV Module Warranty Conditions | Datasheet | Tenderer to attach |  |

### DC Combiner box (Primary and Secondary)

Table 6-3: DC Combiner Box Requirement

| Item No. | Description | Unit | Required Schedule A | Tendered Schedule B |
| --- | --- | --- | --- | --- |
| 1 | Kriel Carport DC String Box (PV DC-DB) |  |  |  |
| 1.1 | Compliance to Section 3.3.2.1 of the Technical Specification | Yes/No | Tenderer to indicate Yes or No |  |
| 1.2 | Technical Datasheet for DC Circuit Breakers | Datasheet | Tenderer to attach |  |
| 2 | Admin Carport DC Combiner Box |  |  |  |
| 2.1 | Compliance to Section 3.3.3.1 of Technical Specification | Yes/No | Tenderer to indicate Yes or No |  |
| 2.2 | Technical Datasheet for DC Combiner box | Datasheet | Tenderer to attach |  |
| 3 | Admin Carport Additional DC Box (If applicable) |  |  |  |
| 3.1 | Additional Combiner box if required | Yes/No | Tenderer to indicate Yes or No |  |
| 3.2 | Supporting documents | - | Tende Tenderer to attach |  |

### DC Cabling and Connectors

Table 6-4: DC Cabling and Connectors Requirement

| Item No. | Description | Unit | Required Schedule A | Tendered Schedule B |
| --- | --- | --- | --- | --- |
| 1 | DC Cabling Product information and Compliance |  |  |  |
| 1.1 | Compliance to Section 3.3.1.2 of the Technical Specification | Yes/No | Tenderer to indicate Yes or No |  |
| 1.2 | Kriel PV: DC string cable size | mm2 | ≥ 6 |  |
| 1.3 | Admin PV: DC string cable size | mm2 | ≥ 6 |  |
| 1.4 | Admin PV: DC Array cable size | mm2 | Tenderer to provide |  |
| 1.4 | Technical Datasheet for DC Cables | Datasheet | Tenderer to attach |  |
| 2 | DC Cabling Connectors Product information and Compliance |  |  |  |
| 2.1 | Compliance to Section 3.3.1.3 of Technical Specification | Yes/No | Tenderer to indicate Yes or No |  |

### String Inverters

Table 6-5: Kriel Carport String Inverter Requirements

| Item No. | Description | Unit | Required Schedule A | Tendered Schedule B |
| --- | --- | --- | --- | --- |
| 1 | Product information and Compliance |  |  |  |
| 1.1 | Compliance to Section 3.3.2.2 of the Technical Specification | Yes/No | Tenderer to indicate Yes or No |  |
| 1.2 | Listed inverter on Appendix A of Technical Specification | Yes/No | Tenderer to indicate Yes or No |  |
| 1.3 | Inverter NRS097-2-1 certificate provided if not listed | Certificate | Tenderer to attach |  |
| 1.4 | AC output rating per Inverter | kWac | ≥ 100 |  |
| 1.5 | Inverter required to have string current monitoring. | Yes/No | Tenderer to indicate Yes or No |  |
| 1.6 | Inverter has power limit and energy export control function | Yes/No | Tenderer to indicate Yes or No |  |
| 1.7 | Technical Datasheet of the Inverter | Datasheet | Tenderer to attach |  |
| 1.8 | User Manual of the inverter to verify string input limits, current monitoring and power limit function | Datasheet | Tenderer to attach |  |
| 1.9 | Inverter Warranty Conditions | Datasheet | Tenderer to attach |  |

### Hybrid System (BESS)

Table 6-6: Admin Carport BESS Requirements

| Item No. | Description | Unit | Required Schedule A | Tendered Schedule B |
| --- | --- | --- | --- | --- |
| 1 | Hybrid Inverter Product information and Compliance |  |  |  |
| 1.1 | Compliance to Section 3.3.3.2 and Section 3.3.3.3 of the Technical Specification | Yes/No | Tenderer to indicate Yes or No |  |
| 1.2 | Inverter NRS097-2-1 certificate provided in not listed | Certificate | Tenderer to attach |  |
| 1.3 | AC output rating per inverter | kWac | ≥ 150 |  |
| 1.4 | Technical Datasheet of the hybrid Inverter | Datasheet | Tenderer to attach |  |
| 1.5 | Technical Datasheet of the Solar Charger Controller if split from PCS | Datasheet | Tenderer to attach |  |
| 1.6 | User manual of the Hybrid inverter that explains on-grid and off-grid operation | Manual | Tenderer to attach |  |
| 1.7 | Inverter Warranty Conditions | Datasheet | Tenderer to attach |  |
| 2 | Battery Product information and Compliance |  |  |  |
| 2.1 | Compliance to Section 3.3.3.4 of the Technical Specification | Yes/No | Tenderer to indicate Yes or No |  |
| 2.2 | Energy output rating per Battery | kWh | ≥ 14 |  |
| 2.3 | Technical Datasheet of the Battery | Datasheet | Tenderer to provide |  |
| 2.4 | Battery Warranty Conditions | Datasheet | Tenderer to attach |  |
| 2.5 | Technical Datasheet of the DC cabinet | Datasheet | Tenderer to provide |  |
| 3 | BESS Container Product information and Compliance |  |  |  |
| 3.1 | Compliance to Section 3.3.3.5 of the Technical Specification | Yes/No | Tenderer to indicate Yes or No |  |
| 3.2 | Fire protection and Suppression system | Yes/No | Tenderer to indicate Yes or No |  |
| 3.2 | HVAC system | Yes/No | Tenderer to indicate Yes or No |  |
| 4 | Additional Information – To be listed by the Tenderer |  |  |  |
| 4.1 | To be defined by the Tenderer | - | Tenderer to provide |  |

#### AC Cabling

Table 6-7: AC Cabling Requirements

| Item No. | Description | Unit | Required Schedule A | Tendered Schedule B |
| --- | --- | --- | --- | --- |
| 1 | AC Cabling Compliance |  |  |  |
| 1.1 | Compliance to Section 3.3.1.4 of Technical Specification | Yes/No | Tenderer to indicate Yes or No |  |
| 1.2 | Compliance to Eskom 240-56227443 Standard | Yes/No | Tenderer to indicate Yes or No |  |
| 2 | Kriel Carport AC Cabling Product information |  |  |  |
| 2.1 | Three-phase, 4-core cable size (PV AC-DB to PoC Ext-DB) | mm2 | Tenderer to indicate |  |
| 2.2 | Three-phase, 4-core cable size (Inverters to PV AC-DB) | mm2 | Tenderer to indicate |  |
| 2.3 | Three-phase, 4-core cable size (AC-DB to Sub-DB) | mm2 | 120 |  |
| 2.4 | AC Low Voltage Cable catalogue with all cable ratings | Datasheet | Tenderer to attach |  |
| 3 | Admin Carport AC Cabling Product information per Board |  |  |  |
| 3.1 | Three-phase, 4-core cable size (Inverter to PoC/Switching station) | mm2 | Tenderer to indicate |  |
| 3.2 | Three-phase, 4-core cable size (PoC/Switching station to AC-DB) | mm2 | Tenderer to attach |  |
| 3.3 | Three-phase, 4-core cable size (AC-DB to Sub-DB) | mm2 | 240 |  |
| 3.4 | AC Low Voltage Cable catalogue with all cable ratings | Datasheet | Tenderer to attach |  |

#### AC Distribution Boards

Table 6-8: Kriel Carport AC Distribution Board Requirements

| Item No. | Description | Unit | Required Schedule A | Tendered Schedule B |
| --- | --- | --- | --- | --- |
| 1 | AC Distribution Board (PV AC-DB) and Sub-Distribution Board (Sub-DB) |  |  |  |  |
| 1.1 | Compliance to Section 3.3.2.3 of Technical Specification | Yes/No | Tenderer to indicate Yes or No |  |
| 1.2 | 3-phase 4-pole Circuit Breaker for Inverters | A | Tenderer to indicate |  |
| 1.3 | 3-phase 4-pole Circuit Breaker to PoC | A | Tenderer to indicate |  |
| 1.4 | 3-phase 4-pole Circuit Breaker to Sub-DB | A | 250 |  |
| 1.5 | 3-phase 4-pole Circuit Breaker Sub-DB Main | A | 250 |  |
| 1.6 | Anti-islanding relay | Manufacturer | Tenderer to indicate |  |
| 1.7 | Energy Meter | Manufacturer | Tenderer to indicate |  |
| 1.8 | Datasheet for Anti-islanding relay | Datasheet | Tenderer to attach |  |
| 1.9 | Technical Datasheet for Bi-directional Energy Meter | Datasheet | Tenderer to attach |  |
| 2 | Extension Distribution Board at POC |  |  |  |  |
| 2.1 | Compliance to Section 3.3.2.4 of Technical Specification | Yes/No | Tenderer to indicate Yes or No |  |
| 2.2 | 3-phase 4-pole PoC Circuit Breaker | A | Tenderer to indicate |  |
| 2.3 | 3-phase 4-pole Circuit Breaker for EV charger | A | 250 |  |
| 2.4 | Reroute or install new cables from EV charger sub-DB to new Ext-DB | Reuse/New | Tenderer to indicate |  |
| 2.5 | Technical Datasheet for PoC Circuit breakers (MCCBs) | Datasheet | Tenderer to attach |  |
| 2.6 | Technical Datasheet for PoC Bi-directional Energy Meter | Datasheet | Tenderer to attach |  |

Table 6-9: Admin Carport AC Distribution Board Requirements

| Item No. | Description | Unit | Required Schedule A | Tendered Schedule B |
| --- | --- | --- | --- | --- |
| 1 | AC Distribution Board (PV AC-DB) and Sub-Distribution Board (Sub-DB) |  |  |  |
| 1.1 | Compliance to Section 3.3.3.6 of Technical Specification | Yes/No | Tenderer to indicate Yes or No |  |
| 1.2 | 3-phase 4-pole PoC Circuit Breaker | A | Tenderer to indicate |  |
| 1.3 | 3-phase 4-pole Circuit Breaker for EV charger supply | A | 350 |  |
| 1.4 | 3-phase 4-pole Circuit Breaker Sub-DB Main | A | 350 |  |
| 2 | Switching Station - Distribution Board at POC |  |  |  |
| 2.1 | Compliance to Section 3.3.3.7 of the Technical Specification | Yes/No | Tenderer to indicate Yes or No |  |
| 2.2 | BESS/Grid and DG electrical connection proposal with operating philosophy under normal and abnormal conditions | Report | Tenderer to indicate |  |
| 2.3 | Technical Datasheet for PoC Equipment proposed | Datasheet | Tenderer to attach |  |
| 2.4 | Technical Datasheet for PoC Bi-directional Energy Meter | Datasheet | Tenderer to attach |  |
| 3 | Additional Information – To be listed by the Tenderer |  |  |  |
| 3.1 | To be defined by the Tenderer | - | Tenderer to provide |  |

#### Protection

Table 6-10: Earthing, Lightning and Surge Protection Requirements

| Item No. | Description | Unit | Required Schedule A | Tendered Schedule B |
| --- | --- | --- | --- | --- |
| 1 | Earthing Compliance |  |  |  |
| 1.1 | Compliance to Section 3.3.1.5 of the Technical Specification | Yes/No | Tenderer to indicate Yes or No |  |
| 2 | Surge and Lightning Compliance |  |  |  |
| 2.1 | Compliance to Section 3.3.1.6 of the Technical Specification | Yes/No | Tenderer to indicate Yes or No |  |

### Weather Stations

Table 6-11: Weather Station Requirements per Carport

| Item No. | Description | Unit | Required Schedule A | Tendered Schedule B |
| --- | --- | --- | --- | --- |
| 1 | Product information and Compliance |  |  |  |
| 1.1 | Compliance to Section 3.4.2 of Technical Specification | Yes/No | Tenderer to indicate Yes or No |  |
| 1.2 | Number of Weather station per Solar Carport | Number | 1 |  |
| 1.3 | Technical datasheet of Weather Station | Datasheet | Tenderer to attach |  |

## Control and monitoring system

Table 6-12: CMS Requirements

| Item No. | Description | Unit | Required Schedule A | Tendered Schedule B |
| --- | --- | --- | --- | --- |
| 1 | Kriel Carport Product information and Compliance |  |  |  |
| 1.1 | Compliance to Section 3.4.1 and 3.4.3 of Technical Specification | Yes/No | Tenderer to indicate Yes or No |  |
| 1.2 | Technical datasheet of CMS datalogger | Datasheet | Tenderer to attach |  |
| 2 | Admin Carport Product information and Compliance |  |  |  |
| 2.1 | Compliance to Section 3.4.1 and 3.4.4 of Technical Specification | Yes/No | Tenderer to indicate Yes or No |  |
| 2.2 | Technical datasheet of CMS datalogger | Datasheet | Tenderer to attach |  |

## Safety and security

Table 6-13: Fire Protection Specific Requirements

| Item No. | Description | Unit | Required Schedule A | Tendered Schedule B |
| --- | --- | --- | --- | --- |
| 1 | Kriel Carport Product information and Compliance |  |  |  |
| 1.1 | Compliance to Section 3.6 of Technical Specification | Yes/No | Tenderer to indicate Yes or No |  |
| 1.2 | Portable fire extinguishing equipment | Number | Tenderer to indicate |  |
| 2 | Admin Carport Product information and Compliance |  |  |  |
| 2.1 | Compliance to Section 3.6 of Technical Specification | Yes/No | Tenderer to indicate Yes or No |  |
| 2.2 | FDS System | Number | Tenderer to indicate |  |

## INspection, testing and maintenance

Table 6-14: Inspection, Testing and Maintenance Requirements

| Item No. | Description | Unit | Required Schedule A | Tendered Schedule B |
| --- | --- | --- | --- | --- |
| 1 | Product information and Compliance |  |  |  |
| 1.1 | Compliance to Section 3.7 of Technical Specification | Yes/No | Tenderer to indicate Yes or No |  |
| 1.2 | Compliance to Section 3.9 of Technical Specification | Yes/No | Tenderer to indicate Yes or No |  |
| 1.3 | Compliance to Section 3.10 of Technical Specification | Yes/No | Tenderer to indicate Yes or No |  |
| 1.4 | Confirm to provide 12-months maintenance and included on the Tender costing | Yes/No | Tenderer to indicate Yes or No |  |
| 1.5 | Confirm to provide Training and included on the Tender costing | Yes/No | Tenderer to indicate Yes or No |  |

## Spare Parts

- The Contractor includes in his offer all the spare parts for operation and maintenance of the Project presented below.

- The Contractor recommends the additional spare parts if he considers the minimum requirement on spare parts are not sufficient enough for the Project operation for 25 years of period.

- The Employer, at its option, may decide to purchase such additional spare parts subject to schedule of delivery to be agreed with the Contractor.

Table 6-15: Minimum Spare Parts Requirement

| Item No. | Description | Unit | Required Schedule A | Tendered Schedule B |
| --- | --- | --- | --- | --- |
| 1 | PV Modules and Connectors |  |  |  |
| 1.1 | Crystalline Modules | Pcs | 10 |  |
| 1.2 | Pair of module / string connectors (male + female), for each type installed | Pcs | 10 |  |
| 2 | Protective Devices |  |  |  |
| 2.1 | Fuse holder, for each type installed (Admin) | Pcs | 10 |  |
| 2.2 | DC string fuse, for each type installed (Admin) | Pcs | 10 |  |
| 2.3 | DC Disconnect Switch (Admin) | Pcs | 1 |  |
| 2.4 | DC string breaker, for each type installed (Kriel) | Pcs | 1 spare per DC box |  |
| 2.5 | DC SPD, for each type installed | Pcs | 2 |  |
| 2.6 | AC SPD, for each type installed | Pcs | 2 |  |
| 3 | Protective Devices |  |  |  |
| 3.1 | String Inverter (cold reserve), for each type used | pcs | 1 |  |
| 4 | Tools |  |  |  |
| 4.1 | Set of mechanical tools including any for maintenance of mounting structures, cables and connectors | set | 1 |  |
| 4.2 | Set of special tools for major equipment maintenance | set | 1 |  |
| 4.3 | Set of tools required to clean the PV modules | set | 1 |  |

# Project IMPLEMENTATION Schedule

- The Contractor includes Level 2 project implementation schedule along with the Tender returnable.

- In addition to key milestones presented below, the Contractor provides the level 2 schedule (as returnable along with tender application) which must include key milestones of the project as well as schedules for design completion, procurement, installation of each component, commissioning milestones according to the Works information.

- The schedule includes Kriel SPVC and Admin SPVC/BESS Plants.

Table 7-1: Project Implementation Schedule Key Milestones - Requirements

| Item No. | Description | Required Schedule A | Tendered Schedule B |
| --- | --- | --- | --- |
| 1 | Contract Signature | To be defined by the Employer | N/A |
| 2 | Final Design Document Freeze | 30 days after the Contract Signature |  |
| 3 | Start of Site Mobilization | To be defined by the Tenderer |  |
| 4 | Start of Equipment installation | To be defined by the Tenderer |  |
| 5 | Physical completion of installation of Works | To be defined by the Tenderer |  |
| 6 | Mechanical Completion Test (Pre-commissioning) | To be defined by the Tenderer |  |
| 7 | Electrical Completion Test (Cold and Hot commissioning | To be defined by the Tenderer |  |
| 8 | Guaranteed Substantial Completion Date | Not later than 10 months after the Contract Signature |  |

# document management

| Item No. | Description | Unit | Required Schedule A | Tendered Schedule B |
| --- | --- | --- | --- | --- |
| 1 | Product information and Compliance |  |  |  |
| 1.1 | Compliance to Section 4 of Technical Specification and Appendix C. | Yes/No | Tenderer to indicate Yes or No |  |