{"text_format":"3","workbook":"xls","n_sheets":10,"sheets":["Bill Schedule","Bill No 1- LABOUR RATES","Bill No 2 - COC","Bill No 3 - CB","Bill No 4 - TRENCHING","Bill No 5 - CABLING","Bill No 6 - WIREWAYS & ACCE (2)","Bill No 7 - GENERATOR","Bill No 8 - EARTHING","SUMMARY"],"not_rendered":{"external_links":1,"defined_names":7},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Bill Schedule","index":0,"n_rows":37,"n_cols":4,"rows_kept":37,"merged":[[2,0,2,1]],"flags":["formulas_cached_only"]}
[]
[{"$nulls":3}," "]
["Item",null,"Description","No. of Pages"]
[]
[null,null,"SCHEDULE OF RATES - BILL OF QUANTITIES"]
[]
["A",1,"BILL NO 1: LABOUR RATES",1]
[]
[]
["B",2,"BILL NO 2: CERTIFICATE OF COMPLIANCE",1]
[]
[]
["C",3,"BILL NO 3: CHANGEOVER PANELS",12]
[]
[]
["D",4,"BILL NO 4: CABLE TRENCHING",3]
[]
[]
["E",5,"BILL NO 5: CABLE RETICULATION",6]
[]
[]
["F",6,"BILL NO 6: WIREWAYS & ACCESSORIES",6]
[]
[]
["G",7,"BILL NO 7: WIRING",4]
[]
[]
["H",8,"BILL NO 8: GENERATOR",4]
[]
[]
["I",9,"BILL NO 9: EARTHING",4]
[]
[]
[null,10,"BILL SUMMARY",1]
[]
[]
[null,11,"BILL PAGE TOTAL",42]

{"sheet":"Bill No 1- LABOUR RATES","index":1,"n_rows":36,"n_cols":8,"rows_kept":36,"merged":[[0,1,0,7]],"flags":["formulas_cached_only"]}
[]
[null,"Item","Description","Unit","Qty","Supply & Deliver Rate","Overheads","Total"]
[]
[null,null,"ELECTRICAL WORKS"]
["A",null,"BILL OF QUANTITIES: BILL NO 1 OF 9"]
[]
[null,null,"ARTISAN"]
[null,null,"The artisans and technical persons as described below and registered in terms of the Department of Labour, Engineering Council of South Africa."]
[]
[null,null,"Labour rates for work not covered by any scheduled rates:"]
[null,null,"Labour rates for normal working hours to include transport costs:"]
[]
[null,null,"LABOUR RATES"]
[null,null,"(NORMAL WORKING HOURS - 07:00-16:00)"]
[]
["A",1,"Professional Technician or higher (Engineering Council of South Africa)","hrs",1]
["A",2,"Installation Electrician (Wiremans License)","hrs",1]
["A",3,"Electrical Trade Test Artisan","hrs",1]
["A",4,"General Labour Assistant","hrs",1]
["A",5,"Administration Clerk","hrs",1]
["A",7,"Traveling expenses","km",1]
[null,null,"LABOUR RATES FOR AFTER HOURS WORK "]
[]
[null,null,"LABOUR RATES"]
[null,null,"(AFTER NORMAL WORKING HOURS – 16:00-07:00)"]
[]
["A",8,"Professional Technician (Engineering Council of South Africa)","hrs",1]
["A",9,"Installation Electrician (Wiremans License)","hrs",1]
["A",10,"Electrical Trade Test Artisan","hrs",1]
["A",11,"General Labour Assistant","hrs",1]
[]
[]
[]
[]
[]
[null,null,"TOTAL CARRIED TO BILL SUMMARY Page 92 EE"]

{"sheet":"Bill No 2 - COC","index":2,"n_rows":26,"n_cols":8,"rows_kept":26,"merged":[[0,1,0,7]],"flags":["formulas_cached_only"]}
[]
[null,"Item","Description","Unit","Qty","Supply & Deliver Rate","Install Rate","  Amount"]
[]
[null,null,"ELECTRICAL WORKS"]
["B",null,"BILL OF QUANTITIES: BILL NO 2 OF 9"]
[]
[null,null,"CERTIFICATE OF COMPLIANCE"]
[null,null,"Allow for the tesing, commissioning and issuing of the Electrical Compliance Certificate in terms of SANS10142: Wiring Code, latest revision and to be completed by the recognised person in terms of the Wiring Code and Department of Labour."]
[]
["B",1,"Single phase Distribution Board: CoC","No",1]
["B",2,"Three phase Distribution Board: CoC","No",1]
["B",3,"Infra-Red Testing","per day",1]
["B",4,"Testing and fault finding on low voltage(up to 1000V) grade cables using special equipment. (Using a cable fault locator)","per cable",1]
["B",5,"Electrical Warning/Danger Signage (Distribution Board)","No",1]
["B",6,"Power Load logging, analysis and  report on a 230V or 400V system up to 3000A (Low voltage substation and distribution board)","per day",1]
{"$rows_empty":10}
[null,null,"TOTAL CARRIED TO BILL SUMMARY Page 92 EE"]

{"sheet":"Bill No 3 - CB","index":3,"n_rows":74,"n_cols":8,"rows_kept":74,"merged":[[0,1,0,7]],"flags":["formulas_cached_only"]}
[]
[null,"Item","Description","Unit","Qty","Supply & Deliver Rate","Install Rate"," Amount"]
[]
[null,null,"ELECTRICAL WORKS"]
["C",null,"BILL OF QUANTITIES: BILL NO 3 OF 9"]
[]
[null,null,"CHANGEOVER PANEL"]
[]
[null,null,"CHANGEOVER PANEL"]
[]
[null,null,"Supply, deliver and install miniature circuit breakers in accordance with SANS 156. Approved by SABS. The circuit breakers are to be fitted into existing or new distribution boards."]
[]
[null,null,"400Vac LV PANEL inclusive of 100A 4-pole 10kA Socomec remote Auto-Change switch with Deepsea Controller panel (all associated automation controlls shall be built inside the panel) or similar approved, ALL INCLUSIVE i.e. Installation in existing LV Meter Room, Type Testing, Terminations, Busbars, Accessories. Refer to Single Line Diagram and Specifcation for information."]
[]
[null,1,"400Vac LV PANEL inclusive of 200A 4-pole 10kA Socomec remote Auto-Change switch with Deepsea Controller panel (all associated automation controlls shall be built inside the panel) or similar approved, ALL INCLUSIVE i.e. Installation in existing LV Meter Room, Type Testing, Terminations, Busbars, Accessories. Refer to Single Line Diagram and Specifcation for information.","No.",1]
[]
[null,null,"400Vac LV PANEL inclusive of 300A 4-pole 10kA Socomec remote Auto-Change switch with Deepsea Controller panel (all associated automation controlls shall be built inside the panel) or similar approved, ALL INCLUSIVE i.e. Installation in existing LV Meter Room, Type Testing, Terminations, Busbars, Accessories. Refer to Single Line Diagram and Specifcation for information."]
[]
[null,null,"400Vac LV PANEL inclusive of 400A 4-pole 10kA Socomec remote Auto-Change switch with Deepsea Controller panel (all associated automation controlls shall be built inside the panel) or similar approved, ALL INCLUSIVE i.e. Installation in existing LV Meter Room, Type Testing, Terminations, Busbars, Accessories. Refer to Single Line Diagram and Specifcation for information."]
[]
[null,null,"400Vac LV PANEL inclusive of 500A 4-pole 10kA Socomec remote Auto-Change switch with Deepsea Controller panel (all associated automation controlls shall be built inside the panel) or similar approved, ALL INCLUSIVE i.e. Installation in existing LV Meter Room, Type Testing, Terminations, Busbars, Accessories. Refer to Single Line Diagram and Specifcation for information."]
[]
[null,null,"400Vac LV PANEL inclusive of 600A 4-pole 10kA Socomec remote Auto-Change switch with Deepsea Controller panel (all associated automation controlls shall be built inside the panel) or similar approved, ALL INCLUSIVE i.e. Installation in existing LV Meter Room, Type Testing, Terminations, Busbars, Accessories. Refer to Single Line Diagram and Specifcation for information."]
[]
[null,null,"400Vac LV PANEL inclusive of 800A 4-pole 10kA Socomec remote Auto-Change switch with Deepsea Controller panel (all associated automation controlls shall be built inside the panel) or similar approved, ALL INCLUSIVE i.e. Installation in existing LV Meter Room, Type Testing, Terminations, Busbars, Accessories. Refer to Single Line Diagram and Specifcation for information."]
{"$rows_empty":11}
[null,null,"Carried to Collection Page 14EE"]
[null,"Item","Description","Unit","Qty","Supply & Deliver Rate","Install Rate","Amount"]
[null,null,"ELECTRICAL WORKS"]
[null,null,"BILL OF QUANTITIES: BILL NO 3 OF 9"]
[null,null,"COLLECTION"]
[null,null,"CHANGEOVER PANEL"]
[]
[]
[null,null,"Page 3 EE"]
{"$rows_empty":28}
[null,null,"TOTAL CARRIED TO BILL SUMMARY Page 92 EE"]

{"sheet":"Bill No 4 - TRENCHING","index":4,"n_rows":69,"n_cols":8,"rows_kept":69,"merged":[[0,1,0,7]],"flags":["formulas_cached_only"]}
[]
[null,"Item","Description","Unit","Qty","Supply & Deliver Rate","Install Rate"," Amount"]
[]
[null,null,"ELECTRICAL WORKS"]
["D",null,"BILL OF QUANTITIES: BILL NO 4 OF 9"]
[]
[null,null,"CABLE TRENCHING"]
[null,null,"EXCAVATIONS: TRENCHING & BACKFILLING"]
[null,null,"All prices below shall include the excavation of trenches and holes, separating of stones, ground and rock, leveling of trench bed, refill compacting and reparation of all surfaces to their original finish. Trenching shall be calculated using the formula below: (1m3 =  a trench of 600mm deep * 420mm wide * 4m length) (1m3 =  4m linear of trenching)"]
[]
["D",1,"Excavate and backfilling in soft ground(pickable material)","m³",50]
["D",2,"Excavate and backfilling in soft rock","m³",50]
["D",3,"Excavate and backfilling in hard rock","m³",50]
["D",4,"Excavating for cable road crossing and placing 4 x 110m sleeves across road way."]
["D",5,"Backfilling road crossing and reinstating road surface and compaction as before.","m³",50]
["D",6,"Provide sand or stone-free ground complete with handling cost","m³",50]
["D",7,"Compaction of all electrical and telecoms sleeve trenches under hardended surfaces to 95% MOD AASHTO"]
["D",8,"Remove all waste material complete with handling cost","m³",50]
[]
[null,null,"CABLE MARKERS"]
["D",9,"Electrical reinforced concrete cable route marker with inscription as per engineers detail. Dimension: Height: 265mm, Depth: 750mm, "]
[]
[null,null,"Weight: 19.5kg","No",5]
[]
[]
[null,null,"Carried to Collection Page 17EE"]
[null,"Item","Description","Unit","Qty","Supply & Deliver Rate","Install Rate","Amount"]
[]
["D",10,"Electrical concrete cable route marker with inscription as per engineers detail. Dimension: Height: 250mm, Width: 250mm, Depth: 250mm","No",5]
["D",11,"Electrical concrete cable route marker with inscription as per engineers detail. Dimension: Height: 305mm, Width: 305mm, Depth: 152mm, including 101x76mm lead insert for inscription","No",5]
[]
[null,null,"CABLE DANGER TAPE"]
[]
["D",12,"Electrical buried danger tape in compliance with OSHA 1910.144 for marking physical hazards. The tape shall be lightweight and of high visibility safety yellow polyethylene (plastic) with bold black letters(2 inch height). The tape shall be 76mm wide and 0.102mm thick. The cable warning/danger tape shall be placed 150mm above the cables in excavations. ","m",1000]
[]
[null,null,"MANHOLES"]
[]
["D",13,"Electrical manhole 1200x1200x790mm deep with 230mm brick surround, 150mm concrete base and complete with 6mm flush chequer plate and 150mm concrete base. As per Ethewini Electricity: Manhole specifications for cable circuits where there are hardened surfaces. Drawing: SS_Manholes","Item",5]
[]
["D",14,"Electrical manhole 1200x1200x790mm deep with 230mm brick surround, 150mm concrete base and complete with heavy duty polymer plate and 150mm concrete base. As per Ethewini Electricity: Manhole specifications for cable circuits where there are hardened surfaces. Drawing: SS_Manholes","Item",5]
[]
[null,null,"Carried to Collection Page 17EE"]
[null,"Item","Description","Unit","Qty","Supply & Deliver Rate","Install Rate","Amount"]
[]
[null,null,"ELECTRICAL WORKS"]
[null,null,"BILL OF QUANTITIES: BILL NO 4 OF 9"]
[null,null,"COLLECTION"]
[]
[null,null,"CABLE TRENCHING"]
[]
[null,null,"Page 15 EE"]
[null,null,"Page 16 EE"]
{"$rows_empty":15}
[null,null,"CABLE TRENCHING"]
[null,null,"TOTAL CARRIED TO BILL SUMMARY Page 92 EE"]

{"sheet":"Bill No 5 - CABLING","index":5,"n_rows":139,"n_cols":8,"rows_kept":139,"merged":[[0,1,0,7]],"flags":["formulas_cached_only"]}
[]
[null,"Item","Description","Unit","Qty","Supply & Deliver Rate","Install Rate"," Amount"]
[]
[null,null,"ELECTRICAL WORKS"]
["E",null,"BILL OF QUANTITIES: BILL NO 5 OF 9"]
[null,null,"CABLE RETICULATION"]
[]
[null,null,"LOW VOLTAGE CABLING"]
[null,null,"Supply, deliver and install low voltage(600/1000V), PVC insulated, PVC bedded SWA, PVC sheathed, ECC stranded copper conductor cables. Checking of cable and overhead conductor lengths. The Contractor shall check such lengths on site before ordering the cable as he will not be paid for excess cable after the completion of the service. Any allowance for off-cuts shall be made in the unit rates. The final measurements shall be based on the net route length of cables and overhead lines concerned, installed in accordance with the requirements. However, the onus is on the Contractor to prove compliance with the specification. The cabling shall be installed either in excavations, cable trays, trunking, wireways, ground, sleeves, ducts, etc(measured elsewhere) and shall include all necessary fittings, fixtures and accessories required for the works. The cables shall be as per Abedare Cables or equal approved."]
[]
[null,null,"FOUR CORE"]
["E",1,"16mm2","m",1]
["E",2,"25mm2","m",1]
["E",3,"35mm2","m",1]
["E",4,"50mm2","m",1]
["E",5,"70mm2","m",1]
["E",6,"95mm2","m",1]
["E",7,"120mm2","m",1]
["E",8,"150mm2","m",1]
["E",9,"185mm2","m",1]
[]
[null,null,"LOW VOLTAGE CABLE TERMINATIONS"]
[null,null,"Supply, deliver and install low voltage(600/1000V), PVC insulated, PVC bedded SWA, PVC sheathed, ECC stranded copper conductor cable terminations. The terminations shall be for the referred cables specified and shall include for all shrouds, glands, lugs, connections, fittings, fixtures and accessories for the terminations in terms of the relevant SANS guidelines."]
[]
[]
[null,null,"FOUR CORE"]
["E",1,"16mm2","No",1]
["E",2,"25mm2","No",1]
["E",3,"35mm2","No",1]
["E",4,"50mm2","No",1]
["E",5,"70mm2","No",1]
["E",6,"95mm2","No",1]
["E",7,"120mm2","No",1]
["E",8,"150mm2","No",1]
["E",9,"185mm2","No",1]
[]
[null,null,"Aerial Bundle Conductor (ABC) Cable"]
[null,null,"Supply, deliver and install low voltage (600/1000V), XLPE insulated, self supporting copper conductor cable. The terminations shall be for the referred cables specified and shall include for all shrouds, glands, lugs, connections, fittings, fixtures and accessories for the terminations in terms of SANS 1418 part 1 and part 2 The cables shall be as per Abedare Cables or equal approved."]
[]
["E",10,"25mm2","m",1]
["E",11,"35mm2","m",1]
["E",12,"50mm2","m",1]
["E",13,"70mm2","m",1]
["E",14,"95mm2","m",1]
[]
[]
[null,null,"Carried to Collection Page 23 EE"]
[null,"Item","Description","Unit","Qty","Supply & Deliver Rate","Install Rate","Amount"]
[]
[null,null,"LOW VOLTAGE CABLE JOINT KITS"]
[null,null,"Supply, deliver and install epoxy resin joint kits for low voltage (600/1000V) copper insulated, PVC bedded SWA, PVC sheathed, ECC stranded copper conductor cables. The cable joint kits shall be complete with all necessary fittings, fixtures and accessories required for the works. The cable kit shall be IEC/SANS approved. The cable kit shall be as per 3M Scotchcast or equal approved SIZES"]
[]
["E",1,"16mm2 to 35mm2","No",1]
["E",2,"35mm2 to 50mm2","No",1]
["E",3,"50mm2 to 95mm2","No",1]
["E",4,"120mm2 to 150mm2","No",1]
["E",5,"150mm2 to 240mm2","No",1]
[]
[null,null,"JUNCTION BOXES: NORMAL APPLICATIONS"]
[null,null,"Supply, deliver and install junction boxes:normal applications for low voltage(600/1000V), PVC/SWA/PVC copper cables. The junction boxes shall be complete with all necessary, fittings, fixtures, compression glands, connectors, clamps, blanking plugs, accessories, etc to complete the works. The junction boxes shall be as Pratley or equal approved."]
[]
["E",6,"Enviro Junction box - Rectangular standard hinged cover","No",1]
["E",7,"Bottom entry Junction box - standard - for armoured or unarmoured cable. Size 1 - Polycarbonate lid","No",1]
["E",8,"Bottom entry Junction box - standard - for armoured or unarmoured cable. Size 2 - Polycarbonate lid","No",1]
["E",9,"Encono Junction box - No 1","No",1]
["E",10,"Eeze fit - Instrumentation - Junction Box - 0 - standard for unarmoured cable. Polycarbonate lid","No",1]
["E",11,"Klik-Lok Junction Box (Standard) - for unarmoured or armoured cable. Polycarbonate lid","No",1]
["E",12,"Zed Junction box - No 0","No",1]
[]
[]
[]
[]
[]
[null,null,"Carried to Collection Page 23 EE"]
[null,"Item","Description","Unit","Qty","Supply & Deliver Rate","Install Rate","Amount"]
[]
[null,null,"HIGH DENSITY POLYETHYLENE CABLE SLEEVES"]
[null,null,"Supply, deliver and install underground HDPE cable sleeves for low voltage(600/1000V), PVC/SWA/PVC copper cables. The sleeve shall carry the SANS certification mark in respect of South African National Standard SANS 61386-24 : 2005 (type N 450). The sleeves shall be complete with all necessary couplers, seals, plugs, rings, bell mouths, spacer modules, brushes, etc required to complete the works. The sleeve shall be as per Kabelflex or equal approved."]
[]
["E",13,"50mm diameter","m",1]
["E",14,"110mm diameter","m",1]
{"$rows_empty":27}
[null,null,"Carried to Collection Page 23 EE"]
[null,"Item","Description","Unit","Qty","Supply & Deliver Rate","Install Rate","Amount"]
[]
[null,null,"ELECTRICAL WORKS"]
[null,null,"BILL OF QUANTITIES: BILL NO 5 OF 9"]
[]
[null,null,"COLLECTION"]
[null,null,"CABLE RETICULATION"]
[]
[null,null,"Page 18 EE"]
[null,null,"Page 19 EE"]
[null,null,"Page 20 EE"]
[null,null,"Page 21 EE"]
[null,null,"Page 22 EE"]
{"$rows_empty":16}
[null,null,"TOTAL CARRIED TO BILL SUMMARY Page 92 EE"]

{"sheet":"Bill No 6 - WIREWAYS & ACCE (2)","index":6,"n_rows":186,"n_cols":8,"rows_kept":186,"merged":[[0,1,0,7]],"flags":["formulas_cached_only"]}
[]
[null,"Item","Description","Unit","Qty","Supply & Deliver Rate","Install Rate","Amount"]
[null,null,"ELECTRICAL WORKS"]
[null,null,"BILL OF QUANTITIES: BILL NO 6 OF 9"]
[null,null,"WIREWAYS & ACCESSORIES"]
["F",null,"PVC CONDUIT"]
[null,null,"The supply and installation of PVC conduit, prices to include for couplings, saddles, adaptors, spacers, lids, conduit boxes and all bending, gluing and other necessary material. The conduit shall be installed in concrete, walls, ground, brickwork,  roof spaces, against trusses, etc and shall include for all against trusses, etc and shall include for all necessary fittings, fixtures and accessories to complete the installation. The conduit shall comply to SANS 950."]
[]
[null,null,"Chased into brickwork"]
["F",1,"20mm diameter","m",1]
["F",2,"25mm diameter","m",1]
["F",3,"32mm diameter","m",1]
["F",4,"50mm diameter","m",1]
[]
[null,null,"Chased into concrete"]
["F",5,"20mm diameter","m",1]
["F",6,"25mm diameter","m",1]
["F",7,"32mm diameter","m",1]
["F",8,"50mm diameter","m",1]
[]
[null,null,"Cast into concrete"]
["F",9,"20mm diameter","m",1]
["F",10,"25mm diameter","m",1]
["F",11,"32mm diameter","m",1]
["F",12,"50mm diameter","m",1]
["F",13,"100mm diameter sleeve","m",1]
[]
[null,null,"Fixed on surface"]
["F",14,"20mm diameter","m",1]
["F",15,"25mm diameter","m",1]
["F",16,"32mm diameter","m",1]
["F",17,"50mm diameter","m",1]
[]
[null,null,"Carried to Collection Page 29 EE"]
[null,"Item","Description","Unit","Qty","Supply & Deliver Rate","Install Rate","Amount"]
[null,null,"GALVANISED STEEL CONDUIT: BOSAL"]
[null,null,"The supply and installation of galvanised steel conduit, prices to include for couplings, saddles, adaptors, spacers, lids, conduit boxes and all bending, gluing and other necessary material. The conduit shall be installed in concrete, walls, ground, brickwork, roof spaces, against trusses, etc and shall include for all against trusses, etc and shall include for all necessary fittings, fixtures and accessories to complete the installation. The conduit shall comply to SANS 1065 Parts 1 & 2."]
[]
[null,null,"Fixed on surface"]
["F",18,"20mm diameter","m",1]
["F",19,"25mm diameter","m",1]
["F",20,"32mm diameter","m",1]
["F",21,"50mm diameter","m",1]
[]
[null,null,"CONDUIT ACCESSORIES"]
[null,null,"The supply and installation of conduit accessories for PVC and galvanised steel conduit(Bosal). The conduit accessories shall be fitted as per installation details for the conduit. The accessories shall be complete with all screws, adaptors, etc required to complete the installation. The conduit accessories shall comply to SANS 950."]
[]
[null,null,"EXTENSION BOXES"]
[null,null,"All extension boxes shall be of the galvanised steel type and shall be of 1mm thickness. The boxes shall be suitable for standard switches(lights and plugs) application. The boxes shall be in accordance with SANS 1085 and the plates with SANS 1084"]
[]
["F",22,"100 x 100 x 50mm","No",1]
["F",23,"100 x 50 x 50mm","No",1]
["F",24,"100 x 100 x 75mm(back to back)","No",1]
["F",25,"100 x 50 x 75mm(back to back)","No",1]
[]
[null,null,"PVC: CONDUIT BOXES"]
["F",26,"One Way","No",1]
["F",27,"Two Way","No",1]
["F",28,"Three Way","No",1]
["F",29,"Four Way","No",1]
[]
[null,null,"Carried to Collection Page 29 EE"]
[null,"Item","Description","Unit","Qty","Supply & Deliver Rate","Install Rate","Amount"]
[null,null,"FLEXIBLE CONDUIT"]
[null,null,"The supply and installation of flexible conduit accessories for PVC and galvanised steel conduit(Bosal). The flexible conduit shall be complete with all necessary connectors, fittings, fixtures and accessories required for the complete works. The flexible conduit shall comply to SANS 950, SANS 1065"]
[]
[null,null,"PVC: FLEXIBLE CONDUIT (SPRAGUE)"]
["F",30,"20mm diameter","m",1]
["F",31,"25mm diameter","m",1]
["F",32,"32mm diameter","m",1]
["F",33,"50mm diameter","m",1]
["F",34,"75mm diameter","m",1]
[]
[null,null,"GALVANISED STEEL: FLEXIBLE CONDUIT (SPRAGUE)"]
["F",35,"20mm diameter","m",1]
["F",36,"25mm diameter","m",1]
["F",37,"32mm diameter","m",1]
["F",38,"50mm diameter","m",1]
["F",39,"75mm diameter","m",1]
[]
[null,null,"GENERAL"]
[null,null,"The conduit accessories listed below shall be utilised for existing installations. It shall be complete with all necessary screws, fittings, fixtures and accessories to complete the works."]
[]
[null,null,"PVC SADDLES"]
["F",40,"20mm diameter","No",1]
["F",41,"25mm diameter","No",1]
["F",42,"32mm diameter","No",1]
["F",43,"50mm diameter","No",1]
[]
[null,null,"PVC HOSPITAL SADDLES"]
["F",44,"20mm diameter","No",1]
["F",45,"25mm diameter","No",1]
["F",46,"32mm diameter","No",1]
["F",47,"50mm diameter","No",1]
[]
[null,null,"BOSAL SADDLES"]
["F",48,"20mm diameter","No",1]
["F",49,"25mm diameter","No",1]
["F",50,"32mm diameter","No",1]
["F",51,"40mm diameter","No",1]
[]
[null,null,"Carried to Collection Page 29 EE"]
[null,"Item","Description","Unit","Qty","Supply & Deliver Rate","Install Rate","Amount"]
[null,null,"BOSAL HOSPITAL SADDLES"]
["F",52,"20mm diameter","No",1]
["F",53,"25mm diameter","No",1]
["F",54,"32mm diameter","No",1]
["F",55,"50mm diameter","No",1]
[]
[null,null,"PVC COUPLINGS"]
["F",56,"20mm diameter","No",1]
["F",57,"25mm diameter","No",1]
["F",58,"32mm diameter","No",1]
["F",59,"50mm diameter","No",1]
[]
[null,null,"BOSAL COUPLINGS"]
["F",60,"20mm diameter","No",1]
["F",61,"25mm diameter","No",1]
["F",62,"32mm diameter","No",1]
["F",63,"50mm diameter","No",1]
[]
[null,null,"TRUNKING & WIRING DUCT"]
[null,null,"PVC TRUNKING"]
[null,null,"Supply and install PVC compact mini trunking complete with cover plates, tees, angles(internal, external and flat), bends, end caps and all necessary fittings fixtures and accessories required to complete the works. The trunking shall be installed surface on brickwork, slab, concrete, walls, ceilings, etc as required. The trunking shall be as Cabstrut or equal approved."]
[]
["F",64,"YT/1: 16mm x 16mm","m",1]
["F",65,"YT/2: 25mm x 16mm","m",1]
["F",66,"YT/2.5: 25mm x 25mm","m",1]
["F",67,"YT/3: 40mm x 16mm","m",1]
["F",68,"YT/4: 40mm x 25mm","m",1]
["F",69,"YT/5: 40mm x 40mm","m",1]
["F",70,"NBT/4: 100mm x 40mm","m",1]
[]
[null,null,"Carried to Collection Page 29 EE"]
[null,"Item","Description","Unit","Qty","Supply & Deliver Rate","Install Rate","Amount"]
[null,null,"GALVANISED STEEL TRUNKING"]
[null,null,"Supply and install galvanised steel trunking complete with PVC cover plates, tees, angles(internal, external and flat), bends, end caps, bolts, screws, anchors, threaded rods, hangards, anchors, suspension system and all necessary fittings, fixtures and accessories required to complete the works. The trunking shall be installed surface on brickwork, slab, concrete,  walls, ceilings, etc as required. The trunking shall be as Cabstrut or equal approved."]
[]
["F",71,"P2000: 41mm x 41mm x 1mm","m",1]
["F",72,"P8000: 76mm x 76mm x 0.8mm","m",1]
["F",73,"P9800: 127mm x 76mm x 0.8mm","m",1]
[]
[null,null,"CABLE TRAYS"]
[null,null,"Supply and install galvanised steel cable trays complete with tees, bends, elbows, splices, bolts, screws, anchors, threaded rods, hangars, anchors, suspension system and all necessary fittings, fixtures and accessories required to complete the works. The trays shall be installed 300mm from surface on brickwork, slab,  concrete, walls, ceilings, etc as required. The trays shall be as Cabstrut or equal approved."]
[]
[null,null,"LIGHT DUTY"]
["F",74,"103mm x 19mm x 1mm","m",1]
["F",75,"205mm x 19mm x 1.2mm","m",1]
["F",76,"305mm x 19mm x 1.2mm","m",1]
[null,null,"MEDIUM DUTY"]
["F",77,"152mm x 38mm x 1.6mm","m",1]
["F",78,"229mm x 38mm x 1.6mm","m",1]
["F",79,"305mm x 38mm x 1.6mm","m",1]
[null,null,"HEAVY DUTY"]
["F",80,"152mm x 76mm x 1.6mm","m",1]
["F",81,"229mm x 76mm x 1.6mm","m",1]
["F",82,"305mm x 76mm x 1.6mm","m",1]
[]
[null,null,"Carried to Collection Page 29 EE"]
[null,"Item","Description",{"$nulls":4},"Amount"]
[null,null,"ELECTRICAL WORKS"]
[null,null,"BILL OF QUANTITIES: BILL NO 6 OF 9"]
[]
[null,null,"COLLECTION PAGE"]
[null,null,"WIREWAYS & ACCESSORIES"]
[]
[null,null,"Page 24 EE"]
[null,null,"Page 25 EE"]
[null,null,"Page 26 EE"]
[null,null,"Page 27 EE"]
[null,null,"Page 28 EE"]
{"$rows_empty":13}
[null,null,"WIREWAYS & ACCESSORIES"]
[null,null,"TOTAL CARRIED TO BILL SUMMARY Page 92 EE"]

{"sheet":"Bill No 7 - GENERATOR","index":7,"n_rows":179,"n_cols":8,"rows_kept":179,"merged":[[0,1,0,7]],"flags":["formulas_cached_only"]}
[]
[null,"Item","Description","Unit","Qty","Supply & Deliver Rate","Install Rate","Amount"]
[null,null,"ELECTRICAL WORKS"]
[null,null,"BILL OF QUANTITIES: BILL NO 7 OF 9"]
[null,null,"GENERATOR"]
["F"]
[null,null,"Supply and install the Fully Enclosed Outdoor All-Weather Type Diesel Generator set including the cooling system, Trox or equally approved sound attenuation system (special care must be given to the attenuation as the set is proposed in an office environment - <75dB(A) or less at one meter from the set), under unit Double Skin base fuel tank with fully topped-up fuel tank diesel after commissioning, built-in fuel filtration system, stainless steel exhaust system cladded with stainless steel, weather proof painted 3CR12 Canopy and radiator louver, battery and battery charger system and AMF DeepSea control  panel, including cabling and stainless steel cable supports from AMF panel to generator, and remote emergency stop installed on pallisade fence via a P2000 HDG floor mouunted bracket on checmial anchor bolts and wiring included. Refer to the Generator Standard and Technical Specification, and returnable schedule.Generator shall be CUMMINS, PERKINS, CATERPILLAR, SCANIA or other similar approved"]
[]
["F",1,"Supply and install 100kVA, 400/230V, 50Hz standby ","m",100]
["F",2,"Rig into position ","m",100]
["F",3,null,"m",5]
["F",4,"Supply and install 150kVA, 400/230V, 50Hz standby ","m",5]
[null,null,"Rig into position "]
[]
["F",5,"Supply and install 200kVA, 400/230V, 50Hz standby ","m",100]
["F",6,"Rig into position ","m",100]
["F",7,null,"m",5]
["F",8,"Supply and install 300kVA, 400/230V, 50Hz standby ","m",5]
[null,null,"Rig into position "]
[]
["F",9,"Supply and install 400kVA, 400/230V, 50Hz standby ","m",50]
["F",10,"Rig into position ","m",50]
["F",11,null,"m",5]
["F",12,"Supply and install 500kVA, 400/230V, 50Hz standby ","m",5]
["F",13,"Rig into position ","m",5]
[]
[null,null,"Supply and install 800kVA, 400/230V, 50Hz standby "]
["F",14,"Rig into position ","m",300]
[]
[]
[]
[]
[null,null,"Carried to Collection Page 29 EE"]
[null,"Item","Description","Unit","Qty","Supply & Deliver Rate","Install Rate","Amount"]
[null,null,"GALVANISED STEEL CONDUIT: BOSAL"]
[null,null,"The supply and installation of galvanised steel conduit, prices to include for couplings, saddles, adaptors, spacers, lids, conduit boxes and all bending, gluing and other necessary material. The conduit shall be installed in concrete, walls, ground, brickwork, roof spaces, against trusses, etc and shall include for all against trusses, etc and shall include for all necessary fittings, fixtures and accessories to complete the installation. The conduit shall comply to SANS 1065 Parts 1 & 2."]
[]
["F",1,"Generator shall include an audible/visual indication that the generator is running"]
["F",2,"Allowance for the first commissioning of the unit immediately after installation completed.  Commissioning to be witnessed by the User and Engineering Representative.  All consumables included."]
["F",3]
["F",4,"Allowance for commissioning of the unit after connection into the distribution network.  Commissioning to be done in the presence of the User.  All consumables  included."]
[]
[null,null,"Instruction of the User staff for correct operation of the plant complete with the issue of THREE sets of users manuals and A4 short form guidelines on laminated white board."]
[]
[null,null,"GSM Cellular communications unit suitable to transmit a minimum of three alarms to two staff members.  Cost to allow for all cellular registration and initial contract fees."]
["F",{"$error":"#REF!"},"Prepare, certify and submit a full set of as built drawings for each part of the works as described in the document. To be submitted on completion of each section of the contract"]
["F",{"$error":"#REF!"},"100 x 100 x 75mm(back to back)"]
["F",{"$error":"#REF!"},"Builders work"]
[null,null,"Structural Engineer's approval and certification fee of slab and bund wall."]
["F",{"$error":"#REF!"}]
["F",{"$error":"#REF!"},"Allow for the construction of new generator plinth to withstand the "]
["F",{"$error":"#REF!"},"weight of the proposed generator. As per suppliers specification."]
[null,null,"Bund wall to be contructed to contain 110% of diesel in generator"]
[]
[null,null,"Carried to Collection Page 29 EE"]
[null,"Item","Description","Unit","Qty","Supply & Deliver Rate","Install Rate","Amount"]
[null,null,"FLEXIBLE CONDUIT"]
[null,null,"The supply and installation of flexible conduit accessories for PVC and galvanised steel conduit(Bosal). The flexible conduit shall be complete with all necessary connectors, fittings, fixtures and accessories required for the complete works. The flexible conduit shall comply to SANS 950, SANS 1065"]
[]
[null,null,"PVC: FLEXIBLE CONDUIT (SPRAGUE)"]
["F",{"$error":"#REF!"},"20mm diameter","m",15]
["F",{"$error":"#REF!"},"25mm diameter","m",15]
["F",{"$error":"#REF!"},"32mm diameter","m",15]
["F",{"$error":"#REF!"},"50mm diameter","m",15]
["F",{"$error":"#REF!"},"75mm diameter","m",15]
[]
[null,null,"GALVANISED STEEL: FLEXIBLE CONDUIT (SPRAGUE)"]
["F",{"$error":"#REF!"},"20mm diameter","m",15]
["F",{"$error":"#REF!"},"25mm diameter","m",15]
["F",{"$error":"#REF!"},"32mm diameter","m",15]
["F",{"$error":"#REF!"},"50mm diameter","m",15]
["F",{"$error":"#REF!"},"75mm diameter","m",15]
[]
[null,null,"GENERAL"]
[null,null,"The conduit accessories listed below shall be utilised for existing installations. It shall be complete with all necessary screws, fittings, fixtures and accessories to complete the works."]
[]
[null,null,"PVC SADDLES"]
["F",{"$error":"#REF!"},"20mm diameter","No",100]
["F",{"$error":"#REF!"},"25mm diameter","No",100]
["F",{"$error":"#REF!"},"32mm diameter","No",100]
["F",{"$error":"#REF!"},"50mm diameter","No",100]
[]
[null,null,"PVC HOSPITAL SADDLES"]
["F",{"$error":"#REF!"},"20mm diameter","No",100]
["F",{"$error":"#REF!"},"25mm diameter","No",100]
["F",{"$error":"#REF!"},"32mm diameter","No",100]
["F",{"$error":"#REF!"},"50mm diameter","No",100]
[]
[null,null,"BOSAL SADDLES"]
["F",{"$error":"#REF!"},"20mm diameter","No",100]
["F",{"$error":"#REF!"},"25mm diameter","No",100]
["F",{"$error":"#REF!"},"32mm diameter","No",100]
["F",{"$error":"#REF!"},"40mm diameter","No",100]
[]
[null,null,"Carried to Collection Page 29 EE"]
[null,"Item","Description","Unit","Qty","Supply & Deliver Rate","Install Rate","Amount"]
[null,null,"BOSAL HOSPITAL SADDLES"]
["F",{"$error":"#REF!"},"20mm diameter","No",100]
["F",{"$error":"#REF!"},"25mm diameter","No",100]
["F",{"$error":"#REF!"},"32mm diameter","No",100]
["F",{"$error":"#REF!"},"50mm diameter","No",100]
[]
[null,null,"PVC COUPLINGS"]
["F",{"$error":"#REF!"},"20mm diameter","No",100]
["F",{"$error":"#REF!"},"25mm diameter","No",100]
["F",{"$error":"#REF!"},"32mm diameter","No",100]
["F",{"$error":"#REF!"},"50mm diameter","No",100]
[]
[null,null,"BOSAL COUPLINGS"]
["F",{"$error":"#REF!"},"20mm diameter","No",100]
["F",{"$error":"#REF!"},"25mm diameter","No",100]
["F",{"$error":"#REF!"},"32mm diameter","No",100]
["F",{"$error":"#REF!"},"50mm diameter","No",100]
[]
[null,null,"TRUNKING & WIRING DUCT"]
[null,null,"PVC TRUNKING"]
[null,null,"Supply and install PVC compact mini trunking complete with cover plates, tees, angles(internal, external and flat), bends, end caps and all necessary fittings fixtures and accessories required to complete the works. The trunking shall be installed surface on brickwork, slab, concrete, walls, ceilings, etc as required. The trunking shall be as Cabstrut or equal approved."]
[]
["F",{"$error":"#REF!"},"YT/1: 16mm x 16mm","m",50]
["F",{"$error":"#REF!"},"YT/2: 25mm x 16mm","m",50]
["F",{"$error":"#REF!"},"YT/2.5: 25mm x 25mm","m",50]
["F",{"$error":"#REF!"},"YT/3: 40mm x 16mm","m",50]
["F",{"$error":"#REF!"},"YT/4: 40mm x 25mm","m",50]
["F",{"$error":"#REF!"},"YT/5: 40mm x 40mm","m",50]
["F",{"$error":"#REF!"},"NBT/4: 100mm x 40mm","m",50]
[]
[null,null,"Carried to Collection Page 29 EE"]
[null,"Item","Description","Unit","Qty","Supply & Deliver Rate","Install Rate","Amount"]
[null,null,"GALVANISED STEEL TRUNKING"]
[null,null,"Supply and install galvanised steel trunking complete with PVC cover plates, tees, angles(internal, external and flat), bends, end caps, bolts, screws, anchors, threaded rods, hangards, anchors, suspension system and all necessary fittings, fixtures and accessories required to complete the works. The trunking shall be installed surface on brickwork, slab, concrete,  walls, ceilings, etc as required. The trunking shall be as Cabstrut or equal approved."]
[]
["F",{"$error":"#REF!"},"P2000: 41mm x 41mm x 1mm","m",50]
["F",{"$error":"#REF!"},"P8000: 76mm x 76mm x 0.8mm","m",50]
["F",{"$error":"#REF!"},"P9800: 127mm x 76mm x 0.8mm","m",50]
[]
[null,null,"CABLE TRAYS"]
[null,null,"Supply and install galvanised steel cable trays complete with tees, bends, elbows, splices, bolts, screws, anchors, threaded rods, hangars, anchors, suspension system and all necessary fittings, fixtures and accessories required to complete the works. The trays shall be installed 300mm from surface on brickwork, slab,  concrete, walls, ceilings, etc as required. The trays shall be as Cabstrut or equal approved."]
[]
[null,null,"LIGHT DUTY"]
["F",{"$error":"#REF!"},"103mm x 19mm x 1mm","m",50]
["F",{"$error":"#REF!"},"205mm x 19mm x 1.2mm","m",50]
["F",{"$error":"#REF!"},"305mm x 19mm x 1.2mm","m",50]
[null,null,"MEDIUM DUTY"]
["F",{"$error":"#REF!"},"152mm x 38mm x 1.6mm","m",50]
["F",{"$error":"#REF!"},"229mm x 38mm x 1.6mm","m",50]
["F",{"$error":"#REF!"},"305mm x 38mm x 1.6mm","m",50]
[null,null,"HEAVY DUTY"]
["F",{"$error":"#REF!"},"152mm x 76mm x 1.6mm","m",50]
["F",{"$error":"#REF!"},"229mm x 76mm x 1.6mm","m",50]
["F",{"$error":"#REF!"},"305mm x 76mm x 1.6mm","m",50]
[]
[null,null,"Carried to Collection Page 29 EE"]
[null,"Item","Description",{"$nulls":4},"Amount"]
[null,null,"ELECTRICAL WORKS"]
[null,null,"BILL OF QUANTITIES: BILL NO 6 OF 9"]
[]
[null,null,"COLLECTION PAGE"]
[null,null,"WIREWAYS & ACCESSORIES"]
[]
[null,null,"Page 24 EE"]
[null,null,"Page 25 EE"]
[null,null,"Page 26 EE"]
[null,null,"Page 27 EE"]
[null,null,"Page 28 EE"]
{"$rows_empty":13}
[null,null,"WIREWAYS & ACCESSORIES"]
[null,null,"TOTAL CARRIED TO BILL SUMMARY Page 92 EE"]

{"sheet":"Bill No 8 - EARTHING","index":8,"n_rows":143,"n_cols":8,"rows_kept":143,"merged":[[0,1,0,7]],"flags":["formulas_cached_only"]}
[]
[null,"Item","Description","Unit","Qty","Supply & Deliver Rate","Install Rate"," Amount"]
[null,null,"ELECTRICAL WORKS"]
["R",null,"BILL OF QUANTITIES: BILL NO 8 OF 8"]
[null,null,"LIGHTNING & SURGE PROTECTION"]
[null,null,"Supply, deliver and install low voltage surge protection equipment and devices. The equipment shall include all necessary fittings, fixtures and accessories to complete the works. BARE COPPER EARTH CABLE: Supply, deliver and install low voltage(600/1000V), bare, stranded, compacted, copper conductor cables. Checking of cable and overhead conductor lengths. The Contractor shall check such lengths on site before ordering the cable as he will not be paid for excess cable after the completion of the service. Any allowance for off-cuts shall be made in the unit rates. The final measurements shall be based on the net route length of cables concerned, installed in accordance with the requirements. However, the onus is on the Contractor to prove compliance with the specification. The cabling shall be installed either in excavations, cable trays, trunking, wireways, ground, sleeves, ducts, etc(measured elsewhere) and shall include all necessary fittings, fixtures and accessories required for the works. The cables shall be as per Abedare Cables or equal approved."]
[]
["R",1,"70mm2 Bare Copper earth conductor","m",5]
["R",2,"70mm2 Insulated Copper earth conductor","m",5]
["R",3,"150mm2 Bare Copper earth conductor ","m",5]
["R",4,"150mm2 Insulated Copper earth conductor","m",5]
[]
[null,null,"EARTH ROD (Roof Conductor)"]
[null,null,"Supply, deliver and install low voltage(600/1000V), copper"]
[null,null,"clad, 16mm diameter, 1.8m earth rods, SABS approved. "]
[null,null,"The rods shall be complete with all terminations, double nuts,"]
[null,null,"washers, coupling, clamps, etc required for the works."]
["R",5,"1.8m Copper Earth Rod","No",5]
["R",6,"Extensible copper earth electrodes into ground mech"]
[null,null,"driving, incl cpl driv blt","No",5]
["R",7,"50mm2 Aluminium roof conductor insulated on roof including "]
[null,null,"Aluminium fixing accessories","No",5]
[]
[null,null,"Carried to Collection Page 85 EE"]
[null,"Item","Description","Unit","Qty","Supply & Deliver Rate","Install Rate"," Amount"]
[]
[null,null,"GENERAL ITEMS"]
["R",8,"Sealing of joints with Denso tapes","No",5]
[null,null,"Joining of various round/flat copper conductors by"]
[null,null,"means of bolting, brazing or exothermic bonds"]
["R",9,"Brass clamps termination to copper cable and to the"]
[null,null,"top of the earth electrodes","No",5]
["R",10,"Bonding of air termination conductor between, roof, gutters, etc","No",5]
["R",11,"Bi-Metallic test joint between d/c system and earth","No",5]
["R",12,"Re-inforcing brass bracket complete with galvanised"]
[null,null,"steel wire, U bolt, brass terminal","No",5]
["R",13,"Lightning protection points test in SIS Duo york box  complete "]
[null,null,"with PVC sliding lid, stainless steel screws and engraved cover.","No",5]
["R",14,"Allow for visiting of the site and the carrying out of the required  "]
[null,null,"pre resistivity tests, risk assessments and the issuing of the test "]
[null,null," results and construction shop drawings to the Engineer prior to "]
[null,null,"the works (earthing & lightning protection system)","Item",5]
["R",15,"Allow for the testing of the completed system and the"]
[null,null,"issue of a prescribed test certificate.","Item",5]
[]
[null,null,"SURGE ARRESTORS"]
[null,null,"Supply, deliver and install indoor surge arrestors in existing or "]
[null,null,"new switchboards."]
[null,null,"The units shall comply with SANS 61643 or VDE 0675."]
[null,null,"The equipment shall include all necessary fittings, fixtures and "]
[null,null,"accessories to complete the works."]
[null,null,"The units shall be as Dehn or equal approved."]
[]
[null,null,"SINGLE PHASE"]
[null,null,"Combined SPDS TYPE 1: Type 1, Class 1"]
["R",16,"Modular combined lightning current and surge arrestor","No",5]
[]
[null,null,"SINGLE PHASE"]
[null,null,"Combined SPDS TYPE 2: Type 2, Class 2"]
["R",17,"Modular combined lightning current and surge arrestor","No",5]
[]
[null,null,"THREE PHASE"]
[null,null,"Combined SPDS TYPE 1: Type 1, Class 1"]
["R",18,"Modular combined lightning current and surge arrestor","No",5]
[]
[null,null,"THREE PHASE"]
[null,null,"Combined SPDS TYPE 2: Type 2, Class 2"]
["R",19,"Modular combined lightning current and surge arrestor","No",5]
[]
[null,null,"Carried to Collection Page 85 EE",{"$nulls":4},0]
[null,"Item","Description","Unit","Qty","Supply & Deliver Rate","Install Rate"," Amount"]
[]
[null,null,"UNDER/OVERVOLTAGE RELAYS"]
[null,null,"Supply, deliver and install under/over voltage relays in existing or "]
[null,null,"new switchboards. The unit shall be complete with all auxillary "]
[null,null,"components, connections, terminations, circuit breakers, etc "]
[null,null,"The unit shall be as per Clearline or equal approved."]
["R",20,"12-00407 Trip-Connect (Single Phase),"]
[null,null,"Single Phase under/overvoltage relay fixed line"]
[null,null,"protection system complete with circuit breaker","Item",5]
[]
["R",21,"12-00409 Trip-Connect 3P (Programmable),"]
[null,null,"Three Phase under/overvoltage relay fixed line"]
[null,null,"protection system complete with circuit breaker","Item",5]
{"$rows_empty":23}
[null,null,"Carried to Collection Page 85 EE",{"$nulls":4},0]
[null,"Item","Description","Unit","Qty","Supply & Deliver Rate","Install Rate"," Amount"]
[]
[null,null,"ELECTRICAL WORKS"]
[null,null,"BILL OF QUANTITIES: BILL NO 18 OF 19"]
[]
[null,null,"COLLECTION"]
[]
[null,null,"LIGHTNING & SURGE PROTECTION"]
[]
[null,null,"Page 82 EE",{"$nulls":4},0]
[null,null,"Page 83 EE",{"$nulls":4},0]
[null,null,"Page 84 EE",{"$nulls":4},0]
{"$rows_empty":21}
[null,null,"LIGHTNING & SURGE PROTECTION"]
[null,null,"TOTAL CARRIED TO BILL SUMMARY Page 92 EE",{"$nulls":4},0]

{"sheet":"SUMMARY","index":9,"n_rows":24,"n_cols":4,"rows_kept":24,"merged":[[0,1,2,2],[0,3,1,3]],"flags":["formulas_cached_only"]}
[]
[]
[]
[null,"Page","Description"," Amount"]
[null,null,"SCHEDULE OF RATES - BILL SUMMARY "]
[]
["A",1,"BILL NO 1: LABOUR RATES"]
[]
["B",2,"BILL NO 2: CERTIFICATE OF COMPLIANCE"]
[]
["C",13,"BILL NO 3: CHANGEOVER PANELS"]
[]
["D",16,"BILL NO 4: CABLE TRENCHING"]
[]
["E",21,"BILL NO 5: CABLE RETICULATION"]
[]
["F",27,"BILL NO 6: WIREWAYS & ACCESSORIES"]
[]
["G",31,"BILL NO 7: GENERATOR"]
[]
["R",83,"BILL NO 8: EARTHING"]
[]
[]
[null,null,"TOTAL EXCLUDING VAT  (CARRIED TO FINAL SUMMARY)"]