| BU/Power Station: | Reviewer Name: Interviewee Name/s: | Date: |
| --- | --- | --- |

| Item No. | Review Item/Review Question | Source of Evidence Required | RACI | Source of Evidence Available Y/N | General Comments Findings / Observations/ AFI’s / Best Practice |
| --- | --- | --- | --- | --- | --- |
| A: FIRE PROTECTION EQUIPMENT PERFORMANCE AND CONDITION |  |  |  |  |  |
| PLANT DESIGN |  |  |  |  |  |
|  | Fixed Fire Protection Systems |  |  |  |  |
|  | The following is a list of the minimum requirements of fixed fire protection as per the Eskom Standard and NFPA. Confirm that fixed fire protection (water/foam/gas) is designed, installed, commissioned and in working order on the following plant: |  |  |  |  |
| A1 | Fuel Handling and Storage – Gas: Liquid Petroleum Gas (LPG) bulk storage vessel | Plant Walk – visual confirmation. | Eng | Y | PM’s available |
| A2 | Fuel Handling and Storage – Gas: Hydrogen bulk storage vessels | Plant Walk – visual confirmation. | Eng | N/A | The project was not completed |
| A3 | Fuel Handling and Storage – Gas: Hydrogen cylinders | Plant Walk – visual confirmation. | Eng | N/A | The project was not completed |
| A4 | Fuel Handling and Storage – Oil: Bulk fuel oil storage tanks | Plant Walk – visual confirmation. | Eng | Y | PM’s available |
| A5 | Fuel Handling and Storage – Oil: Bulk fuel oil pumping (HP and LP) and heating facilities | Plant Walk – visual confirmation. | Eng | Y | PM’s available |
| A6 | Fuel Handling and Storage – Oil: Bulk diesel storage tanks on site | Plant Walk – visual confirmation. | Eng |  |  |
| A7 | Fuel Handling and Storage – Coal: Critical Coal Conveyors | Plant Walk – visual confirmation. | Eng | Y | Defects are reported and PM’s available for hydrants |
| A8 | Fuel Handling and Storage – Coal: Critical Conveying and handling structures | Plant Walk – visual confirmation. | Eng | Y | Defects are reported and PM’s available for hydrants |
| A9 | Fuel Handling and Storage – Coal: Critical Transfer houses | Plant Walk – visual confirmation. | Eng |  |  |
| A10 | Boiler Area: Boiler Face – Oil Burners | Plant Walk – visual confirmation. | Eng |  | PM’s available |
| A11 | Boiler Area: Boiler Feed Pumps (EFP’s and SPFT’s) | Plant Walk – visual confirmation. | Eng | Partial | Defects are reported |
| A12 | Boiler Area: Pulverisers - Mills | Plant Walk – visual confirmation. | Eng | Y | PM’s available for hydrants |
| A13 | Boiler Area: Air Heaters | Plant Walk – visual confirmation. | Eng |  | No fixed fire protection |
| A14 | Turbine Area: Hydraulic Oil Control System | Plant Walk – visual confirmation. | Eng |  | System installation incomplete |
| A15 | Turbine Area: Lubricating Oil Room/Pipe/Pumps | Plant Walk – visual confirmation. | Eng |  | System installation incomplete |
| A16 | Turbine Area: Turbine-generator area (under-floor) | Plant Walk – visual confirmation. | Eng |  | System installation incomplete |
| A17 | Turbine Area: Turbine-generator bearings | Plant Walk – visual confirmation. | Eng |  | System installation incomplete |
| A18 | Turbine Area: Hydrogen seal oil | Plant Walk – visual confirmation. | Eng |  | System installation incomplete |
| A19 | Turbine Area: Oil Pipe gallery | Plant Walk – visual confirmation. | Eng |  | System installation incomplete |
| A20 | Electrical Equipment: Control Room/s | Plant Walk – visual confirmation. | Eng |  |  |
| A21 | Electrical Equipment: Equipment Rooms | Plant Walk – visual confirmation. | Eng | Y | Contract in place for detection system |
| A22 | Electrical Equipment: Switchgear rooms | Plant Walk – visual confirmation. | Eng |  |  |
| A23 | Electrical Equipment: Cable Spreading Rooms | Plant Walk – visual confirmation. | Eng | Y | Defects corrected and the system is charged |
| A24 | Electrical Equipment: Cable Tunnels | Plant Walk – visual confirmation. | Eng | Y | Defects corrected and the system is charged |
| A25 | Electrical Equipment: Generator/Unit/Station Transformers | Plant Walk – visual confirmation. | Eng | Y | PM’s available |
| A26 | Electrical Equipment: Auxiliary Transformers | Plant Walk – visual confirmation. | Eng | Y | Barricaded |
| A27 | Auxiliary Equipment: Emergency Diesel Generators | Plant Walk – visual confirmation. | Eng | Y | Defects reported. WIP update P&ID’s |
| A28 | Auxiliary Equipment: Offices | Plant Walk – visual confirmation. | Eng | N | Contract in place for detection system and fire extinguishers available |
| A29 | Auxiliary Equipment: Workshops | Plant Walk – visual confirmation. | Eng | N | Contract in place for detection system and fire extinguishers available |
| A30 | Auxiliary Equipment: Stores | Plant Walk – visual confirmation. | Eng | N | Detection system |
| A31 | Auxiliary Equipment: Diesel driven fire water pumps | Plant Walk – visual confirmation. | Eng | Y | PM’s available |
| A32 | Auxiliary Equipment: Other diesel driven pumps/compressors | Plant Walk – visual confirmation. | Eng |  |  |
| A33 | Auxiliary Equipment: Auxiliary Boilers | Plant Walk – visual confirmation. | Eng | Y | PM’s available |
| A34 | Auxiliary Equipment: Oil Store | Plant Walk – visual confirmation. | Eng | N | Extinguishers available |
|  | Fire Water Pumps (includes header tanks) |  |  |  |  |
| A35 | Fire pumps status indication signals (Local and DCS alarms) | Plant walk – visual confirmation | Eng |  |  |
| A36 | Confirm worst case flow and pressure requirement for the site – does fire pump design cater for worst case flow and pressure requirement with 100% back-up supply. | Fire water and fire pump capacity report | Eng | N | Project underway to upgrade the fire protection system. Commercial process in progress |
|  | Fire Water Supply |  |  |  |  |
| A37 | Confirm worst case flow and pressure requirement for the site – does water capacity cater for 2 hour dedicated supply. | Fire water and fire pump capacity report | Eng | N | Project underway to upgrade the fire protection system. Commercial process in progress |
| A38 | Is back-up water supply available or can 2 hour water storage be replenished in 8 hours | Fire water and fire pump capacity report | Eng | N | Project underway to upgrade the fire protection system. Commercial process in progress |
|  | Compartmentalisation Integrity |  |  |  |  |
| A39 | Are fire rated compartmentalisation integrity maintained as part of the original design – examples include Turbine Lubrication Oil Room, Battery/Equipment/Switchgear rooms inside turbine hall/boiler house, Auxiliary Bay floor and unit compartmentalisation etc. | Plant Walk – visual confirmation. | Eng |  | Not yet done. To liaise with the contractor. |
|  | Drainage/Bunding/Curbing Integrity |  |  |  |  |
| A40 | Are drainage/bunding/curbing integrity maintained as part of the original design – examples include drainage provided where designed fixed fire protection systems are installed, drainage not blocked, bunding/curbing maintained as per original design etc. | Plant Walk – visual confirmation. | Eng | Y | Drainage and bund walls maintained as per original design. |
|  | Alarming on Fixed Fire Protection System Activation |  |  |  |  |
| A41 | All Pressure switches/Flow Switches supplied as part of fixed fire protection systems interfaced with Fire Detection System to alarm in control room on system activation. | Plant Walk – visual confirmation. | Eng |  | Not all connected |
| EQUIPMENT CONDITION |  |  |  |  |  |
| A42 | Do you do routine inspections on the plant to confirm that fire protection equipment is maintained adequately? | Examples of such documents must be presented. | Eng | Y | PM’s and check sheet |
| A43 | Confirm condition of Fire Doors installed on site? | Plant Walk – visual confirmation. | Eng | Y | Non-compliant fire doors are being replaced as per project schedule. |
| A44 | Confirm condition of Fire Stops/Seals installed on site – mainly in cable spreading areas. | Plant Walk – visual confirmation. | Eng | N |  |
| A45 | Confirm condition of Foam Concentrate on site for foam protection system. | Test certificate to be provided. | Eng | N | Material Safety Data Sheets are obtained upon receipt. |
| A46 | Confirm condition of Fire Water Pumps on site through fire water pump performance tests. | Test Report to be provided. | Eng | Y | Pump curve |
| A47 | Confirm condition/expected life of fire water main supply piping. Example, type of material, expected life, replacement strategy if any etc. | Plant Walk – visual confirmation. System Engineer Evidence provided Test certificate to be provided. | Eng | Y | Run to failure. The main supply piping old and to be replaced during water supplies upgrade. Commercial process in progress. |
| TESTING AND MAINTENANCE |  |  |  |  |  |
| A48 | Are routine inspection, testing and maintenance being performed on the station in accordance with PM requirements? | Examples of such documents must be presented. | Eng | Y | PM’s available |
| A49 | How do you confirm that it is done? | System Engineer Evidence provided | Eng | Y | Completed PM’s are signed by executers. |

| Item No. | Review Item/Review Question | Source of Evidence Required | RACI | Source of Evidence Available Y/N | General Comments Findings / Observations/ AFI’s / Best Practice |
| --- | --- | --- | --- | --- | --- |
| B: FIRE PROTECTION SYSTEM - DOCUMENTATION |  |  |  |  |  |
| DESIGN BASELINE DOCUMENTATION |  |  |  |  |  |
| B1 | In terms of fire protection designs are the following documents available for each of the fixed protection systems: - Isometric drawings of all the systems - Node diagrams and hydraulic calculations - Plant layout drawings (including pump house layout and pipe distribution system) - Drawings showing spray pattern of the systems - P&ID’s of all systems | Examples of such documents must be presented. | Eng | Y | P&ID’s of all system. Excluding the new system or incomplete system. New system has isometric drawing |
| B2 | In terms of fire protection design - do the station have the following: - System description of the fire system - Control philosophy of the fire system - Data sheets of all fire protection equipment. | Examples of such documents must be presented. | Eng | Y | Applicable for new system and old system we have spares list. |
| B3 | Are all of these designs/drawings updated according to current plant layout? | Examples of such documents must be presented. | Eng | Y | P&ID’s 90% complete |
| B4 | Do you have a drawing showing all sectional isolation valves on the fire protection lines and all the hydrants on the system? If you do have a drawing like this – is it updated according to current plant layout? | Examples of such documents must be presented. | Eng | N | Process to be initiated |
| OPERATING AND MAINTENANCE DOCUMENTATION |  |  |  |  |  |
| B5 | Is there a complete (up-to-date) signed fire system maintenance strategy in place? When last was the strategy reviewed? | Examples of such documents must be presented. | Eng | Y | Revised in 2020 |
| B6 | Is the current strategy in line with the Eskom Document 240-54937454 Inspection, Testing and Maintenance of Fire Protection Systems? It the current strategy a comprehensive, complete, good quality document? | Correlation between strategy and Eskom Inspection document needs to be proven. | Eng | Y | Old system and to roll it on new system |
| B7 | Does the strategy incorporate fire protection (active and passive [drains, fire traps, bund walls, fire doors, fire sealing, etc]) in its entirety? | Examples of such documents must be presented. | Eng | Y | Maintenance strategy for fire |
| B8 | Are other disciplines/systems of Fire Risk Management (fire detection, fire and smoke control systems for HVAC, fire fighter equipment, emergency management equipment) also captured in this document to capture integration? | Examples of such documents must be presented. | Eng | Y | Maintenance strategy for fire |
| B9 | If the other disciplines/systems of Fire Risk Management is not in one document (strategy) – is there a separate documents indicating all the interfaced systems (active, passive, detection and fire and smoke control systems for HVAC, fire fighter equipment, emergency management equipment)? | Examples of such documents must be presented. | Eng | N |  |
| B10 | Is the fire protection PM’s in the SAP system? | Examples of such documents must be presented. | Eng | Y | Except newly installed system. Work in progress update P&ID’s |
| B11 | When last have you reviewed the content of the Fire Protection system PM’s? | Examples of such documents must be presented. | Eng | Y | 2017 |
| B12 | Are the current PM’s in line with the current maintenance strategy? | Examples of such documents must be presented. | Eng | Y | PM available |
| B13 | Are the PMs integrated for the interfaced systems – the interfaced systems include active, passive, detection and fire and smoke control systems for HVAC, fire fighter equipment, emergency management equipment. | Examples of such documents must be presented. | Eng | N | To be incorporated in the fire detection and protection contract. |
| B14 | If the PMs are available for the interfaced systems, do the PMs (for testing) incorporate the systematic test procedures as well as the list of people that need to verify and sign off the tests? | Examples of such documents must be presented. | Eng | N | Function outsourced to Sizanani 7. PM available. |
| B15 | Is there a floor plan drawing indicating smoke and fire control equipment related to HVAC (i.e Air Handling Units, Fire Dampers, Fans, Air conditioning)? | Examples of such documents must be presented. | Eng | N | Verify equipment room drawing |
| STANDARDS |  |  |  |  |  |
| B16 | What would you say are the critical standards that you as a system engineer need to follow in your day to day work from a Fire Protection Perspective? | System Engineer is confident in his/her system knowledge and working. | Eng |  | Inspection, testing and maintenance of fire protection system, Fire protection and life safety standard, FPDA standard |

| Item No. | Review Item/Review Question | Source of Evidence Required | RACI | Source of Evidence Available Y/N | General Comments Findings / Observations/ AFI’s / Best Practice |
| --- | --- | --- | --- | --- | --- |
| C: FIRE PROTECTION SYSTEMS – MANAGEMENT & LEADERSHIP |  |  |  |  |  |
| STRUCTURE & STAFFING |  |  |  |  |  |
| C1 | Are you dedicated to fire protection systems on the power station? (Thus you are only responsible for the fire protection systems on the plant?) | System Engineers Responsibilities. | Eng |  | No. Seconded to Auxiliary Engineering from Auxiliary Maintenance |
| C2 | Do you have dedicated maintenance personnel for fire protection on your site? | System Engineer has knowledge of who is looking after his/her system. | Eng | Yes | Auxiliary Maintenance and C&I Maintenance |
| C3 | Are roles and responsibilities clear between Operating, Fire Risk Department and Maintenance in terms of inspections of the fire protection systems? If it is – where is it documented? | Examples of such documents must be presented. | Eng | Yes | HSPPIS004-R4 Impairment Procedure |
| ASSESSMENTS |  |  |  |  |  |
| C4 | Are all fire protection insurance recommendations closed out? | Independent Assessment: Examples of such documents must be presented. | Eng | Y | Worst case fire scenario on commercial process stage. |
| C5 | Is there a plan in place to close out the recommendations? | Independent Assessment: Examples of such documents must be presented. | Eng | Y | ERA’s are raised for big project such as replace of fire doors and worst case fire scenario. |
| C6 | Are all fire protection ERAP’s recommendations closed out? | Independent Assessment: Examples of such documents must be presented. | Eng | Y | Not all closed due to funding issue |
| C7 | Is there a plan in place to close out the recommendations? | Independent Assessment: Examples of such documents must be presented. | Eng | Y | ERA’s at execution phase and other at commercial phase. |
| C8 | Self-assessments have been done on QCP’s, PM’s, inspections, tests etc. (Effectiveness of controls is monitored and periodically assessed.) | Examples of such documents must be presented. | Eng | Y | Performance test done on fire system. Periodical inspection of the system done. |
| FIELD OBSERVATIONS |  |  |  |  |  |
| C9 | Are you doing regular inspections on your plant? | System Engineer is confident in his/her system knowledge and working. | Eng | Y | Verification of the system is done since P&ID’s are being revised. |
| C10 | Are you aware of the systems or equipment that are isolated and the duration that they have been out of service | System Engineer is confident in his/her system knowledge and working | Eng | Y | Impairment process |
| INCIDENT MANAGEMENT |  |  |  |  |  |
| C11 | What are your involvement/responsibilities in fire related incidents on the power station? | System Engineers Responsibilities. | Eng |  | Incident investigation |
| C12 | Is fire related incidents on the power station captured? How are fire related incidents on the power station captured? | Examples of such documents must be presented. | Eng |  | Out of normal process and SAP QIM |
| C13 | How do you do fire related incident trending and analysis on the power station? | Examples of such documents must be presented. | Eng | Y | Weekly report sent Safety Manager |

| Item No. | Review Item/Review Question | Source of Evidence Required | RACI | Source of Evidence Available Y/N | General Comments Findings / Observations/ AFI’s / Best Practice |
| --- | --- | --- | --- | --- | --- |
| D: FIRE PROTECTION SYSTEM: CONTROL |  |  |  |  |  |
| IMPAIRMENTS |  |  |  |  |  |
| D1 | Describe what an “impairment” on the fire protection system means? | System Engineer is confident in his/her system knowledge and working. | Eng | Y | Permission granted to impair a plant |
| D2 | What process is followed when the fire protection system is impaired? | System Engineer is confident in his/her system knowledge and working. | Eng | Y | Verify the impaired system as impairment register. |
| D3 | What role do you play as the fire protection engineer in the impairment process? | System Engineer is confident in his/her system knowledge and working. | Eng | Y | Reinstate fire forum |
| D4 | What documentation (as a minimum) should be produced when a fire protection system is impaired? | Examples of such documents must be presented. | Eng | Y | Impairment certificated are issued. Form A & B |
| D5 | Who is notified (internal to BU and outside of BU) when there is impairment? | System Engineer is confident in his/her system knowledge and working. | Eng | Y | Arnot P/S, Steve Tshwete municipality |
| D6 | How is it monitored and tracked that an impairmhhhent is cleared as quickly as possible? | System Engineer is confident in his/her system knowledge and working. | Eng | Y | Impairment register |
| D7 | What process is used to close an impairment on the fire protection system? | System Engineer is confident in his/her system knowledge and working. | Eng | Y | Impairment are cleared when PSR PTW permit is cleared. |
| QUALITY CONTROL (AFTER TESTS AND MAINTENANCE ON FIRE PROTECTION SYSTEMS) |  |  |  |  |  |
| D8 | Are there any quality control measures taken (QCPs) during maintenance of fire protection system - i.e. to determine if correct spares were used, sprayers/sprinklers and valves are positioned back to original positions etc. | Examples of such documents must be presented. | Eng | N | None |
| D9 | Does integrated testing (discharge tests with all relevant disciplines present) take place on the fire systems – with all disciplines signing after the test? | Examples of such documents must be presented. | Eng | N | Draft for transformer sprinkler system to be registered. |
| D10 | If QCPs/ITPs are being used – does engineering also sign during certain critical maintenance/inspections? | Examples of such documents must be presented. | Eng | N |  |
| MODIFICATIONS |  |  |  |  |  |
| D11 | Describe the process that you follow when doing a modification on the fire protection system? | System Engineer is confident in his/her process knowledge and application. | Eng |  | Engineering change management process |
| D12 | Typically what generic PCM’s would you use during the modification process? | System Engineer is confident in his/her process knowledge and application. | Eng | Y | Engineering change management process |
| D13 | Are updated design baseline documentation available (have you completed the updates) once modifications has been completed? | Examples of such documents must be presented. | Eng | Y | Work in progress to update P&ID’s for new fire protection system |
| SPARES |  |  |  |  |  |
| D14 | Have critical spares for the fire protection system been identified? Has it been documented? | Examples of such documents must be presented. | Eng | Y | Critical spares made stock item |
| D15 | Are the spares for the fire protection system available and do you have holding capacity for critical spares in the stores? | System Engineer is confident in his/her system knowledge and working. (Physically show location in store?) | Eng | Y | Stock item |

| Item No. | Review Item/Review Question | Source of Evidence Required | RACI | Source of Evidence Available Y/N | General Comments Findings / Observations/ AFI’s / Best Practice |
| --- | --- | --- | --- | --- | --- |
| E: FIRE PROTECTION SYSTEM: TRAINING AND QUALIFICATION |  |  |  |  |  |
| KNOWLEDGE AND SKILLS |  |  |  |  |  |
| E1 | Have you attended the Fire and Life Safety Basic Course presented at EAL? | Attendance Register/LSO record of attendance. | Eng | N | No |
| E2 | Do you know where an how to access the Eskom Fire and Life Safety Standards? | Describe/Show where the current/updated standards are accessible. | Eng | Y | Hyperwave |
| E3 | Do you utilise the Eskom Fire and Life Safety Care Group (SCOT) SharePoint site for information, discussions and questions you have on the fire protection systems? | Fire and Life Safety SharePoint site “Top Visitors Report”. | Eng | N | Not yet but in contact with fire system specialist |
| E4 | Do you regularly attend the Generation Fire System Focus Group (chaired by Mbali) as scheduled during the year for networking and information sharing? | Fire System Focus Group Attendance Register. | Eng | N | Not yet |
| E5 | Which fire protection system/s is/are taken as the worst case scenario and why? | System Engineer is aware of system extreme. | Eng |  | - Tubine bearings, AC/DC lubricating oil pump, LP turbine underfloor, Unit lubricating tank, Boiler feed pump, condenser pumps, Emergency diesel generator - Unit transformer, Generator transformer, Turbine transformer |
| E6 | What are the total fire water capacity, flow and pressure requirements for the worst case scenario? | System Engineer is confident in his/her system knowledge and working. | Eng |  | 8596,52 l/min and 461.87 kPa |
| E7 | What is the pumping (duty rating) capacity of fire water? Where is it documented? | System Engineer is confident in his/her system knowledge and working. | Eng |  | 3667.67 l/min at 1200kPa SPP pump performance data sheet |