{"text_format":"3","workbook":"xlsx","n_sheets":1,"sheets":["51HV1210"],"not_rendered":{"images":1,"external_links":1,"defined_names":5},"read":"whole","date_system":"1900"}

{"sheet":"51HV1210","index":0,"n_rows":66,"n_cols":26,"rows_kept":66,"merged":[[0,3,0,13],[0,14,0,15],[0,16,0,23],[0,25,0,26],[1,3,1,13],[1,14,1,15],[1,16,1,26],[2,3,3,13],[2,14,2,15],[2,16,2,20],[2,21,2,22],[2,23,2,26],[3,0,3,2],[3,14,3,15],[3,16,3,26],[4,0,4,2],[4,3,4,13],[4,14,4,15],[4,16,4,26],[6,0,8,2],[6,3,6,7],[6,9,6,13],[6,14,6,19],[6,21,6,26],[7,3,7,8],[7,9,7,13],[7,14,7,19],[7,21,7,26],[8,3,8,7],[8,9,8,13],[8,14,8,20],[8,21,8,26],[9,0,17,2],[9,3,9,7],[9,9,9,13],[9,14,9,19],[9,21,9,22],[9,23,9,24],[9,25,9,26],[10,3,10,7],[10,9,10,13],[10,14,10,16],[10,17,10,20],[10,21,10,22],[10,23,10,24],[10,25,10,26],[11,3,11,7],[11,9,11,13],[11,14,11,18],[11,21,11,22],[11,23,11,24],[11,25,11,26],[12,3,12,7],[12,9,12,13],[12,14,12,19],[12,21,12,22],[12,23,12,24],[12,25,12,26],[13,3,13,7],[13,9,13,13],[13,14,13,19],[13,21,13,22],[13,23,13,24],[13,25,13,26],[14,3,14,7],[14,9,14,13],[14,14,14,19],[14,21,14,22],[14,23,14,24],[14,25,14,26],[15,3,15,7],[15,9,15,13],[15,14,15,19],[15,21,15,26],[16,3,16,7],[16,9,16,13],[16,14,16,19],[16,21,16,26],[17,3,17,7],[17,9,17,13],[17,14,17,19],[17,21,17,26],[18,0,23,2],[18,3,18,7],[18,9,18,13],[18,14,18,19],[18,21,18,26],[19,3,19,7],[19,9,19,13],[19,14,19,19],[19,21,19,26],[20,3,20,7],[20,9,20,13],[20,14,20,19],[20,21,20,26],[21,3,21,7],[21,9,21,13],[21,14,21,19],[21,21,21,26],[22,3,22,7],[22,9,22,13],[22,14,22,19],[22,21,22,26],[23,3,23,7],[23,9,23,13],[23,14,23,19],[23,21,23,26],[24,0,29,2],[24,3,24,7],[24,9,24,13],[24,14,24,19],[24,21,24,26],[25,3,25,7],[25,9,25,13],[25,14,25,19],[25,21,25,26],[26,3,26,7],[26,9,26,13],[26,14,26,19],[26,21,26,26],[27,3,27,7],[27,9,27,13],[27,14,27,20],[27,21,27,26],[28,3,28,7],[28,9,28,13],[28,14,28,20],[28,21,28,26],[29,3,29,7],[29,9,29,13],[29,14,29,19],[29,21,29,26],[30,0,34,2],[30,3,30,7],[30,9,30,13],[30,14,30,19],[30,21,30,26],[31,3,31,7],[31,9,31,13],[31,14,31,19],[31,21,31,26],[32,3,32,7],[32,9,32,13],[32,14,32,19],[32,21,32,26],[33,3,33,7],[33,9,33,13],[33,14,33,20],[33,21,33,26],[34,3,34,7],[34,9,34,12],[34,14,34,19],[34,21,34,26],[35,0,40,2],[35,3,35,7],[35,9,35,13],[35,14,35,19],[35,21,35,26],[36,3,36,7],[36,9,36,13],[36,14,36,19],[36,21,36,26],[37,3,37,7],[37,9,37,13],[37,14,37,19],[37,21,37,26],[38,3,38,7],[38,9,38,13],[38,14,38,19],[38,21,38,26],[39,3,39,7],[39,9,39,13],[39,14,39,19],[39,21,39,26],[40,3,40,8],[40,9,40,13],[40,14,40,20],[40,21,40,26],[41,0,44,2],[41,3,41,7],[41,9,41,13],[41,14,41,19],[41,21,41,26],[42,3,42,8],[42,9,42,13],[42,14,42,19],[42,21,42,26],[43,3,43,7],[43,9,43,13],[43,14,43,19],[43,21,43,26],[44,3,44,7],[44,9,44,13],[44,14,44,19],[44,21,44,26],[45,0,45,2],[50,11,50,13],[56,1,56,26],[57,0,57,1],[57,2,57,4],[57,5,57,11],[57,12,57,14],[57,15,57,17],[57,18,57,20],[57,21,57,23],[57,24,57,26],[58,0,58,1],[58,2,58,4],[58,5,58,11],[58,12,58,14],[58,15,58,17],[58,18,58,20],[58,21,58,23],[58,24,58,26],[59,0,59,1],[59,2,59,4],[59,5,59,11],[59,12,59,14],[59,15,59,17],[59,18,59,20],[59,21,59,23],[59,24,59,26],[60,0,60,1],[60,2,60,4],[60,5,60,11],[60,12,60,14],[60,15,60,17],[60,18,60,20],[60,21,60,23],[60,24,60,26],[61,0,61,1],[61,2,61,4],[61,5,61,11],[61,12,61,14],[61,15,61,17],[61,18,61,20],[61,21,61,23],[61,24,61,26],[62,0,62,1],[62,2,62,4],[62,5,62,11],[62,12,62,14],[62,15,62,17],[62,18,62,20],[62,21,62,23],[62,24,62,26],[63,0,63,1],[63,2,63,4],[63,5,63,11],[63,12,63,14],[63,15,63,17],[63,18,63,20],[63,21,63,23],[63,24,63,26],[64,0,64,26],[65,0,65,26]]}
[{"$nulls":3},"INSTRUMENT DATA SHEET",{"$nulls":10},"Doc No",null,"51-NC091-**-A153",{"$nulls":7},"Rev","01A"]
[{"$nulls":3},"ON / OFF  VALVE",{"$nulls":10},"Item No",null,"51-XV 2056/7/8/9"]
[{"$nulls":14},"Sheet",null,"1 OF 1",{"$nulls":4},"Date",null,"04/08/2022"]
[{"$nulls":14},"Job No",null,"P075.1165"]
[{"$nulls":3},"00-15005-**-A013",{"$nulls":10},"MFD No",null,"23242-EE-5100-13002-**-D201"]
[]
["GENERAL",null,null,"Service",{"$nulls":5},"Petrol",{"$nulls":4},"Line Number",{"$nulls":6},"51-PPP-2317-AB-10\""]
[{"$nulls":3},"Equipment No.",{"$nulls":5},"51-XV 2056/7/8/9",{"$nulls":4},"Line Size & Spec",{"$nulls":6},"10\" / 150# / AB"]
[{"$nulls":3},"Area Classification",{"$nulls":5},"ZONE 2",{"$nulls":4},"Design Pressure & Temperature",{"$nulls":6},"1700 kPag / 65°C"]
["PROCESS CONDITIONS",null,null,"Fluid / Product Type",{"$nulls":5},"Petrol",{"$nulls":4},"Flowing Conditions",{"$nulls":6},"Min",null,"Norm",null,"Max"]
[{"$nulls":3},"Compression Factor",{"$nulls":10},"Flow Rate",null,null,"(NOTE1,2,3,4)"]
[{"$nulls":3},"Molecular Weight",{"$nulls":10},"Inlet Pressure",{"$nulls":5},"kPa(g)"]
[{"$nulls":3},"SP Heat Ratio   Cp/Cv",{"$nulls":10},"Pressure Drop",{"$nulls":5},"kPa"]
[{"$nulls":3},"Density @ F.T.",{"$nulls":4},"kg/m3",812,{"$nulls":4},"Calculated CV"]
[{"$nulls":3},"Viscosity @ F.T.",{"$nulls":4},"mPas",3,{"$nulls":4},"Valve Opening",{"$nulls":5},"%"]
[{"$nulls":3},"Vapour Pressure @ F.T.",{"$nulls":4},"kPa(a)",7,{"$nulls":4},"Max Shut Off Pressure",{"$nulls":5},"kPa","1700"]
[{"$nulls":3},"Critical Pressure",{"$nulls":4},"kPa(a)",{"$nulls":5},"Max Temperature",{"$nulls":5},"°C",65]
[{"$nulls":3},"Corrosive",{"$nulls":10},"Flowing Temperature",{"$nulls":5},"°C",20]
["VALVE BODY",null,null,"Size",{"$nulls":5},"10\"",{"$nulls":4},"Type",{"$nulls":6},"TRIPLE ECENTRIC VALVE"]
[{"$nulls":3},"Face to Face Dimension",{"$nulls":4},"mm",330,{"$nulls":4},"Material",{"$nulls":6},"CARBON STEEL"]
[{"$nulls":3},"Connections",{"$nulls":5},"FLANGED",{"$nulls":4},"Rating",{"$nulls":6},"150# RF ANSI B16.5"]
[{"$nulls":3},"Bonnet Type",{"$nulls":5},"N/A",{"$nulls":4},"Packing"]
[{"$nulls":3},"Stem Material",{"$nulls":10},"Flow Action"]
[{"$nulls":3},"Noise",{"$nulls":4},"dB","<85",{"$nulls":4},"Tight Shutoff Required",{"$nulls":6},"ISO 5208 - RATE A"]
["VALVE TRIM",null,null,"Trim Size",{"$nulls":5},"FULL",{"$nulls":4},"Selected CV",{"$nulls":6},"N/A"]
[{"$nulls":3},"Disk Material",{"$nulls":5},"WCB",{"$nulls":4},"Trim Characterisation",{"$nulls":6},"BUTTERFLY"]
[{"$nulls":3},"Seal Material",{"$nulls":5},"ASTM A240 - UNS SS1803 + H.D.G.",{"$nulls":4},"Guiding"]
[{"$nulls":3},"Trim Material",{"$nulls":5},"THERMANIT 19/15",{"$nulls":4},"Fire Safe     (Required/Selected)",{"$nulls":6},"YES / YES"]
[{"$nulls":3},"Gaskets",{"$nulls":10},"SIL Rating   ",{"$nulls":6},"2/3"]
[]
["ACTUATOR          ( Note 10)",null,null,"Model",{"$nulls":10},"Size"]
[{"$nulls":3},"Type",{"$nulls":5},"Pneumatic",{"$nulls":4},"Hand Wheel",{"$nulls":6},"No"]
[{"$nulls":3},"Action on Air Failure",{"$nulls":5},"Fail Close (Note8)",{"$nulls":4},"Max DP for Actuator Sizing",{"$nulls":5},"kPa",1700]
[{"$nulls":3},"Power Supply",{"$nulls":4},"Vac",{"$nulls":5},"SIL Rating   ",{"$nulls":6},"2/3"]
[{"$nulls":3},"Explosion Protection"]
["ACCESSORIES",null,null,"Air Regulator",{"$nulls":4},"kPa",600,{"$nulls":4},"Max Air Supply",{"$nulls":5},"kPa",850]
[{"$nulls":3},"Solenoid",{"$nulls":5},"Yes",{"$nulls":4},"Limit Switch",{"$nulls":6},"Yes (Open&Close)"]
[{"$nulls":3},"Model Number",{"$nulls":10},"Model Number"]
[{"$nulls":3},"Manufacturer",{"$nulls":10},"Manufacturer"]
[{"$nulls":3},"Explosion Protection",{"$nulls":5},"Ex d",{"$nulls":4},"Explosion Protection",{"$nulls":6},"Ex d"]
[{"$nulls":3},"SIL Rating     ",{"$nulls":5},"2/3",{"$nulls":4},"SIL Rating  ",{"$nulls":6},"2/3"]
["PURCHASING",null,null,"Supplier",{"$nulls":10},"Requisition Number"]
[{"$nulls":3},"Manufacturer",{"$nulls":10},"Purchase Order Number"]
[{"$nulls":3},"Model Number",{"$nulls":10},"Material Master Number",{"$nulls":6},50051523]
[]
["NOTES  :"]
["1 )","Liquid flow rate units: m3/h @ flowing conditions"]
["2)","Gas & Vapour = nm3/h "]
["3)","Steam & Boiler feed water  =  kg/h"]
["4)","Standard reference conditions are:101.33kPa abs @ 0 °C  for gas & vapour flow. "]
["5)","Current revisions are noted with BOLD TEXT."]
["6)","South African Inspection Authority certificates required for all certified equipment"]
["7)","Valve to be supplied with removable body and disc seats."]
["8) ","Valve to close in not less than 60 seconds"]
{"$rows_empty":8}
["01A",null,"2022-08-04",null,null,"P075.1165 - Issued for inquiry "]
["Rev",null,"Date",null,null,"Description",{"$nulls":6},"Originator",null,null,"Chk'd E&I",null,null,"Lead Eng E&I",null,null,"Proc. Eng",null,null,"Approved"]
["PetroSA"]
["SOUTH AFRICA"]