FEZILE DABI DISTRICT MUNICIPALITY

##### MUNICIPAL INFRASTRUCTURE GRANT (MIG)

##### PROGRAMME 2024/23

A CIDB DOCUMENT

BID NO: FDDM/BID NO: 012/2023-24

Project Title:  
DRILLING AND EQUIPPING OF EIGHT NEW BOREHOLES AND REFURBISHING OF TWO EXISTING BOREHOLES IN TWEELING/MAFAHLANENG

| Tenderer |  |
| --- | --- |
| Address of Tenderer |  |
| Telephone |  |
| Facsimile |  |
| Tender Amount |  |
| Completion Period |  |

JUNE 2024

EMPLOYER:	EMPLOYER’S AGENT

Fezile Dabi District Municipality	FLAGG Consulting Engineers PTY ltd

P.O. Box 10	P O Box 864

SASOLBURG, 1947	FRANKFORT, 9830

Telephone	: +27 (016) 970 8600	Telephone	: 058 813 2173

Facsimile	: +27 (016) 970 8733	Facsimile	: 058 813 4254

### FEZILE DABI DISTRICT MUNICIPALITY

DRILLING AND EQUIPPING OF SIX NEW BOREHOLES AND REFURBISHMENT OF TWO EXISTING BOREHILES IN TWEELING/MAFAHLANENG
BID NO: FDDM/BID NO: 012/2023-24

### CONTENTS

THESE DOCUMENTS CONSIST OF THE FOLLOWING:	PAGE

VOLUME I:  TENDERING PROCEDURES

T1.1	:	TENDER PROCEDURE	2
T1.2	:	TENDER DATA 	5
T1.2.1	:	Instructions to Tenderers	5
T1.2.2	: 	Invitation to Bid (MBD 1)	10
T1.2.3	:	Tax Clearance Certificate Requirement (MBD 2)	13
T1.2.4	:	Declaration of Interest (MBD 4)	14
T1.2.5	:	Conditions of Tender Pertaining to Preferential Procurement (MBD 6.1)	17
T1.2.6	: 	Declaration Certificate for Local Production (MBD 6.2)	23
T1.2.7	:	Functionality Summary	27

VOLUME 2:  RETURNABLE DOCUMENTS

T2.1	:	LIST OF RETURNABLE DOCUMENTS	29

C1.1	:	FORM OF OFFER AND ACCEPTANCE (TENDER)	30

C2.2	:	SCHEDULE / BILL OF QUANTITIES	36

T2.2	:	RETURNABLE SCHEDULES	54

T2.2.1	 :	Authority of Signatory	54
T2.2.2	:	Schedule of Plant Available	56
T2.2.3	:	Previous Experience of Tenderer	57
T2.2.4	:	Daywork Schedule	58
T2.2.5	:	Status of Concern Submitting the Tender	60
T2.2.6 	:	Preliminary Programme / Cash Flow Schedule	61
T2.2.7	:	Sub – Contractors Schedule	63
T2.2.8	:	Staffing Profile	64
T2.2.9	:	Alterations by Tenderer	65
T2.2.10	:	Certificate of Tenderer’s Visit to Site	66
T2.2.11	:	Financial Ability to Execute the Project	67
T2.2.12	:	Municipality Rates and Taxes (MBD 8)	68
T2.2.13	: 	Declaration of Bidders Past Supply Chain Management Practices	69
T2.2.14	:	Certificate of Independent Bid Determination (MBD9)	71

VOLUME 3:  CONTRACT

C1.2	:	CONTRACT DATA TO TENDER	75

C1.2.1	:	Schedule of Contract Documents	76

C1.2.2	:	General Conditions of Contract	76

C1.2.3	:	Special Conditions of Contract	77

C2.	:	PRICING DATA	81

C3.	:	PROJECT SPECIFICATION	82

C3.1	:	SCOPE OF WORKS	82

C3.2	:	VARIATIONS ON STANDARDISED SPECIFICATIONS /
		PARTICULAR SPECIFICATION	100

C4	:	SITE INFORMATION	101

ANNEXURE A 	:	PRO FORMA DOCUMENTS	103

ANNEXURE B	:	STANDARDISED / PARTICULAR SPECIFICATIONS	109

ANNEXURE C	:	OCCUPATIONAL HEALTH AND SAFETY	156

ANNEXURE D	:	CONFORMITY WITH EPWP GUIDELINES	198

LIST OF TENDER DRAWINGS

VOLUME 1

TENDERING PROCEDURES
FEZILE DABI DISTRICT MUNICIPALITY

DRILLING AND EQUIPPING OF SIX NEW BOREHOLES AND REFURBISHMENT OF TWO EXISTING BOREHOLES IN TWEELING/MAFAHLANENG

FDDM/BID NO: 012/2023-24

TENDER DOCUMENT

PART T1: TENDERING PROCEDURE

DATA PROVIDED BY THE TENDERER

NAME OF TENDERER:

The legal name of the Contractor

ADDRESS OF TENDERER:

Physical address, postal address and e-mail address where the Contractor will receive notice

TELEPHONE No. :

FAX No. :

AUTHORISED PERSON:

TENDER AMOUNT:		R

TIME FOR COMPLETION:	The Works shall be completed within

State total number of days, weeks, months or years which must include the special non-working days and the year-end break.

# TENDERER: ………………………………………………	DATE: …………………………

COPYRIGHT

NOTICE

# CONDITIONS FOR THE ACQUIRING OR PURCHASE OF THIS DOCUMENT

It is explicitly agreed that any person acquiring or purchasing this document does so with the sole purpose of submitting a bona fide tender in terms of the document and will be prohibited to make public the contents of the document or any part thereof or supply it to or let it be used by any other party other than for the purpose of assistance by such other party in meeting any necessary requirements related to the submission of a bona fide tender in terms of the document.

The copy or transformation of any part of this document in any form or by any process whatsoever, without the written consent of the FLAGG Consulting Engineers is prohibited in terms of the Copy Right Act 98 of 1987 except for the purpose as set out above.

## FLAGG Consulting Engineers

# FRANKFORT

|  | # FEZILE DABI DISTRICT MUNICIPALITY MUNICIPAL MANAGER OFFICE John Vorster Road Phone: 016 970 8600 P O Box 10 Fax: 016 970 8733 SASOLBURG, 1947 E-mail: |
| --- | --- |

(For publication on the Municipal notice board, Newspaper, website and e-tender portal)

Competitive bidding process

| BID No | Bid Description | Evaluation criteria | Contact numbers | Non-refundable document fee | Compulsory Briefing |  | Document availability date |  |  | Closing Date and Time |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| FDDM/BID NO: 012/2023-24 | Drilling and equipping of boreholes in Mafahlaneng/Tweeling CIDB 5CE PE/6CE or Higher Grading certificate. Specific goals: Max. 20 points - Locality: 5 points - Within the boundaries of Mafube LM (5 points); Within the boundaries of Fezile Dabi district (3 points); Within the boundaries of Free State province (1 points); Outside the boundaries of Free State province (0 point). - Youth: 5 Points. - HDI,s : 5 Points. - Women: 5 Points | Functionality 1. Project Experiences- References (contactable) on similar projects: 50 points 2. Personal Capacity & Resources relevant to the scope of work: 30 points 3. Financial Viability: 5 points 4. Letter of good standing: 15 points | Me. Moletsane Morakane (078 778 8495) | R1500.00 | Briefing will be held on 18th June 2024 at 10h00 pm Tweeling Municipal Hall |  | 14/06/2024 |  |  | 24/06/ 2024@ 11:00 am |
| Documents are available from: Supply Chain Management Office; Fezile Dabi District Municipality; John Voster Road, Sasolburg; 1947 from 07:30am to 15:30pm Alternatively, @ www.etenders.gov.za Enquiries to directed to Supply Chain 016 970 8600 Minimum Requirements: - Valid original tax clearance certificates must be attached, or pin supplied. - Certified copy of the company registration / founding certificate must be attached. - Certified copy of the identity document - Municipal rates & taxes account not older than 90 days or Valid lease agreement together with Landlord’s Municipal account must be attached. - CSD registration report does not order than 90 days. - CIDB 5CE PE/6CE or Higher Grading certificate. - Letter of good standing (COIDA) - CVs and professional certificates - Experience and references letters. - Bank rating and latest Annual Financial Statement. - Company Profile - Letter of Authority - Joint Venture Agreement if applicable - No bids will be accepted from person in the service of the state. - No telegraphic, telefax and late bids will be accepted. - Bid will remain valid for 90 days. - All quotations will be evaluated in terms of preferential points system as prescribed in the preferential procurement policy regulation of 2022. Please note: - (a) Section 217 of the Constitution of the Republic of Republic of South Africa requires an organ of state to contract for goods and services in accordance with a system which is fair, equitable, transparent, competitive, and cost effective. (b) No bid (s) will be accepted from a person in the service of the state. (c) No telegraphic, telefax and late bids will be accepted. (d) The lowest bid/proposal will not be accepted, and the Municipality reserves the right to accept where applicable a part of portion of any bid or where possible accepts bids or proposal from multiple bidders. (e) Municipal Supply Chain Management policy and Preferential Procurement policy Framework Act No 5 of 2000 and its regulations (2022) will be applied. - To claim preference points for specific goals. A. locality –Where the tenderer is the owner of the property of the company, shall submit a Municipal rates and taxes registered in the name of the tenderer, where the tenderer is not the owner of the property of the company (A valid lease agreement or Affidavit from the property owner that the address used to claim points is being rented out to the tenderer) B. Youth, Women, Locality and HDIs – The bidders must submit ID documents for them to be able to claim points. Bidders who fail to submit the relevant documents will not get 20 points |  |  |  |  |  | All completed Bid documents to be submitted at: Fezile Dabi District Municipality; Tender Box; John Voster Road, Sasolburg; 1947 |  |  |  |  |
|  |  |  |  |  |  |  |  | Points |  |  |
|  |  |  |  |  |  | Price |  | 80 |  |  |
|  |  |  |  |  |  | Specific Goals |  | 20 |  |  |
|  |  |  |  |  |  | _____________________________ Mr. S THOMAS Municipal Manager Date: ____/_____/______ |  |  |  |  |

### T1.2 	TENDER DATA

### T1.2.1	INSTRUCTIONS TO TENDERERS

1.	ISSUE OF DOCUMENTS

Tender documents will be obtainable from Fezile Dabi District Municipality, John Vorster (Tel: 016 970 8600) on the date as advertised. Only cash shall be accepted.

2.	TENDER DOCUMENTS

Tenderers shall satisfy themselves that the documents are complete and conform to the index.  Should any pages be missing or anything concerning the documents not be clear, the Tenderer shall immediately notify the Engineer, in order to have any discrepancy solved, because neither the Employer nor the Engineer will assume any responsibility for any discrepancies not rectified during the tendering period.

3.	TENDER PROCUDURE

Tenders, completed in full, shall be submitted with all the signatures entered where required.

Tenders are to be entered on the Form of Tender, which shall not be detached from this document.

The complete document, priced and completed in full, with any covering letters, specifications, drawings and data to be supplied by the Tenderer, is to be sealed, marked “BID NO: FDDM/BID NO: 012/2023-24” DRILLING AND EQUIPPING OF SIX NEW BOREHOLES AND REFURBISHMENT OF TWO EXISTING BOREHOLES IN MAHAFAHLANENG /TWEELING” and reach the Fezile Dabi District Municipality, John Vorste before 11h00 on the date as advertised.

4.	RETURNABLE DOCUMENTS

All returnable documents included in these documents shall be completed in full by the Tenderer and signed where required. The complete list of returnable documents is tabled in section T2.1 of the tender document.

Should insufficient space be provided in any returnable document, the Tenderer shall include additional annexures, of the same format as the document.  Should all returnable documents not be completed in full, the tender shall be rendered incomplete and may not be taken into consideration.

5.	CLARIFICATION MEETING

The clarification meeting is compulsory.

The Consulting Engineer will meet prospective tenderers at the venue and on the date as advertised to show prospective tenderers the site.  Prospective tenderers shall arrange their own transport.

6.	TENDER PRICES

Tenderers shall allow in the tender prices for all labour, material, plant and all other matters required to execute and complete the contract in accordance with the contract documents.

7.	VALUE ADDED TAX

All unit rates and lump sum prices entered in the Schedule of Quantities shall exclude Value Added Tax.

Provision has however been made for the addition of Value Added Tax to the extended total in the Summary of the Schedule of Quantities.  This figure including VAT shall be carried over to the Form of Tender.

8.	“RATE ONLY” ITEMS

“Rate only” items shall also be priced by the Tenderer but shall not be included in the extended total.

Where “Rate only” items tend to be excessively high or inappropriate, the Employer shall have the right to notify the Tenderer to afford him the opportunity to rectify these rates.

9.	ALTERNATIVE TENDERS

9.1	ALTERNATIVE SYSTEM PROPOSAL

Alternative tenders will not be accepted.

9.2	ALTERNATIVE ITEMS PROPOSAL

Not applicable

10.	RESOLUTION OF AUTHORITY

If the tender is submitted by a company, it shall be signed by a person authorized to do so. A resolution of authorization, by the directors of the company, shall be submitted with the tender.

If the tender is submitted by a consortium of two or more persons or companies for firms, the following shall be attached:

- The original or certified copy of the agreement setting out the composition of the consortium, the conditions on which it operates as well as the period of validity of the consortium.

- A certificate signed by each member of all participating parties, companies or firms, affording power of attorney to a nominated person.

11.	VALIDITY OF TENDER

The tender shall be valid for the period as stated in the Annexure to the Tenderer.

12.	TELEGRAPHIC TENDERS

Telegraphic tenders will NOT be considered.

13.	WITHDRAWAL OF A TENDER

Any Tenderer has the right to change or withdraw a tender after submission providing, he applies for withdrawal before the closing date and time.

The original tender with the written changes on it will be accepted as the final submission.

After the official closing date and time, a tender will not be allowed to be withdrawn or changed.

Should the successful Tenderer withdraw his tender after the advertised closing date, or after notification that his tender has been accepted, fail to sign the contract in accordance with the Form of tender within a period of 14 days, or an extended time agreed, he will be held responsible for all additional costs incurred in re-advertising the contract and/or the difference in cost incurred by appointing a less favourable Tenderer.

14.	INCOMPLETE TENDERS

Any tender that does not comply with the conditions of tender will be considered incomplete and will be liable for rejection.

15.	TENDER EXPENSES

The Employer will not be held liable for any expenses incurred in preparing and lodging tenders.

16.	ALTERATION OF TENDER BY EMPLOYER

16.1	ARITHMETICAL ERRORS

The responsive tender offers shall be checked for arithmetical errors, which will be corrected in the following manner (Per Government Gazette, 9 June 2004, No 26427):

- Where there is a discrepancy between the amounts in figures and in words, the amount in words shall govern.

- For this schedule / bill of quantities, where there is an error in the line-item total resulting from the product of the unit rate and the quantity, the line-item total shall govern, and the rate shall be corrected. Where there is an obviously gross misplacement of the decimal point in the unit rate, the line-item total as quoted shall govern, and the unit rate will be corrected.

Where there is an error in the total of the prices either because of other corrections required by this checking process or in the tenderer’s addition of prices, the total of the prices shall govern, and the tenderer will be asked to revise selected item prices (and their rates if a bill of quantities applies) to achieve the tendered total of the prices.

16.2	INAPPROPRIATE TENDER PRICES

Should any price or rate seem inappropriate or unacceptable to the Employer, the Employer shall require of the Tenderer the following:

To justify the specific price or rate by doing a financial breakdown of the complete rate, and/or to change the rate or price.

Should a Tenderer refuse to alter any price or rate, the Employer may disqualify the Tender, after 7 days written notification thereof.

17.	ADDITIONAL INFORMATION REQUIRED

The Tenderer shall include with his tender all information, data, design calculations and drawings as may be stipulated in the specification and annexures.

The Employer reserves the right to demand more information where such information as submitted is considered inadequate. The Tenderer shall supply the required supplementary information within 7 days after notification.

All costs incurred during the design of proposals and compilation of the required information, shall be included in the tendered rates.

18.	OWNERSHIP OF TENDER DOCUMENTS

All persons in possession of the Tender Documents, whether Tenders are submitted or not, shall regard the contents of the Documents as private and confidential.

No part of any Document may be reproduced or copied without the prior consent of the Consulting Engineers, FLAGG Consulting Engineers.

19.	TIME OF COMPLETION

The time of completion shall be determined by the tenderer; taking into account all factors, which may influence the construction period.  This shall be entered in the appropriate position in the Summary of Tender as well as the Contract data page 30 of this Tender.

20.	ACCEPTANCE AND REJECTION OF TENDERS

Acceptance of a tender does not imply that the program, construction method or any other item in detail will be accepted in full.  Final drawings for final approval in accordance with the General Conditions of Contract shall be submitted, should that be a requirement of the tender.

Tenders may be rejected if additional requirements are not presented as requested in the tender documents, or if the tender has been qualified, other than indicated in “Alterations by Tenderer”, or if any absurdities is encountered in the form of tender, annexures or bill of quantities.

The Employer is not compelled to accept the lowest or any tender.

21.	REVENUE STAMPS

Any stamp duties related to the contract shall be for the account of the Tenderer.

22.	SECURITY

It is a provision of the contract that the Contractor shall provide the Employer with the “Type of Security” for the due performance of the Contract, as selected in the Contract Data. The time to deliver the guarantee and the liability of the guarantee are stated in the Contract Data (C1.2.4).

23.	VARIATIONS BY THE TENDERER

Should the Tenderer wish to vary any terms of the General Conditions of Contract or Specification, he shall do so in Annexure 1 attached to this document.  In the absence of any entries in this Annexure, the tender will be treated as a tender complying in every respect with the General Conditions and Specification.  Preference will be given, other things being generally equal to tenders entailing a minimum of alterations.

24.	AMBIGUITY

In the event of there being any doubt about any matter or of further information being required, Tenderers are invited to obtain such further information from the Consulting Engineers.

25.	FOREIGN TENDERERS

Tenderers not resident in the Republic of South Africa will supply the name and address of their official agent in the Republic.  Any tender failing to comply with this condition will be rejected.

26.	DISQUALIFICATION AS THE RESULT OF UNJUST INFLUENCING AND CANVASSING

Shall there be any evidence of any unjust influencing or canvassing by the Tenderer his tender will be liable to rejection.

27.	“TIME IS OF THE ESSENCE” (MORA)

Time is an essential element of the Contract.

28.	REDUCTION OF WORK

The Employer reserves the right to withdraw any section of item in the bill of quantities in which case the Contractor will have no claim in this respect.

29.	GENERAL CONDITIONS

29.1.1	The following general conditions are applicable to this tender:

- The Main Contractor must appoint a Community Liaison Officer (CLO) for the entire duration of the Project; the CLO will be identified by the Mafube Local Municipality.

- The Main Contractor may import only key personnel for the execution of the project. All general labour and subcontractors must be locally based within the Mafube Municipal Area.

- A Tender / Quotation submitted by a Company which is in arrears of payment for services provided by the Council, will not be considered.

- Failures to provide and attach to the Tender / Quotation the information required may result in a loss of points or disqualification.

- Tenderers are expected to supply out of own funds an amount for accredited training, which amount is expected to be 2% of tender price. This amount is allowed to be added to item 1.1.9 in the schedule of quantities in the tender document

BID NO: FDDM/BID NO: 012/2023-24							MBD 1

T1.2.2

PART A

INVITATION TO BID

| YOU ARE HEREBY INVITED TO BID FOR REQUIREMENTS OF THE FEZILE DABI DISTRICT MUNICIPALITY |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| BID NUMBER: | BID NO: FDDM/BID NO: 012/2023-24 |  | CLOSING DATE: |  | 25 June 2024 |  |  |  |  |  | CLOSING TIME: |  |  |  |  | 11:00 |
| DESCRIPTION | DRILLING AND EQUIPPING OF SIX NEW BOREHOLES AND REFURBISHMENT OF TWO EXISTING BOREHOLES IN TWEELING/MAFAHLANENG |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| THE SUCCESSFUL BIDDER WILL BE REQUIRED TO FILL IN AND SIGN A WRITTEN CONTRACT FORM (MBD7). |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| BID RESPONSE DOCUMENTS MAY BE DEPOSITED IN THE BID BOX SITUATED AT (STREET ADDRESS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| JOHN VORSTER ROAD |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| SASOLBURG |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1947 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| SUPPLIER INFORMATION |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| NAME OF BIDDER |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| POSTAL ADDRESS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| STREET ADDRESS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TELEPHONE NUMBER |  | CODE |  |  |  |  |  |  | NUMBER |  |  |  |  |  |  |  |
| CELLPHONE NUMBER |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| FACSIMILE NUMBER |  | CODE |  |  |  |  |  |  | NUMBER |  |  |  |  |  |  |  |
| E-MAIL ADDRESS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| VAT REGISTRATION NUMBER |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TAX COMPLIANCE STATUS |  | TCS PIN: |  |  |  |  | OR |  |  | CSD No: |  |  |  |  |  |  |
| B-BBEE STATUS LEVEL VERIFICATION CERTIFICATE [TICK APPLICABLE BOX] |  | Yes No |  |  |  |  | B-BBEE STATUS LEVEL SWORN AFFIDAVIT |  |  |  |  | Yes No |  |  |  |  |
| [A B-BBEE STATUS LEVEL VERIFICATION CERTIFICATE/ SWORN AFFIDAVIT (FOR EMES & QSEs) MUST BE SUBMITTED IN ORDER TO QUALIFY FOR PREFERENCE POINTS FOR B-BBEE] |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| #### ARE YOU THE ACCREDITED REPRESENTATIVE IN SOUTH AFRICA FOR THE GOODS /SERVICES /WORKS OFFERED? |  | Yes No [IF YES ENCLOSE PROOF] |  |  |  |  |  | #### ARE YOU A FOREIGN BASED SUPPLIER FOR THE GOODS /SERVICES /WORKS OFFERED? |  |  |  |  |  |  | Yes No [IF YES, ANSWER PART B:3 ] |  |
| #### TOTAL NUMBER OF ITEMS OFFERED |  |  |  |  |  |  |  | #### TOTAL BID PRICE |  |  |  |  |  |  | R |  |
| #### SIGNATURE OF BIDDER |  | ……………………………… |  |  |  |  |  | #### DATE |  |  |  |  |  |  |  |  |
| #### CAPACITY UNDER WHICH THIS BID IS SIGNED |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| BIDDING PROCEDURE ENQUIRIES MAY BE DIRECTED TO: |  |  |  |  |  | TECHNICAL INFORMATION MAY BE DIRECTED TO: |  |  |  |  |  |  |  |  |  |  |
| DEPARTMENT |  | FINANCE |  |  |  | CONTACT PERSON |  |  |  |  |  |  |  | Me. Moletsane Morakane |  |  |
| CONTACT PERSON |  | M MOEKETSI |  |  |  | TELEPHONE NUMBER |  |  |  |  |  |  |  | (078 778 8495) |  |  |
| TELEPHONE NUMBER |  | 016 970 8709 |  |  |  | FACSIMILE NUMBER |  |  |  |  |  |  |  |  |  |  |
| FACSIMILE NUMBER |  |  |  |  |  | E-MAIL ADDRESS |  |  |  |  |  |  |  | morakanemm@feziledabi.gov.za |  |  |
| E-MAIL ADDRESS |  | mariam@feziledabi.gov.za |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

PART B

TERMS AND CONDITIONS FOR BIDDING

- BID SUBMISSION:

- BIDS MUST BE DELIVERED BY THE STIPULATED TIME TO THE CORRECT ADDRESS. LATE BIDS WILL NOT BE ACCEPTED FOR CONSIDERATION. - ALL BIDS MUST BE SUBMITTED ON THE OFFICIAL FORMS PROVIDED–(NOT TO BE RE-TYPED) - THIS BID IS SUBJECT TO THE PREFERENTIAL PROCUREMENT POLICY FRAMEWORK ACT AND THE PREFERENTIAL PROCUREMENT REGULATIONS, 2017, THE GENERAL CONDITIONS OF CONTRACT (GCC) AND, IF APPLICABLE, ANY OTHER SPECIAL CONDITIONS OF CONTRACT.

- TAX COMPLIANCE REQUIREMENTS

- BIDDERS MUST ENSURE COMPLIANCE WITH THEIR TAX OBLIGATIONS. - BIDDERS ARE REQUIRED TO SUBMIT THEIR UNIQUE PERSONAL IDENTIFICATION NUMBER (PIN) ISSUED BY SARS TO ENABLE THE ORGAN OF STATE TO VIEW THE TAXPAYER’S PROFILE AND TAX STATUS. - APPLICATION FOR THE TAX COMPLIANCE STATUS (TCS) CERTIFICATE OR PIN MAY ALSO BE MADE VIA E-FILING. IN ORDER TO USE THIS PROVISION, TAXPAYERS WILL NEED TO REGISTER WITH SARS AS E-FILERS THROUGH THE WEBSITE WWW.SARS.GOV.ZA. - FOREIGN SUPPLIERS MUST COMPLETE THE PRE-AWARD QUESTIONNAIRE IN PART B:3. - BIDDERS MAY ALSO SUBMIT A PRINTED TCS CERTIFICATE TOGETHER WITH THE BID. - IN BIDS WHERE CONSORTIA / JOINT VENTURES / SUB-CONTRACTORS ARE INVOLVED, EACH PARTY MUST SUBMIT A SEPARATE TCS CERTIFICATE / PIN / CSD NUMBER. - WHERE NO TCS IS AVAILABLE BUT THE BIDDER IS REGISTERED ON THE CENTRAL SUPPLIER DATABASE (CSD), A CSD NUMBER MUST BE PROVIDED.

- QUESTIONNAIRE TO BIDDING FOREIGN SUPPLIERS

- IS THE ENTITY A RESIDENT OF THE REPUBLIC OF SOUTH AFRICA (RSA)? YES NO - DOES THE ENTITY HAVE A BRANCH IN THE RSA? YES NO - DOES THE ENTITY HAVE A PERMANENT ESTABLISHMENT IN THE RSA? YES NO - DOES THE ENTITY HAVE ANY SOURCE OF INCOME IN THE RSA? YES NO - IS THE ENTITY LIABLE IN THE RSA FOR ANY FORM OF TAXATION? YES NO IF THE ANSWER IS “NO” TO ALL OF THE ABOVE, THEN IT IS NOT A REQUIREMENT TO REGISTER FOR A TAX COMPLIANCE STATUS SYSTEM PIN CODE FROM THE SOUTH AFRICAN REVENUE SERVICE (SARS) AND IF NOT REGISTER AS PER 2.3 ABOVE.

NB: FAILURE TO PROVIDE ANY OF THE ABOVE PARTICULARS MAY RENDER THE BID INVALID.

NO BIDS WILL BE CONSIDERED FROM PERSONS IN THE SERVICE OF THE STATE.

SIGNATURE OF BIDDER:					……………………………………………

CAPACITY UNDER WHICH THIS BID IS SIGNED:		……………………………………………

DATE:								…………………………………………...

# T1.2.3

# MBD 2

TAX CLEARANCE CERTFICATE REQUIREMENTS

It is a condition of bid that the taxes of the successful bidder must be in order, or that satisfactory arrangements have been made with South African Revenue Service (SARS) to meet the bidder’s tax obligations.

- In order to meet this requirement bidders are required to complete in full the attached form TCC 001 “Application for a Tax Clearance Certificate” and submit it to any SARS branch office nationally. The Tax Clearance Certificate Requirements are also applicable to foreign bidders / individuals who wish to submit bids.

- SARS will then furnish the bidder with a Tax Clearance Certificate that will be valid for a period of 1 (one) year from the date of approval.

- The original Tax Clearance Certificate must be submitted together with the bid. Failure to submit the original and valid Tax Clearance Certificate will result in the invalidation of the bid. Certified copies of the Tax Clearance Certificate will not be acceptable.

- In bids where Consortia / Joint Ventures / Sub-contractors are involved; each party must submit a separate Tax Clearance Certificate.

- Copies of the TCC 001 “Application for a Tax Clearance Certificate” form are available from any SARS branch office nationally or on the website www.sars.gov.za.

- Applications for the Tax Clearance Certificates may also be made via eFiling. In order to use this provision, taxpayers will need to register with SARS as eFilers through the website www.sars.gov.za.

Please note that the Commissioner for the South African Revenue Service (SARS) will not exercise his discretionary powers in favour of any person with regard to any interest, penalties and / or additional tax leviable due to the late- or underpayment of taxes, duties or levies or the rendition returns by any person as a result of any system not being year 2000 compliant.

[MBD 2]

BID NO: FDDM/BID NO: 012/2023-24

T1.2.4

MBD 4

DECLARATION OF INTEREST

1.	No bid will be accepted from persons in the service of the state.

- Any person, having a kinship with persons in the service of the state, including a blood relationship, may make an offer or offers in terms of this invitation to bid.  In view of possible allegations of favouritism, should the resulting bid, or part thereof, be awarded to persons connected with or related to persons in service of the state, it is required that the bidder or their authorised representative declare their position in relation to the evaluating/adjudicating authority and/or take an oath declaring his/her interest.

3	In order to give effect to the above, the following questionnaire must be completed and submitted with the bid.

3.1	Full Name:   …………………………………………………………………………

3.2	Identity Number:     …………………………………………………………………

3.3	Company Registration Number:   …………………………………………………

3.4	Tax Reference Number:    …………………………………………………………

3.5	VAT Registration Number:   ………………………………………………………

3.6	Are you presently in the service of the state                                                       YES / NO

3.6.1	If so, furnish particulars.

………………………………………………………………

………………………………………………………………

3.7	Have you been in the service of the state for the past                                         YES / NO

twelve months?

    - If so, furnish particulars.

………………………………………………………………

  - Do you, have any relationship (family, friend, other) with persons in the 	 YES / NO

service of the state and who may be involved with the evaluation and

or adjudication of this bid?

3.8.1		If so, furnish particulars.

………………………………………………………………

………………………………………………………………

  - Are you, aware of any relationship (family, friend, other)			      YES / NO

between a bidder and any persons in the service of the state

who may be involved with the evaluation and or adjudication of this bid?

3.9.1	If so, furnish particulars.

…………………………………………………………….

…………………………………………………………….

3.10	Are any of the company’s directors, managers, principal                                        YES / NO

shareholders or stakeholders in service of the state?

3.10.1	If so, furnish particulars.

………………………………………………………………

………………………………………………………………

  - Are any spouse, child or parent of the company’s directors,                                  YES / NO

managers, principal shareholders or stakeholders in service

of the state?

3.11.1	If so, furnish particulars.

………………………………………………………………

………………………………………………………………

3.12	Are any of the company’s directors, managers, principal                                        YES / NO

shareholders or stakeholders in service of the state?

3.12.1	If so, furnish particulars.

………………………………………………………………

………………………………………………………………

3.13   Are any spouse, child or parent of the company’s directors,                                  YES / NO

managers, principal shareholders or stakeholders in service

of the state?

3.13.1	If so, furnish particulars.

………………………………………………………………

………………………………………………………………

CERTIFICATION

I, THE UNDERSIGNED (NAME)     ………………………………………………………………………

CERTIFY THAT THE INFORMATION FURNISHED ON THIS DECLARATION FORM IS CORRECT.

I ACCEPT THAT THE STATE MAY ACT AGAINST ME SHOULD THIS DECLARATION PROVE TO BE

FALSE.

…………………………………..	………………………………………………………………………

Signature	Date

………………………………….	…………………………………………………………………….

Position 	Name of Bidder

# BID NO: FDDM/BID NO: 012/2023-24

# T1.2.5 					MBD 6.1

PREFERENCE POINTS CLAIM FORM IN TERMS OF THE PREFERENTIAL 	PROCUREMENT REGULATIONS 2022

This preference form must form part of all tenders invited.  It contains general information and serves as a claim form for preference points for specific goals.

NB:	BEFORE COMPLETING THIS FORM, TENDERERS MUST STUDY THE GENERAL CONDITIONS, DEFINITIONS AND DIRECTIVES APPLICABLE IN RESPECT OF THE TENDER AND PREFERENTIAL PROCUREMENT REGULATIONS, 2022

- GENERAL CONDITIONS

  - The following preference point systems are applicable to invitations to tender:

- the 80/20 system for requirements with a Rand value of up to R50 000 000 (all applicable taxes included); and

- the 90/10 system for requirements with a Rand value above R50 000 000 (all applicable taxes included).

  - To be completed by the organ of state

(delete whichever is not applicable for this tender).

- The applicable preference point system for this tender is the 90/10 preference point system.

- The applicable preference point system for this tender is the 80/20 preference point system.

- Either the 90/10 or 80/20 preference point system will be applicable in this tender. The lowest/ highest acceptable tender will be used to determine the accurate system once tenders are received.

  - Points for this tender (even in the case of a tender for income-generating contracts) shall be awarded for:

- Price; and

- Specific Goals.

  - To be completed by the organ of state:

The maximum points for this tender are allocated as follows:

|  | POINTS |
| --- | --- |
| PRICE | 80 |
| SPECIFIC GOALS | 20 |
| Total points for Price and SPECIFIC GOALS | 100 |

  - Failure on the part of a tenderer to submit proof or documentation required in terms of this tender to claim points for specific goals with the tender, will be interpreted to mean that preference points for specific goals are not claimed.

  - The organ of state reserves the right to require of a tenderer, either before a tender is adjudicated or at any time subsequently, to substantiate any claim in regard to preferences, in any manner required by the organ of state.

- DEFINITIONS

- “tender” means a written offer in the form determined by an organ of state in response to an invitation to provide goods or services through price quotations, competitive tendering process or any other method envisaged in legislation;

- “price” means an amount of money tendered for goods or services, and includes all applicable taxes less all unconditional discounts;

- “rand value” means the total estimated value of a contract in Rand, calculated at the time of bid invitation, and includes all applicable taxes;

- “tender for income-generating contracts” means a written offer in the form determined by an organ of state in response to an invitation for the origination of income-generating contracts through any method envisaged in legislation that will result in a legal agreement between the organ of state and a third party that produces revenue for the organ of state, and includes, but is not limited to, leasing and disposal of assets and concession contracts, excluding direct sales and disposal of assets through public auctions; and

- “the Act” means the Preferential Procurement Policy Framework Act, 2000 (Act No. 5 of 2000).

- FORMULAE FOR PROCUREMENT OF GOODS AND SERVICES

  - POINTS AWARDED FOR PRICE

3.1.1   THE 80/20 OR 90/10 PREFERENCE POINT SYSTEMS

A maximum of 80 or 90 points is allocated for price on the following basis:

# 80/20	or	90/10

Ps=801-Pt-PminPmin	or	Ps=901-Pt-PminPmin

Where

Ps	=	Points scored for price of tender under consideration

Pt	=	Price of tender under consideration

Pmin	=	Price of lowest acceptable tender

  - FORMULAE FOR DISPOSAL OR LEASING OF STATE ASSETS AND INCOME GENERATING PROCUREMENT

    - POINTS AWARDED FOR PRICE

A maximum of 80 or 90 points is allocated for price on the following basis:

# 80/20	               or	            90/10

Ps=801+Pt-PmaxPmax	or	Ps=901+Pt-PmaxPmax

Where

Ps	=	Points scored for price of tender under consideration

Pt	=	Price of tender under consideration

Pmax	=	Price of highest acceptable tender

4.	POINTS AWARDED FOR SPECIFIC GOALS

4.1 1	Locality of supplier

A portion of the 20/10 points is allocated to promote this goal, the following location categories should be used. The points per level will be determined in the tender specification document.

| Locality of Supplier (Tick One) | Points |
| --- | --- |
| Within the boundaries of Mafube Local Municipality | 5 |
| Within the boundaries of Fezile Dabi District | 3 |
| Within the boundaries of the Free State | 1 |
| Outside of the boundaries of the Free State | 0 |

4.1.1.2 (i) A tenderer must submit their Municipal rates and taxes statement, which is not older than 	three (3) months (90 days);

(ii) or a proof of residence that is signed by the Accounting Officer or delegated official.

(iii) or valid (not expired at closing date) lease agreement which is in the name of the company and signed.

(iv) If the municipal rates and taxes statement is in the Landlord’s or Director’s name an affidavit certified by the commissioner of oaths must be attached indicating that the company/enterprise is operating from the stated addressed, accompanied by their municipal rates and taxes statement.

4.2.2 	Youth ownership

Youth Ownership of the company/enterprise, if a portion of the 20/10 points is allocated to promote this goal, the following ownership percentage categories should be used. The points per percentage category will be determined in the tender specification document.

| Youth Ownership of Company (Youth is 35 years and younger) | Points |
| --- | --- |
| 81 – 100% Youth Owned | 5 |
| 61 – 80% Youth Owned | 4 |
| 41 – 60% Youth Owned | 3 |
| 21 – 40% Youth Owned | 2 |
| 1 – 20% Youth Owned | 1 |
| 0% Youth Owned | 0 |

4.2.2.1 	A tenderer must submit a copy of their company registration and /or shareholder certificate as 	proof.

4.2.3 		Women owned enterprises.

Women Ownership of the company/enterprise, if a portion of the 20/10 points is allocated to promote this goal, the following ownership percentage categories should be used. The points per percentage category will be determined in the tender specification document.

| Women Owned Enterprises | Points |
| --- | --- |
| 51 – 100% Women Owned | 5 |
| 50 – 80% women Owned | 3 |
| Less than 50% Women Owned | 1 |

4.2.3.1 The Identity document together with CIPC registration certificate must be provided as proof.

4.2.4 	HDI’s

| HDI’s (Black, Indians and Coloureds) | Points |
| --- | --- |
| HDI’s | 5 |

4.2.4.1 Provide CSD report form to claim points

4.3 	Specific goals:    =     ……… (maximum of 10 or 20 points)

(Points claimed in respect of the above must be in accordance with the tables reflected 	in 	paragraph 4.1 and must be substantiated by submitting the required documents.

5.	DECLARATIONS WITH REGARD TO COMPANY/FIRM

Name of company/firm:………………………………………………………………

VAT registration number:……………………………………….…………………………

Company registration number:…………….……………………….…………………

  - TYPE OF COMPANY/ FIRM

Partnership/Joint Venture / Consortium

One person business/sole propriety

Close corporation

Company

(Pty) Limited

[Tick applicable box]

  - DESCRIBE PRINCIPAL BUSINESS ACTIVITIES

………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………

5.3	COMPANY CLASSIFICATION

Manufacturer

Supplier

Professional service provider

Other service providers, e.g. transporter, etc.

[Tick applicable box]

  - MUNICIPAL INFORMATION

Municipality where business is situated: ….……………………………………………….

Registered Account Number: ………………………….

Stand Number:……………………………………………….

  - Total number of years the company/firm has been in business:……………………………

  - I/we, the undersigned, who is / are duly authorised to do so on behalf of the company/firm, certify that the points claimed, based on the B-BBE status level of contributor indicated in paragraphs 1.4 and 6.1 of the foregoing certificate, qualifies the company/ firm for the preference(s) shown and I / we acknowledge that:

- The information furnished is true and correct;

- The preference points claimed are in accordance with the General Conditions as indicated in paragraph 1 of this form;

- In the event of a contract being awarded as a result of points claimed as shown in paragraphs 1.4 and 6.1, the contractor may be required to furnish documentary proof to the satisfaction of the purchaser that the claims are correct;

- If the B-BBEE status level of contributor has been claimed or obtained on a fraudulent basis or any of the conditions of contract have not been fulfilled, the purchaser may, in addition to any other remedy it may have –

  - disqualify the person from the bidding process;

  - recover costs, losses or damages it has incurred or suffered as a result of that person’s conduct;

  - cancel the contract and claim any damages which it has suffered as a result of having to make less favourable arrangements due to such cancellation;

  - recommend that the bidder or contractor, its shareholders and directors, or only the shareholders and directors who acted on a fraudulent basis, be restricted by the National Treasury from obtaining business from any organ of state for a period not exceeding 10 years, after the audi alteram partem (hear the other side) rule has been applied; and

  - forward the matter for criminal prosecution.

WITNESSES

- ……………………………………..

- …………………………………….

……………………………………….

SIGNATURE(S) OF BIDDERS(S)

DATE:		…………………………………..

ADDRESS	…………………………………..

…………………………………..

…………………………………..

BID NO: FDDM/BID NO: 012/2023-24

T1.2.6

MBD 6.2

DECLARATION CERTIFICATE FOR LOCAL PRODUCTION AND CONTENT FOR DESIGNATED SECTORS

This Municipal Bidding Document (MBD) must form part of all bids invited. It contains general information and serves as a declaration form for local content (local production and local content are used interchangeably).

Before completing this declaration, bidders must study the General Conditions, Definitions, Directives applicable in respect of Local Content as prescribed in the Preferential Procurement Regulations, 2017,  the South African Bureau of Standards (SABS) approved technical specification number SATS 1286:2011 (Edition 1) and the Guidance on the Calculation of Local Content together with the Local Content Declaration Templates [Annex C (Local Content Declaration: Summary Schedule), D (Imported Content Declaration: Supporting Schedule to Annex C) and E (Local Content Declaration: Supporting Schedule to Annex C)].

- General Conditions

  - Preferential Procurement Regulations, 2017 (Regulation 8) make provision for the promotion of local production and content.

  - Regulation 8.(2) prescribes that in the case of designated sectors, organs of state must advertise such tenders with the specific bidding condition that only locally produced or manufactured goods, with a stipulated minimum threshold for local production and content will be considered.

  - Where necessary, for tenders referred to in paragraph 1.2 above, a two-stage bidding process may be followed, where the first stage involves a minimum threshold for local production and content and the second stage price and B-BBEE.

  - A person awarded a contract in relation to a designated sector, may not sub-contract in such a manner that the local production and content of the overall value of the contract is reduced to below the stipulated minimum threshold.

  - The local content (LC) expressed as a percentage of the bid price must be calculated in accordance with the SABS approved technical specification number SATS 1286: 2011 as follows:

LC = [1 - x / y] * 100

Where

x 	is the imported content in Rand

y	is the bid price in Rand excluding value added tax (VAT)

Prices referred to in the determination of x must be converted to Rand (ZAR) by using the exchange rate published by South African Reserve Bank (SARB) at 12:00 on the date of advertisement of the bid as indicated in paragraph 4.1 below.

The SABS approved technical specification number SATS 1286:2011 is accessible on http:/www.thedti.gov.za/industrial development/ip.jsp at no cost.

  - A bid may be disqualified if this Declaration Certificate and the Annex C (Local Content Declaration: Summary Schedule) are not submitted as part of the bid documentation;

- The stipulated minimum threshold(s) for local production and content (refer to Annex A of SATS 1286:2011) for this bid is/are as follows:

Description of services, works or goods 	    Stipulated minimum threshold

_______________________________			     	_______%

_______________________________				_______%

_______________________________				_______%

3.	Does any portion of the goods or services offered have any imported content?

(Tick applicable box)

| YES |  | NO |  |
| --- | --- | --- | --- |

3.1	If yes, the rate(s) of exchange to be used in this bid to calculate the local content as prescribed in paragraph 1.5 of the general conditions must be the rate(s) published by SARB for the specific currency at 12:00 on the date of advertisement of the bid.

The relevant rates of exchange information is accessible on www.reservebank.co.za

Indicate the rate(s) of exchange against the appropriate currency in the table below (refer to Annex A of SATS 1286:2011):

| Currency | Rates of exchange |
| --- | --- |
| US Dollar |  |
| Pound Sterling |  |
| Euro |  |
| Yen |  |
| Other |  |

NB: Bidders must submit proof of the SARB rate (s) of exchange used.

4.	Where, after the award of a bid, challenges are experienced in meeting the stipulated minimum threshold for local content the dti must be informed accordingly in order for the dti to verify and in consultation with the AO/AA provide directives in this regard.

LOCAL CONTENT DECLARATION

(REFER TO ANNEX B OF SATS 1286:2011)

LOCAL CONTENT DECLARATION BY CHIEF FINANCIAL OFFICER OR OTHER LEGALLY RESPONSIBLE PERSON NOMINATED IN WRITING BY THE CHIEF EXECUTIVE OR SENIOR MEMBER/PERSON WITH MANAGEMENT RESPONSIBILITY (CLOSE CORPORATION, PARTNERSHIP OR INDIVIDUAL) IN RESPECT OF BID NO. ................................................................................. ISSUED BY: (Procurement Authority / Name of Institution): ............................................................................................................................................................... NB - The obligation to complete, duly sign and submit this declaration cannot be transferred to an external authorized representative, auditor or any other third party acting on behalf of the bidder. - Guidance on the Calculation of Local Content together with Local Content Declaration Templates (Annex C, D and E) is accessible on http://www.thdti.gov.za/industrial development/ip.jsp. Bidders should first complete Declaration D. After completing Declaration D, bidders should complete Declaration E and then consolidate the information on Declaration C. Declaration C should be submitted with the bid documentation at the closing date and time of the bid in order to substantiate the declaration made in paragraph (c) below. Declarations D and E should be kept by the bidders for verification purposes for a period of at least 5 years. The successful bidder is required to continuously update Declarations C, D and E with the actual values for the duration of the contract. I, the undersigned, …………………………….................................................... (full names), do hereby declare, in my capacity as ……………………………………… ……….. of ...............................................................................................................(name of bidder entity), the following: - The facts contained herein are within my own personal knowledge. - I have satisfied myself that: - the goods/services/works to be delivered in terms of the above-specified bid comply with the minimum local content requirements as specified in the bid, and as measured in terms of SATS 1286:2011; and - The local content percentage (%) indicated below has been calculated using the formula given in clause 3 of SATS 1286:2011, the rates of exchange indicated in paragraph 4.1 above and the information contained in Declaration D and E which has been consolidated in Declaration C: Bid price, excluding VAT (y); R. Imported content (x), as calculated in terms of SATS 1286:2011; R. Stipulated minimum threshold for local content (paragraph 3 above). Local content %, as calculated in terms of SATS 1286:2011. If the bid is for more than one product, the local content percentages for each product contained in Declaration C shall be used instead of the table above. The local content percentages for each product has been calculated using the formula given in clause 3 of SATS 1286:2011, the rates of exchange indicated in paragraph 4.1 above and the information contained in Declaration D and E. - I accept that the Procurement Authority / Institution has the right to request that the local content be verified in terms of the requirements of SATS 1286:2011. - I understand that the awarding of the bid is dependent on the accuracy of the information furnished in this application. I also understand that the submission of incorrect data, or data that are not verifiable as described in SATS 1286:2011, may result in the Procurement Authority / Institution imposing any or all of the remedies as provided for in Regulation 14 of the Preferential Procurement Regulations, 2017 promulgated under the Preferential Policy Framework Act (PPPFA), 2000 (Act No. 5 of 2000). SIGNATURE: DATE: ___________ WITNESS No. 1 DATE: ___________ WITNESS No. 2 DATE: ___________

BID NO: FDDM/BID NO: 012/2023-24

T1.2.7 	FUNCTIONALITY SUMMARY

| Functionality | Points Allocation | Total |
| --- | --- | --- |
| EXPERIENCE ON SIMILAR PROJECTS (BOREHOLES) 5 X Completion Certificates & Reference Letters 4 X Completion Certificates & Reference Letters 3 X Completion Certificates & Reference Letters 2 X Completion Certificates & Reference Letters | 50 40 30 20 | 50 |
| PERSONAL CAPACITY AND RESOURCES RELEVANT TO SCOPE OF WORK Contract manager > 7 years + B. Tech; NQF 7 *(In Engineering field) Site Agent > 5 years + N. Dip; NQF 5 (In Engineering field) Other key staff > 5 years or NQF 5 | 30 20 10 | 30 |
| FINANCIAL VIABILITY Provide bank rating letter | 5 | 5 |
| COIDA CERTIFICATE Letter of Good standing | 15 | 15 |
| Maximum possible score for quality | 100 |  |
| Poor score will score 40% of max points |  |  |
| Satisfactory ………………..70% |  |  |
| Good ……………………… 90% |  |  |
| Very good …………………100% |  |  |
| Should the prospective Bidder/Tenderer score less than 70% on Functionality, the bidder will not be evaluated further. |  |  |
| NQF-Is the National Qualification Framework in South African Qualification Authority which can be contacted at www.saqa.org.za |  |  |

### VOLUME 2

### RETURNABLE DOCUMENTS

### FEZILE DABI DISTRICT MUNICIPALITY

DRILLING AND EQUIPPING OF SIX NEW BOREHOLES AND REFURBISMENT OF TWO EXISTING BOREHOLES IN MAFAHLANENG/TWEELING

### BID NO: FDDM/BID NO: 012/2023-24

### PART T2: RETURNABLE DOCUMENTS

| ### T2.1 LIST OF RETURNABLE DOCUMENTS |  |
| --- | --- |
| ### T2.1.1 | ### Company Founding Statement / Registration Certificate of the Enterprise showing composition of the company. |
| ### T2.1.2 | ### Tax Compliance Certificate and CSD Registration report / (T1.2.3) |
| ### T2.1.3 | ### Authority of Signatory Resolution (T2.2.1) |
| ### T2.1.4 | ### Proof of latest Municipal Payment Statement (rates and taxes) reflecting name of company / Letter from landlord confirming not older than 3 months (T2.2.12) |
| ### T2.1.5 | ### Joint Venture Document if applicable |
| ### T2.1.6 | ### CIDB Registration Certificate |
| ### T2.1.7 | ### Health and Safety Plan method statement |
| ### T2.1.8 | ### Technical Approach & Methodology and Work plan |
|  | ### Letter of Good standing (COID) |
| ### The Tenderer must complete all relevant / required documents below in full and ensure they are properly signed and returned as part of the Tender offer: |  |
| ### C1.1 | ### Form of Offer (Pg30 of this Tender) |
| ### C2.2 | ### Schedule / Bill of Quantities (Pg36 to 53 of this Tender) |
| ### T2.2 | ### Returnable Schedules (Pg54 to 71 of this Tender) |

### PART C1: AGREEMENT AND CONTRACT DATA

### C1.1 	FORM OF OFFER AND ACCEPTANCE

(Agreement)

C1.1.1	Offer

The Employer, identified in the Acceptance signature block, has solicited offers to enter into a contract in respect of the following works:

DRILLING AND EQUIPPING OF SIX NEW BOREHOLES AND REFURBISHMENT OF TWO EXISTING BOREHOLES IN MAFAHLANENG/ TWEELING,

The Tenderer, identified in the Offer signature block below, has examined the documents listed in the Tender Data and addenda thereto as listed in the Tender Schedules, and by submitting this Offer has accepted the Conditions of Tender.

By the representative of the Tenderer, deemed to be duly authorised, signing this part of this Form of Offer and Acceptance, the Tenderer offers to perform all of the obligations and liabilities of the Contractor under the Contract including compliance with all its terms and conditions according to their true intent and meaning for an amount to be determined in accordance with the Conditions of Contract identified in the Contract Data.

THE OFFERED TOTAL OF THE PRICES INCLUSIVE OF VALUE ADDED TAX IS

………………………………………………………………………………………………………………………………………………………………………………………………………………………………………… Rand (in words); 
R ……………………………………. (in figures),

This Offer may be accepted by the Employer by signing the Acceptance part of this Form of Offer and Acceptance and returning one copy of this document to the Tenderer before the end of the period of validity stated in the Tender Data, whereupon the Tenderer becomes the party named as the Contractor in the Conditions of Contract identified in the Contract Data.

Signature(s)		…………………………………………	…………………………………………

Name(s)		…………………………………………	…………………………………………

Capacity		…………………………………………	…………………………………………

for the Tenderer	………………………………………………………………………………………………
			(Name and address of organization)

Name & signature of
witness		…………………………………………	…………………………………………
								Date

C1.1.2	Acceptance

By signing this part of this Form of Offer and Acceptance, the Employer identified below accepts the Tenderer's Offer. In consideration thereof, the Employer shall pay the Contractor the amount due in accordance with the, Conditions of Contract identified in the Contract Data. Acceptance of the Tenderer's Offer shall form an agreement, between the Employer and the Tenderer upon the terms and conditions contained in this Agreement and in the, Contract that is the subject of this Agreement.

The terms of the contract, are contained in

Part T1		Tendering Procedures

Part T2		Returnable Documents

Part C1		Agreements and Contract Data, (which includes this Agreement)

Part C2 		Pricing Data

Part C3		Scope of Work

Part C4		Site Information

and drawings and documents or parts thereof, which may be incorporated by reference into Parts I to 4 above.

Deviations from and amendments to the documents listed in the Tender Data and any addenda thereto listed in the Tender Schedules as well as any changes to the terms of the Offer agreed by the Tenderer and the Employer during this process of offer and acceptance, are contained in the Schedule of Deviations attached to and forming part of this Agreement. No amendments to or deviations from said documents are valid unless contained in this Schedule, which must be duly signed by the authorised representative(s) of both parties.

The Tenderer shall within two weeks after receiving a completed copy of this Agreement, including the Schedule of Deviations (if any), contact the Employer's agent (whose details are given in the Contract Data) to arrange the delivery of any bonds, guarantees, proof of insurance and any other documentation to be provided in terms of the, Conditions of Contract identified in the Contract Data at, or just after, the date this Agreement comes into effect. Failure to fulfill any of these obligations in accordance with those terms shall constitute a repudiation of this Agreement.

Notwithstanding anything contained herein, this Agreement comes into effect on the date when the Tenderer receives one fully completed original copy of this document, including the Schedule of Deviations (if any). Unless the Tenderer (now Contractor) within five days of the date of such receipt notifies the Employer in writing of any reason why he cannot accept the contents of this Agreement, this Agreement shall constitute a binding contract between the parties,

Signature(s)		…………………………………………	…………………………………………

Name(s)			…………………………………………	…………………………………………

Capacity		…………………………………………	…………………………………………

for the Employer		………………………………………………………………………………………………
			(Name and address of organization)

Name & signature of
witness		…………………………………………	…………………………………………
								Date

C1.1.3	Schedule of Deviations

Notes:

1.	The extent of deviations from the tender documents issued by the Employer prior to the tender closing date is limited to those permitted in terms of the Conditions of Tender,

2.	A Tenderer's covering letter shall not be included in the final contract document. Should any matter in such, letter, which constitutes a deviation as aforesaid become the subject of agreements reached during the process of, offer and acceptance, the outcome of such agreement shall be recorded here,

3.	Any other matter arising from the process of offer and acceptance either as a confirmation, clarification or change to the tender documents and which it is agreed by the Parties becomes an obligation of the contract shall also be recorded here,

4.	Any change or addition to the tender documents arising from the above agreements and recorded here, shall also be incorporated into the final draft of the Contract,

1	Subject		………………………………………………………………………………………

Details		………………………………………………………………………………………

2	Subject		………………………………………………………………………………………

Details		………………………………………………………………………………………

3	Subject		………………………………………………………………………………………

Details		………………………………………………………………………………………

4	Subject		………………………………………………………………………………………

Details		………………………………………………………………………………………

5	Subject		………………………………………………………………………………………

Details		………………………………………………………………………………………

6	Subject		………………………………………………………………………………………

Details		………………………………………………………………………………………

By the duly authorised representatives signing this Schedule of Deviations, the Employer and the Tenderer agree to and accept the foregoing Schedule of Deviations as the only deviations from and amendments to the documents listed in the Tender Data and addenda thereto as listed in the Tender Schedules, as well as any confirmation, clarification or change to the terms of the offer agreed by the Tenderer and the Employer during this process of offer and acceptance It is expressly agreed that no other matter whether in writing, oral communication or implied during the period between the issue of the tender documents and the receipt by the Tenderer of a completed signed copy of this Agreement shall have any meaning or effect in the contract between the parties arising from this Agreement.

FOR THE TENDERER:

Signature(s)		…………………………………………	…………………………………………

Name(s)			…………………………………………	…………………………………………

Capacity		…………………………………………	…………………………………………

………………………………………………………………………………………………
		(Name and address of organization)

Name & signature of
witness		…………………………………………	…………………………………………
							Date

For the Employer:

Signature(s)		…………………………………………	…………………………………………

Name(s)			…………………………………………	…………………………………………

Capacity		…………………………………………	…………………………………………

………………………………………………………………………………………………
		(Name and address of organization)

### Name & signature of
witness		…………………………………………	…………………………………………
							Date

C1.2.4: CONTRACT DATA FOR: DRILLING AND EQUIPPING OF SIX NEW BOREHOLES AND REFURBISHMENT OF TWO EXISTING BOREHOLES IN MAFAHLANENG /TWEELING

## PART 1: DATA PROVIDED BY THE EMPLOYER ## CONDITIONS OF CONTRACT The General Conditions of Contract (GCC) for Construction Works, Third Edition (2015), published by the South African Institution of Civil Engineering, is applicable to this Contract. ## CONTRACT SPECIFIC DATA The following contract specific data, referring to the GCC, are applicable to this Contract : ## Compulsory Data Clause 1.1.1.13 The Defects Liability Period is 12 months from the date of the Certificate of Completion. Clause 1.1.1.15 : The name of the Employer is Fezile Dabi District Municipality. Clause 1.2.1.2 : The address of the Employer is Fezile Dabi District Municipality, P O Box 10, Sasolburg, 1947 Clause 1.1.11.16 : The name of the Engineer is FLAGG Consulting Engineers (Pty) Ltd. Clause 1.2.1.2 : The address of the Engineers is 6 Mark Street Frankfort, P O Box 864, Frankfort, 9830. Email –frankfort@flaggconsulting.co.za Clause 1.1.1.26 : The Pricing Strategy is Re-measurement Contract. Clause 5.3.1 : The documentation required before commencement with Works execution are : Health and Safety Plan (refer to clause 4.3) Initial programme (refer to clause 5.6) Security (refer to clause 6.2) Insurance (refer to clause 8.6) Clause 5.3.2 : The time to submit the documentation required before commencement with Works execution is 28 days. Clause 5.8.1 : The non-working days are Sundays. The special non-working days are : - New Year’s Day, Human Rights Day, Good Friday, Family Day, Freedom Day, Workers’ Day, Youth Day, National Woman’s Day, Heritage Day, Reconciliation Day, Christmas Day, Day of Goodwill. These days will also be excluded from time calculations. - The year break commences on 8 January 2024 and ends on 15 December 2024

C1.2.4: DRILLING AND EQUIPPING OF SIX NEW BOREHOLES AND REFURBISHMENT OF TWO EXISTING BOREHOLES IN MAFAHLANENG /TWEELING

Clause 5.13.1 : The penalty for failing to complete the Works is R5000.00 per day. Clause 5.16.3 : The latent defect period is 10 years. Clause 6.10.1.5 : The percentage advance on materials not yet built into the Permanent Works is max 80% of invoice price. Clause 6.10.3 : The limit of retention money is 10%. Clause 8.6.1.1.2 : No plant or materials shall be supplied by the Employer. Clause 8.6.1.1.3 : The amount to cover professional fees for repairing damage and loss to be included in the insurance sum is R250 000,00 Clause 8.6.1.3 : The limit of indemnity for liability insurance is R2 000 000.00. Clause 10.5.3 : The number of Adjudication Board Members to be appointed is 1. PART 2 : DATA PROVIDED BY THE CONTRACTOR Clause 1.1.1.9 : The name of the Contractor is …………………………………………………………………………………………………. Clause 1.2.1.2 : The Address of the Contractor is …………….…………………………………………………………………………………. ……………………………………………………………………………………………………………………………………… Clause 1.1.1.14 : The time for achieving Practical Completion is ……………………………….. Clause 6.2.1 : The security to be provided by the Contractor shall be one of the following : TYPE OF SECURITY (inclusive of VAT); Contractor’s Choice Indicate “yes” or “no”. Cash deposit of 10% of the Contract Sum. Performance guarantee of 10% of the Contract Sum. Retention of 10% of the value of the Works. Cash deposit of 5% of the Contract Sum plus retention of 5% of the value of the Works. Performance guarantee of 5% of the Contract Sum plus retention of 5% of the value of the Works.

### PART C2: SCHEDULE OF QUANTITIES

### C2.1	SCHEDULE OF QUANTITIES

The schedule of quantities forms the basis on which the Tenderer arrives at the offered total in the Form of Offer. By signing the Acceptance of the Form of Offer and Acceptance, the Employer accepts the Tenderers offer, and the Schedule of Quantities is then included in the Contract Agreement between the parties.

### C2.1.1	Preamble to Schedule of Quantities

    - The General Conditions of Contract, the Special Conditions of Contract (if any), the Specifications (including the Project Specifications) and the drawings are to be read in conjunction with the Schedule of Quantities.

    - a)	The schedule comprises items covering the Contractor’s profit and costs of general liabilities 	and of the supply and installation of permanent apparatus.

- The Tenderer is at liberty to insert a rate of his own choosing for each item in the schedule and his attention is drawn to the fact that the Contractor has the right, under various circumstances, to payment for additional works carried out and that the Engineer is obliged to base his assessment of the rates to be paid for such additional work on the rates inserted in the schedule by the Contractor.

    - Descriptions in the Schedule of Quantities are abbreviated.

    - The prices and rates to be inserted in the Schedule of Quantities are to be the full inclusive prices to the Employer for apparatus/work described under the several items.  Such prices shall cover all costs and expenses that may be required in and for the execution of the work described, and shall cover the cost of all general risks, liabilities and obligations set forth or implied in the documents on which the tender is based.

    - A price or rate is to be entered against each item in the Schedule of Quantities, whether the quantities are stated or not.  An item against which no price is entered will be considered to be covered by the other prices or rates in the schedule.

    - The contractor will be paid an amount for the item of work in the schedule of quantities which is the rate for the work multiplied by the quantity completed.

    - The units of measurement described in the Bill of Quantities are metric units. Abbreviations used in the Bill of Quantities are as follows:

%	=	percent
h	=	hour
ha 	=	hectare
kg	=	kilogram
kl	=	kilolitre
km	=	kilometer
km-pass	=	kilometer-pass
kPa	=	kilopascal
kW	=	kilowatt
l	=	liter
m	=	meter
mm	=	millimeter
m2	=	square meter
m2-pass	=	square meter-pass
m3	=	cubic meter
m3-km	=	cubic meter-kilometer
MN	=	meganewton
MN.m	=	meganewton-meter
Mpa	=	megapascal
No.	=	number
P Sum	=	Provisional sum
PC sum	=	Prime Cost sum
R/only	=	Rate only
sum	=	lump sum
t	=	ton (1000 kg)
W/day	=	Work

| ITEM | PAYMENT | DESCRIPTION | UNIT | QUANTITY | RATE |  | AMOUNT |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 |  | SECTION 1: PRELIMINARY AND GENERAL |  |  |  |  |  |
| 1.1 | SABS 1200 A | FIXED COST ITEMS |  |  |  |  |  |
| 1.1.1 | 8.3.1 | Contractual Requirements | Sum | 1,00 |  |  |  |
|  | SABS 1200 AB | Establish facilities on site |  |  |  |  |  |
|  | 8.3.2.1 | a) Facilities for Engineer as per PSBA | Sum | 1,00 |  |  |  |
| 1.1.2 | PS 7 | Site office, conference room, car port, toilet facilities and office furniture | Prov Sum | 1,00 | 65 000,00 |  | 65 000,00 |
| 1.1.3 | PSAB 1 | Survey equipment | Sum | 1,00 |  |  |  |
| 1.1.4 |  | One Contract Notice Board | Sum | 1,00 |  |  |  |
|  | 8.3.2.2 | b) Facilities for Contractor |  |  |  |  |  |
| 1.1.5 |  | Offices and stores, workshop, housing, ablution- and latrine facilities, plant and tools | Sum | 1,00 |  |  |  |
| 1.1.6 |  | Water supply, electrical power, reticulation of water and access to site | Sum | 1,00 |  |  |  |
| 1.1.7 | PS 10 | Conformity with RDP requirements | Sum | 1,00 |  |  |  |
| 1.1.8 | 8.3.3 | Additional Fixed Cost liabilities (particulars to be supplied) Specialist | Prov Sum | 1,00 | 280 000,00 |  | 280 000,00 |
| 1.1.9 | 8.3.4 | Removal of site facilities | Sum | 1,00 |  |  |  |
| 1.1.10 |  | Allowance for OHS & Environmental management | Prov Sum | 1,00 | 70 000,00 |  | 70 000,00 |
| 1.2 | 8.4 | TIME RELATED ITEMS |  |  |  |  |  |
| 1.2.1 | 8.4.1 | Contractual Requirements | Sum | 1,00 |  |  |  |
|  | 8.4.2 | Operate and maintain facilities on site |  |  |  |  |  |
|  | 8.4.2.1 | a) Facilities for Engineer for duration of construction (SABS 1200 AB) |  |  |  |  |  |
| 1.2.2 | PS 7 | Site office, conference room, car port, toilet facilities and office furniture | Prov Sum | 1,00 | 20 000,00 |  | 20 000,00 |
| 1.2.4 | PSAB 1 | Accommodations for RE | Prov Sum | 1,00 | 20 000,00 |  | 20 000,00 |
| 1.2.5 |  | Resident Engineer: Cell phone for site purposes | Prov Sum | 1,00 | 5 000,00 |  | 5 000,00 |
|  | 8.4.2.2 | b) Facilities for Contractor for duration of construction |  |  |  |  |  |
| 1.2.6 |  | Offices and stores, workshop, housing, ablution- and latrine facilities, plant and equipment | Sum | 1,00 |  |  |  |
| 1.2.7 |  | Water supply, electrical power, reticulation of water and access to site | Sum | 1,00 |  |  |  |
| 1.2.8 | 8.4.3 | Construction Supervision for the duration of the contract | Sum | 1,00 |  |  |  |
| 1.2.9 | 8.4.4 | Company and head office overhead costs | Sum | 1,00 |  |  |  |
| 1.2.12 |  | Allowance for OHS & Environmental management | Prov Sum | 1,00 | 60 000,00 |  | 60 000,00 |
| 1.2.13 |  | Allowance for CLO | Prov Sum | 1,00 | 55 000,00 |  | 55 000,00 |
| 1.3 |  | TEMPORARY WORK |  |  |  |  |  |
| 1.3.1 | 8.8.1 | Construction and maintenance of all access roads and work for the duration of the contract | Sum | 1,00 |  |  |  |
| 1.4 |  | CONTROL TESTING |  |  |  |  | - |
| 1.4.1 |  | Preliminary Sum allowed for laboratory tests by an independent laboratory when required by the Engineer | Prov Sum | 1,00 | 220 000,00 |  | 220 000,00 |
| 1.4.2 |  | Percentage adds on to Item 1.4.1 for overheads, administration and profit | % | 220000,00 |  |  |  |
| TOTAL SECTION 1 |  |  |  |  |  |  |  |
| ITEM | PAYMENT | DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT |  |
| 2 |  | SECTION 2: RISING MAINS |  |  |  |  |  |
| 2.1 | SABS 1200 C | SITE CLEARANCE |  |  |  |  |  |
| 2.1.1 | 8.2.1 | Clear and grub of site and remove all obstructions on pipeline route up to 3m wide | m | 2 070,00 |  |  |  |
| 2.1.2 |  | a) Girth over 600mm up to 1000mm | No | 8,00 |  |  |  |
| 2.1.3 |  | b) Girth over 1000mm up to 2000mm | No | - |  |  |  |
| 2.1.4 |  | c) Girth over 2000mm up to 3000mm | No | - |  |  |  |
| 2.2 | SABS 1200 DB | EXCAVATION |  |  |  |  |  |
| 2.2.1 |  | Excavate by MACHINE in all materials up to 750mm wide pipe trenches for water pipes only, backfill, compact and dispose of surplus or unsuitable material for depths of: |  |  |  |  |  |
|  |  | Over and up to |  |  |  |  |  |
| 2.2.1.1 | 8.3.2(a) | 0.0m to 1.5m | m | 1 700,00 |  |  |  |
| 2.2.1.2 |  | 1.5m to 2.0m | m | 388,00 |  |  |  |
| 2.2.1.3 |  | 2.0m to 2.5m | m | - |  | Rate Only |  |
| 2.2.1.4 |  | 2.5m to 3.0m | m | - |  | Rate Only |  |
|  |  | Extra-over Item 2.2.1 for: |  |  |  |  |  |
| 2.2.2 | 8.3.2(b) | Hard Excavation | m3 | 753,00 |  |  |  |
| 2.2.3 | 8.3.2(c) | Excavate and dispose of unsuitable material from trench bottom | m3 | 251,00 |  |  |  |
| 2.2.4 |  | Excavate by HAND in all materials suitable for hand excavation for trenches up to 600mm wide pipe trenches for water pipes only, backfill, compact and dispose of surplus or unsuitable material for depths of: |  |  |  |  |  |
|  |  | Over and up to |  |  |  |  |  |
| 2.2.4.1 | PSDB 3.4 | 0.0m 1.0m | m | - |  |  |  |
| 2.2.4.2 | PSDB 3.4 | 1.0m 1.5m | m | - |  |  |  |
|  |  | Extra-over Item 2.2.4 for: |  |  |  |  |  |
| 2.2.5 | PSDB 3.4 | Intermediate excavation | m3 | - |  | Rate Only |  |
| 2.2.6 | PSDB 3.4 | Hard excavation | m3 | - |  | - |  |
| 2.2.7 | 8.3.4 (a) (LI) | Shoring and safeguarding of trench to the satisfaction of the Engineer and the safety regulations | m | 200,00 |  |  |  |
| 2.2.8 | 8.3.3.3 | Soilcrete backfill (7% cement) at crossings with existing streets and compact to 93% Mod. AASHTO densities were ordered by the Engineer | m³ | 7,00 |  |  |  |
| 2.2.9 | 8.3.3.3 | Finishing off the site on completion of the works to the satisfaction of the Engineer, including levelling off, disposal of surplus material, etc | Sum | 1,00 |  |  |  |
| 2.3 | SABS 1200 LB | BEDDING (PIPES) |  |  |  |  |  |
|  |  | Provision of selected granular material for pipe bedding from the following sources: |  |  |  |  |  |
| 2.3.1 | 8.2.1 | Trench excavation within 2 km | m3 | 218,00 |  |  |  |
| 2.3.2 | PSQ 5 | Imported from borrow pit | m3 | 158,00 |  |  |  |
|  |  | Provision of selected fill blanket to 200mm above the pipe from the following sources: |  |  |  |  |  |
| 2.3.3 | 8.2.1 | Trench excavation within 2km | m3 | 218,00 |  |  |  |
| 2.3.4 | PSQ 5 | Imported from borrow pit | m3 | 268,00 |  |  |  |

| ITEM | PAYMENT | DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT |
| --- | --- | --- | --- | --- | --- | --- |
| 2.3.5 | 8.2.2.3 | Provision of 19mm nominal size crushed stone aggregate required for bedding from commercial source when instructed by the Engineer | m3 | 65,00 |  |  |
| 2.4 | SABS 1200 L | MEDIUM PRESSURE PIPELINES |  |  |  |  |
| 2.4.1 |  | HDPE Class PN8 |  |  |  |  |
|  | 8.2.1 | Supplying, laying and jointing of HDPE Class PN8 pipes irrespective of depth. Jointing of pipes using in-situ butt welding, test and disinfect |  |  |  |  |
| 2.4.1.1 |  | 40mm Ø (33,7mm I.D.) Class PN8, PE100 | m | 1 720,00 |  |  |
| 2.4.1.2 |  | 50mm Ø (44,8mm I.D.) Class PN8, PE100 | m | - |  |  |
| 2.4.1.3 |  | 63mm Ø (56,7mm I.D.) Class PN8, PE100 | m | 400,00 |  |  |
| 2.4.1.4 |  | 75mm Ø (67,4mm I.D.) Class PN8, PE100 | m | 450,00 |  |  |
| 2.4.2 |  | HDPE Class PN12.5 |  |  |  |  |
|  | 8.2.1 | Supplying, laying and jointing of HDPE Class PN12.5 pipes irrespective of depth. Jointing of pipes using in-situ butt welding, test and disinfect |  |  |  |  |
| 2.4.2.1 |  | 40mm Ø (33,7mm I.D.) Class PN12.5, PE100 | m | - |  |  |
| 2.4.2.2 |  | 50mm Ø (42,2mm I.D.) Class PN12.5, PE100 | m | - |  |  |
| 2.4.3 |  | HDPE Class PN20 |  |  |  |  |
|  | 8.2.1 | Supplying, laying and jointing of HDPE Class PN20 pipes irrespective of depth. Jointing of pipes using in-situ butt welding, test and disinfect |  |  |  |  |
| 2.4.3.1 |  | 40mm Ø (30,5mm I.D.) Class PN20, PE100 | m | - |  |  |
| 2.4.3.2 |  | 63mm Ø (47,9mm I.D.) Class PN20, PE100 | m | - |  |  |
| 2.4.3.3 |  | 75mm Ø (57,2mm I.D.) Class PN20, PE100 | m | - |  |  |
| 2,5 |  | PIPELINE MARKERS |  |  |  |  |
| 2.5.1 |  | Supply all labour and material for concrete pipeline markers as per the water general details. Concrete markers to be supplied at change of horizontal direction | No | 12,00 |  |  |
| 2,6 |  | CONNECTION TO EXISTING WATER NETWORK |  |  |  |  |
| 2.6.1 |  | Supply all labour and material (fittings) to connect to main supply pipeline including excavation backfill, disposal of surplus material, cutting of pipes and moving of fittings and making good | Prov Sum | 1,00 | 20 000,00 | 20 000,00 |
| TOTAL SECTION 2 |  |  |  |  |  |  |

| ITEM | PAYMENT | DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT |
| --- | --- | --- | --- | --- | --- | --- |
| 3 |  | SECTION 3: BOREHOLES PUMP HOUSE STRUCTURE |  |  |  |  |
| 3,1 |  | EARTHWORKS |  |  |  |  |
| 3.1.1 |  | 150mm G7 layer compacted to 93% Mod Aashto density | m3 | 75,00 |  |  |
| 3,2 |  | FLOOR SLAB |  |  |  |  |
|  |  | Suitable founding conditions |  |  |  |  |
| 3.2.1 |  | 3m x 3m x 150mm Concrete base with 2 layers (Top and Bottom) of REF 617 welded mesh | No. | 6,00 |  |  |
|  |  | Unsuitable founding conditions |  |  |  |  |
| 3.2.2 |  | 3m x 3m x 250mm Concrete base with 2 layers (Top and Bottom) of REF 888 welded mesh | No. | 6,00 |  |  |
|  |  | Precast concrete borehole security structure |  |  |  |  |
| 3.2.3 |  | Supply and install precast concrete borehole structure according to drawing F0285-G103 to G104) | No. | 6,00 |  |  |
| 3.2.4 |  | FENCING |  |  |  |  |
| 3.2.4.1 |  | Fabricate and install new 358 single skin security gate 4,05m x 2,0m high (vehicles) as per drawings clear view | No. | 8,00 |  |  |
| 3.2.4.2 |  | Supply and install new security gate 1m x 2,0m (pedestrians) - Clear view visibility security gate completes including excavation, labour and all materials required. Anti cut robust wire and welded joints, anti-climb gate. | No. | 8,00 |  |  |
| 3.2.4.3 |  | Supply and Install Clear-VU (Singleskin) fencing, 2.1m High with poles and access gate with a lockable mechanism, including all associated works such excavation and concrete for foundation, all nuts and bolts for fastening etc | m | 580,00 |  |  |
| 3.2.4.4 |  | Finishing of the site on completion of the works to the satisfaction of the Engineer, including levelling off, disposal of surplus material, etc | No | 8,00 |  |  |
| 3,3 |  | BOREHOLE EQUIPPING |  |  |  |  |
|  |  | Equipe boreholes according to drawing F0285-G100 |  |  |  |  |
| 3.3.1 |  | Supply and install of HDPE pipe inside borehole casing |  |  |  |  |
| 3.3.2 |  | B0 - Submersible Borehole Pump by Fraklin or Similar Approved Supplier | No | 8,00 |  |  |
| 3.3.3 |  | B1 - 90° Galvanised Bend (Female) To Suit Pipe Diameter | No | 8,00 |  |  |
| 3.3.4 |  | B2 - 900mm Long Heavy-Duty Galvanised Steel Pipe | No | 8,00 |  |  |
| 3.3.5 |  | B3 - Flanged Water Meter to Suit Pipe Diameter. | No | 8,00 |  |  |
| 3.3.6 |  | B4 - 125mm Long Heavy-Duty Galvanised Steel Pipe Threated Both Ends | No | 8,00 |  |  |
| 3.3.7 |  | B5 - Heavy duty Galvanized Tee complete with plug fitted to branch 1 for pressure switch on electrical installation | No | 8,00 |  |  |
| 3.3.8 |  | B6 - 100mm Glycerine Filled Pressure Gauge Ranging From 0-1500KPa Complete With 2 x 8 x 75mm Long. Ngi. Pipe Threaded Both Ends And 1 X 8mm Female Threated Ball-O-Top Isolating Cock. | No | 8,00 |  |  |
| 3.3.9 |  | B6.1 - 50mmØ heavy duty galvanized reducing tee | No | 8,00 |  |  |
| 3.3.10 |  | B7 - 50mmØ Heavy duty galvanized steel pipe | No | 8,00 |  |  |
| 3.3.11 |  | B8 - 50mmØ heavy duty galvanized equal tee | No | 8,00 |  |  |
| 3.3.12 |  | B9 - 50mmØ Butterfly Gate Valve | No | 8,00 |  |  |
| 3.3.13 |  | B10 - 50mmØ non-return valve suitable for 1000 kPA pressure | No | 8,00 |  |  |
| 3.3.14 |  | B11 - 50mmØ 700mm long heavy-duty galvanized steel pipe, threaded both ends | No | 8,00 |  |  |
| 3.3.15 |  | B12 - 90° Galvanised Bend (Female) To Suit Pipe Diameter | No | 8,00 |  |  |
| 3.3.16 |  | B12.1 - 90° Galvanised Bend to Suit Pipe Diameter | No | 8,00 |  |  |
| 3.3.17 |  | B13 - 50mmØ 1500mm long heavy-duty galvanized steel pipe, threaded both ends | No | 8,00 |  |  |
| 3.3.18 |  | B14 - 50mmØ Flange Adaptor for Pvc Pipe | No | 8,00 |  |  |
| 3.3.19 |  | B15 - 50mmØ heavy duty galvanized equal tee | No | 8,00 |  |  |
| 3.3.20 |  | B15.1 - 50mmØ Butterfly Gate Valve | No | 8,00 |  |  |
| 3.3.21 |  | B15.2 - 50mmØ Isolating Valve for Air Release & Vacuum Break Valve | No | 8,00 |  |  |
| TOTAL SECTION 3 |  |  |  |  |  |  |

| ITEM | PAYMENT | DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT |
| --- | --- | --- | --- | --- | --- | --- |
| 4 |  | SECTION 4: MECHANICAL & ELECTRICAL EQUIPMENT |  |  |  |  |
| 4,1 |  | TREATMENT PLANT SCHEME 1 FOR SINGLE RISING MAIN |  |  |  |  |
| 4.1.1 |  | Supply and Install MCC panels (According to drawing specs including timers), cables and lighting (electrical cable length shall include distance from Eskom/Municipal Transformer to MCC panel in Borehole Security Structure and from MCC panel down into the borehole) | No | 8,00 |  |  |
| 4.1.2 |  | Supply submersible borehole pumps capable of supplying 7.42m3/hr with dynamic head = 158.75m complete with heavy duty motor | No | 2,00 |  |  |
| 4.1.3 |  | Supply submersible borehole pumps capable of supplying 4.32m3/hr with dynamic head = 86.76m complete with heavy duty motor | No | 2,00 |  |  |
| 4.1.4 |  | Supply submersible borehole pumps capable of supplying 1.98m3/hr with dynamic head = 149.03m complete with heavy duty motor | No | 2,00 |  |  |
| 4.1.5 |  | Supply submersible borehole pumps capable of supplying 5.76m3/hr with dynamic head = 141.93m complete with heavy duty motor | No | 2,00 |  |  |
| 4.1.6 |  | Contractors profit for the supply of pumps in respect of item 7.1.2 to 7.1.5 | % | 0,00 |  |  |
| 4.1.7 |  | Install pumps (See drawings for pump specifications) | No | 8,00 |  |  |
| 4.1.8 |  | Supply and install telemetry system for all boreholes and the booster pump station | No | 8,00 |  |  |
| 4.1.9 |  | Contractors profit for the supply and installing of telemetry system in respect of item 4.3.4 | % | 0,00 |  |  |
| 4.1.10 |  | Commissioning, manuals and training | No | 8,00 |  |  |
| 4,2 |  | TREATMENT PLANT SCHEME FOR TREATMENT OF BOREHOLE WATER TO CLASS 1 WATER |  |  |  |  |
|  |  | The treatment plant will consist of pre-oxidation, flocculation, dual media filtration, Iron removal filters and chlorine disinfection |  |  |  |  |
| 4.2.1 |  | Supply and place 10kl tank as per drawing on concrete plinth | No | 2,00 |  |  |
| 4.2.2 |  | Supply and install filter feed pumps that pump the water through the filtration system to the storage tank complete with piping and valves | No | 4,00 |  |  |
| 4.2.3 |  | Supply and place piping from filter pump to filters | No | 2,00 |  |  |
| 4.2.4 |  | Sodium hypochlorite dosing system consisting of 1x 200l tank, dosing lines, dosing pump and injector, for disinfection using systems (flocculant and liquid chlorine) | No | 2,00 |  |  |
| 4.2.5 |  | Flocculant aid dosing system consisting of 1x 200l tank, dosing lines, dosing pump and injector | No | 2,00 |  |  |
| 4.2.6 |  | Set of automatic dual media sand filters to remove turbidity from the water | No | 2,00 |  |  |
| 4.2.7 |  | Set of automatic Iron removal filters to remove iron from the water | No | 2,00 |  |  |
| 4.2.8 |  | Control panel and wiring for the plant with electronic filter backwash controller and electronic flow meter to monitor flow rate from the treatment plant | No | 2,00 |  |  |
| 4.2.9 |  | Installation | No | 2,00 |  |  |
| 4.2.10 |  | Start-up chemicals for two weeks | Prov Sum | 1,00 | 50 000,00 | 50 000,00 |
| 4.2.11 |  | commissioning, manuals and training | Sum | 1,00 |  |  |
| TOTAL SECTION 4 |  |  |  |  |  |  |
| 5 |  | SECTION 5: UPGRADING OF ESKOM TRANSFORMERS |  |  |  |  |
| 5,1 |  | Provide new Eskom Transformers | Prov Sum | 2,00 | 150 000,00 | 300 000,00 |
| 5.1.1 |  | Site Establishment | No | 1,00 |  |  |
| 5.1.2 |  | Excavation | No | 80,00 |  |  |
| 5.1.3 |  | Pole Dress & planting | No | 80,00 |  |  |
| 5.1.4 |  | Supply, Delivery and String Mink Conductor | m | 700,00 |  |  |
| 5.1.5 |  | Transformer Structure | No | 2,00 |  |  |
| 5.1.6 |  | MV Earthing | Sum | 1,00 |  |  |
| 5.1.7 |  | LV Earthing | Sum | 1,00 |  |  |
| 5.1.8 |  | Labels | Sum | 1,00 |  |  |
| 5.1.9 |  | MV Stays | Sum | 1,00 |  |  |
| 5.1.10 |  | Section Links. | Sum | 1,00 |  |  |
| 5.1.11 |  | MV Fuse Cut Out Set | Sum | 1,00 |  |  |
| TOTAL SECTION 5 |  |  |  |  |  |  |

BID NO: FDDM/BID NO: 012/2023-24

### C2.1.2		SUMMARY OF SCHEDULES

| ###### CIVIL SECTION | DESCRIPTION | AMOUNT |
| --- | --- | --- |
| 1 2 3 4 5 | Preliminary and general Borehole Rising Mains Boreholes Pump House Structure Mechanical & Electrical Equipment Upgrading of Eskom Transformers | R R R R R |
| SUBTOTAL A Contingencies: Allow 10% |  | R R |
| SUBTOTAL B Add Value Added Tax (15%) |  | R R |
| TOTAL CARRIED TO FORM OF TENDER |  | R |

TIME FOR COMPLETION :	………….weeks

TENDERER : ………………………………………			DATE : …………………………………………

CIDB Status : ………………………….				SIGNATURE : ……………………………….

Capacity of Signatory in Organization :	…………………………………………………

BANKING DETAILS

Bank :			……………………………………………………………..

Branch :		……………………………………………………………..

Clearance No. : 	……………………………………………………………..

Account No. :		……………………………………………………………..

Phone Number of Branch : ……………………………………………………….

BID NO: FDDM/BID NO: 012/2023-24

### T2.2 	RETURNABLE SCHEDULES

T2.2.1 : Authority of Signatory

T2.2.1.1 :

Signatories for Companies shall establish their authority by attaching a copy of the relevant Resolution of the Board of Directors, duly signed and dated, to this form.  An example is shown below:

"By Resolution of the Board of Directors at a meeting on ……………………………………………………… 20 ….

Mr. ……………………………………………………………………  has been duly authorized to sign all documents

In connection with Tender No. ……… of …………………………………………………………..……… on behalf of

(block capitals) …………………………………………………………………………………………………………..…

..………………………………………………………………………………………………………………………………

# SIGNED ON BEHALF OF COMPANY :..……….………………………………………………………………………

..………………………………………………………………………………………………………………………………

# IN HIS CAPACITY AS :	…………………………………………………..

# SIGNATURE OF SIGNATORY :	…………………………………………………..

T2.2.1.2 : Signatories for Close Corporation

We, the undersigned, being the key members in the business trading as..………………………………………… hereby authorize Mr. / Ms. ……………………………………………….., to sign all documents in connection with the tender and any contract resulting from it on our behalf.

| name | address | signature | date |
| --- | --- | --- | --- |

NOTE :	This certificate is to be completed and signed by all of the key members upon whom rests the direction of the affairs of the Close Corporation as a whole.

T2.2.1.3	 : Signatories for Joint Venture

We, the undersigned, are submitting this tender offer in Joint Venture and hereby authorize 
Mr. / Ms. ……………………………………………….., authorized signatory of the company ………………………………………………………………………. , acting in the capacity of lead partner, to sign all documents in connection with the tender offer and any contract resulting from it on our behalf.

| name of firm | address | authorising signature, name & capacity |
| --- | --- | --- |
| Lead partner |  |  |

T2.2.1.4 : Signatories for Other Concern

We, the undersigned, being the key members in the business trading as..………………………………………… hereby authorize Mr. / Ms. ……………………………………………….., to sign all documents in connection with the tender and any contract resulting from it on our behalf.

| name | address | signature | date |
| --- | --- | --- | --- |

NOTE :	This certificate is to be completed and signed by all of the key members upon whom rests the direction of the affairs of the Concern as a whole.

# T2.2.2: SCHEDULE OF PLANT AVAILABLE

The Tenderer's attention is drawn to the various sections of the Specifications.

The Tenderer shall state below which plant would be immediately available, which plant would be available from orders for plant outstanding, and which further plant would be acquired for the work should the Tenderer be awarded the Contract.

(a)	Plant immediately available for this work:

- Plant on order and which will be put on the work on arrival:

(c)	Plant that will be acquired for the work if Tender is accepted:

TENDERER : ………………………………………			DATE : …………………………………………

BID NO: FDDM/BID NO: 012/2023-24

T2.2.3: PREVIOUS EXPERIENCE OF TENDERER

The Tenderer shall, in the schedule hereunder, list all work, of a similar nature to that contained in this Contract, which has been carried out by him during the last three years.

This information is material to the award of the Contract.

| No | Employer - Organ of State | Contact Person : Consulting Engineer / Municipal official (Name, telephone no & fax no) | Title of contract for the similar construction works | Project Value (R, VAT included) | Year(s) executed |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
| 5 |  |  |  |  |  |
| 6 |  |  |  |  |  |
| 7 |  |  |  |  |  |
| 8 |  |  |  |  |  |
| 9 |  |  |  |  |  |
| 10 |  |  |  |  |  |

TENDERER: ………………………………………			DATE: …………………………………………

BID NO: FDDM/BID NO: 012/2023-24

T2.2.4: DAYWORK SCHEDULE

The Tenderer shall complete this Annexure in every respect.

The rates and prices given below shall be utilized in settling any claim or claims for which no comparable rate is available in the Schedule of Quantities.

The Tenderer will be required to prove that such rates and prices are reasonable.

1.	MATERIAL

Cement	Per 50kg pocket delivered

Sand	Per cubic metre delivered

38mm - Nom. stone	Per cubic metre delivered

20mm - Nom. stone	Per cubic metre delivered

13mm - Nom. stone	Per cubic metre delivered

Clay face bricks	Per 1000 delivered

Engineering clay bricks	Per 1000 delivered

2.	LABOUR

Foreman	Per week

Ass Foreman	Per week

Steel Erectors	Per hour

Sheet Layers	Per hour

Carpenters	Per hour

Painters	Per hour

Gangers	Per hour

Unskilled labour	Per day

Plumbers	Per day

Brick layers	Per day

The above wages and rates shall allow for the gross remuneration of workmen and foremen and the nett cost of materials actually used. These rates shall be subject to the mark up percentages stated in the Contract data as required under Clause 40(4)b of the General Conditions of Contract.

3.	TRANSPORT

Rate per cubic meter per kilometer as

Measured in vehicle

Rate per metric ton per kilometer

No percentage allowance shall be added to rates for transport.

4.	PLANT

The Contractor is to provide rates for any equipment and plant he may consider necessary for the execution of any daywork he may encounter.  Rates stated here shall include all profit, etc.  These rates will be deemed to include the cost of operator/s if any. In the event of plant used for which no rates are mentioned hereunder, the costs will be held as the average of the rates supplied by three recognized plant hire specialists including an extra over of 15%.

| ### DESCRIPTION |  | OPERATING TARIFF | STANDING TIME TARIFF |
| --- | --- | --- | --- |
| TLB EXCAVATOR TIPPER TRUCK Backactor Case Backactor Loader Tippers …. m3 Compressor c.f.m. Grader Bulldozer Bulldozer Water Truck ………………………………… | Per hour Per hour Per hour Per hour Per hour Per hour Per hour Per hour Per hour Per hour Per hour Per hour |  |  |

TENDERER : ………………………………………			DATE : …………………………………………

BID NO: FDDM/BID NO: 012/2023-24

T2.2.5: STATUS OF CONCERN SUBMITTING THE TENDER

- GENERAL

State whether the tenderer is a company, a closed corporation, a partnership or a one-man concern)

(Make an X in the appropriate space hereunder)

| Company |  | ##### Closed Corporation |  | ##### Joint Venture |  | ##### Other |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

- INFORMATION TO BE PROVIDED (Block letters)

  - If the tenderer is a company :

- Affix a certified copy of the Certificate of Incorporation to this page

- List of Directors

  - If the tenderer is a closed corporation :

- Affix a certified copy of the Founding Statement to this page

- List of Members

  - If the tenderer is a jOINT VENTURE:

- Affix a certified copy of the relevant status documents of concern to this page

- List the firms forming part of the Joint Venture

  - If the tenderer is aNY OTHER:

Provide full particulars and description for type of concern

TENDERER : ………………………………………			DATE : …………………………………………

BID NO: FDDM/BID NO: 012/2023-24

T2.2.6: PRELIMINARY PROGRAMME / CASH FLOW SCHEDULE

Tenderers shall provide their preliminary programme and estimated cash flow for the contract period including a provision for expected escalation but excluding contingencies.

|  | # ACTIVITY | # WEEKS |  |  |  | # WEEKS |  |  |  | # WEEKS |  |  |  | # WEEKS |  |  |  | # WEEKS |  |  |  | # WEEKS |  |  |  | # WEEKS |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | # 1 | # 2 | # 3 | # 4 | # 5 | # 6 | # 7 | # 8 | # 9 | # 10 | # 11 | # 12 | # 13 | # 14 | # 15 | # 16 | # 17 | # 18 | # 19 | # 20 | # 21 | # 22 | # 23 | # 24 | # 25 | # 26 | # 27 | # 28 |
| 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 6 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 8 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 9 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 11 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 12 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 13 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 14 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 15 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| CASH FLOW |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  | # ACTIVITY | # WEEKS |  |  |  | # WEEKS |  |  |  | # WEEKS |  |  |  | # WEEKS |  |  |  | # WEEKS |  |  |  | # WEEKS |  |  |  | # WEEKS |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | # 29 | # 30 | # 31 | # 32 | # 33 | # 34 | # 35 | # 36 | # 37 | # 38 | # 39 | # 40 | # 41 | # 42 | # 43 | # 44 | # 45 | # 46 | # 47 | # 48 | # 49 | # 50 | # 51 | # 52 | # 53 | # 54 | # 55 | # 56 |
| 16 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 17 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 18 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 19 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 20 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 21 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 22 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 23 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 24 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 25 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 26 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 27 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 28 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 29 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 30 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| CASH FLOW |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

TENDERER : ………………………………………..										DATE : …………………………………………

BID NO: FDDM/BID NO: 012/2023-24
T2.2.7: SUB-CONTRACTORS SCHEDULE

Should the Tenderer decide to execute certain portions of the work by employing additional subcontractors, this schedule must be completed.

| NAME AND ADDRESS OF SUBCONTRACTOR | DESCRIPTION OF WORK TO BE DONE BY SUB-CONTRACTOR | ###### % age OF CONTRACT | ###### VALUE OF WORK |
| --- | --- | --- | --- |

TENDERER : ………………………………………			DATE : …………………………………………

BID NO: FDDM/BID NO: 012/2023-24

T2.2.8: STAFFING PROFILE

The tenderer shall indicate in this schedule the number of site personnel to be employed on this project.

This information is material to the award of the Contract.

| ## DESCRIPTION | ## NON LOCAL LABOUR | ## LOCAL LABOUR |  |  |
| --- | --- | --- | --- | --- |
|  | ## * Key Staff | ## MEN | ## WOMEN | ## YOUTH |
| Contracts Manager Site Agent Foreman ### Technical Personnel Administrative Personnel Artisans Skilled Labour Unskilled Labour |  |  |  |  |
| #### TOTAL NUMBER OF PERSONNEL |  |  |  |  |

| DESIGNATION | NAME | QUALIFICATIONS Tertiary and/or NQF | EXPERIENCE AND PRESENT OCCUPATION |
| --- | --- | --- | --- |
| Contracts Manager (5 years, BTech or NQF 5) |  |  |  |
| Site Agent (min > 5 years or NQF 5) |  |  |  |
| Technical Personnel (min >3 years or NQF 4) |  |  |  |
| Construction supervisor (give designation) (min >3 years or NQF 4) |  |  |  |
| Other key staff (give designation) |  |  |  |
| NQF-Is the National Qualification Framework in South African Qualification Authority which can be contacted at www.saqa.org.za |  |  |  |

* Abbreviated CV's of key staff (max 2 pages) to be used in the project and their roles must be provided

TENDERER: ………………………………………			DATE: …………………………………………

BID NO: FDDM/BID NO: 012/2023-24

T2.2.9: ALTERATIONS BY TENDERER

Should the Tenderer desire to make any departures from or modifications to the General Conditions of Contract, Specification, Schedule of Quantities or Drawings, or to qualify his tender in any way, he shall set out his proposals clearly hereunder or alternatively state them in a covering letter attached to his tender and referred to hereunder, failing which the tender will be deemed to be unqualified.

| ## PAGE | ## CLAUSE OR ITEM |
| --- | --- |

TENDERER : ………………………………………			DATE : …………………………………………

BID NO: FDDM/BID NO: 012/2023-24

T2.2.10: CERTIFICATE OF TENDERER’S VISIT TO THE SITE

This is to certify that I, the undersigned Tenderer, visited the site on (date) ............................................

having previously studied the Contract Documents, I carefully examined the site.

I further CERTIFY that I am satisfied with the description of this work and explanations given by the said Engineer and that I understand perfectly the work to be done, as specified and implied, in the execution of this Contract.

Signature		…………………………………………

Name			…………………………………………

Capacity		…………………………………………

for the Tenderer	………………………………………………………………………………………………
			(Name and address of organization)

It is hereby confirmed that the above tenderer visited the site.

ENGINEER	………………………………………………………………………………………………
			FLAGG Consulting Engineers (Pty) Ltd

T2.2.11:	FINANCIAL ABILITY TO EXECUTE THE PROJECT

Provide details on the surety you will provide if the tender is awarded to you

Which of the following institutions will provide surety?

- Bank registered in terms of the Bank Act 1990 (Act 94 of 1990)

- Insurance Company registered in terms of the Short-Term Insurance Act 1998 (Act 53 of 1998)

- Cash

- Other (specify) 	………………………………………………………………………………

FINANCIAL STATEMENTS

I/We agree, if required, to furnish an audited copy of the latest set of financial statements together with my/our Directors’ and Auditors’ report.

DETAILS OF TENDERING ENTITY’S BANK

If the Tenderer is a Joint Venture or partnership, the information requested below is required for each member / partner.

I/We hereby authorise the Employer/Engineer to approach all or any of the following banks for the purposes of obtaining a financial reference:

| DESCRIPTION OF BANK DETAIL | BANK DETAILS APPLICABLE TO TENDERER |
| --- | --- |
| Name of bank |  |
| Contact person |  |
| Branch name |  |
| Branch code |  |
| Street address |  |
| Postal address |  |
| Telephone number | ( ) |
| Fax number | ( ) |
| Account number |  |
| Type of account, (i.e. cheque account) |  |

TENDERER’S TAX DETAILS

Tenderer’s VAT vendor registration number:

Tenderer’s SARS tax reference number:

TENDERER : ………………………………………			DATE : …………………………………………

# FEZILE DABI

DISTRICT MUNICIPALITY

John Voster Road									P O Box 10

SASOLBURG									SASOLBURG

1947

1947

Tel: 016 970 8600

Fax: 016 970 8762

_____________________________________________________________________________________________

Enquiries: Supply Chain Management Unit

MUNICIPAL SERVICES, RATES AND TAXES CLEARANCE CERTIFICATE FOR SUPPLY CHAIN MANAGEMENT PURPOSE

The purpose of this form is to obtain prove that municipal services, rates and taxes of the service provider are not more than three months in arrears with the relevant municipality / landlord in the municipal area where the service provider conduct his / her business. This form is to be completed only if the service provider’s rates and taxes are not in arrears for more than three months.

PART A – to be completed by the relevant municipality in the case where the service provider is the registered owner of the site / owner pays for municipal services / tenant pays for municipal services

OR

PART B – to be completed by the landlord in the case where the service provider is renting the premises / rental paid by tenant include municipal services.

PART A (TO BE COMPLETED BY THE RELEVANT MUNICIPALITY)

Name of the Municipality:

Property Physical Address:

Registered Name:

Official’s Name: ______________________________ Municipality Stamp Here Signature : ___________________________________ Date: ________________________________________ Please tick whether in arrears or up-to-date Rates and taxes : Up-to-date / in arrears for more than 3 months Water: Up-to-date / in arrears for more than 3 months Electricity: Up-to-date / in arrears for more than 3 months Refuse : Up-to-date / in arrears for more than 3 months Other services: Up-to-date / in arrears for more than 3 months

PART B ( TO BE COMPLETED BY THE LANDLORD)

Name of the Landlord:

Property Physical Address:

Landlord Signature:

Date: _______________________________ Landlord’s business stamp here Or an Affidavit from SAPS ( in the event the landlord does not have a business stamp) Please tick whether up-to-date or in arrears Rental: Up-to-date / in arrears for more than 3 months Municipal services: Up-to-date / in arrears for more than 3 months

BID NO: FDDM/BID NO: 012/2023-24
T2.2.13

MBD 8

# DECLARATION OF BIDDER’S PAST SUPPLY CHAIN MANAGEMENT PRACTICES

- This Municipal Bidding Document must form part of all bids invited.

- It serves as a declaration to be used by municipalities and municipal entities in ensuring that when goods and services are being procured, all reasonable steps are taken to combat the abuse of the supply chain management system.

- The bid of any bidder may be rejected if that bidder, or any of its directors have:

  - abused the municipality’s / municipal entity’s supply chain management system or committed any improper conduct in relation to such system;

  - been convicted for fraud or corruption during the past five years;

  - willfully neglected, reneged on or failed to comply with any government, municipal or other public sector contract during the past five years; or

  - been listed in the Register for Tender Defaulters in terms of section 29 of the Prevention and Combating of Corrupt Activities Act (No 12 of 2004).

- In order to give effect to the above, the following questionnaire must be completed and submitted with the bid.

| Item | Question | Yes | No |
| --- | --- | --- | --- |
| 4.1 | Is the bidder or any of its directors listed on the National Treasury’s Database of Restricted Suppliers as companies or persons prohibited from doing business with the public sector? (Companies or persons who are listed on this Database were informed in writing of this restriction by the Accounting Officer/Authority of the institution that imposed the restriction after the audi alteram partem rule was applied). The Database of Restricted Suppliers now resides on the National Treasury’s website(www.treasury.gov.za) and can be accessed by clicking on its link at the bottom of the home page. | Yes | No |
| 4.1.1 | If so, furnish particulars: |  |  |
| 4.2 | Is the bidder or any of its directors listed on the Register for Tender Defaulters in terms of section 29 of the Prevention and Combating of Corrupt Activities Act (No 12 of 2004)? The Register for Tender Defaulters can be accessed on the National Treasury’s website (www.treasury.gov.za) by clicking on its link at the bottom of the home page. | Yes | No |
| 4.2.1 | If so, furnish particulars: |  |  |
| 4.3 | Was the bidder or any of its directors convicted by a court of law (including a court of law outside the Republic of South Africa) for fraud or corruption during the past five years? | Yes | No |
| 4.3.1 | If so, furnish particulars: |  |  |
| Item | Question | Yes | No |
| 4.4 | Does the bidder or any of its directors owe any municipal rates and taxes or municipal charges to the municipality / municipal entity, or to any other municipality / municipal entity, that is in arrears for more than three months? | Yes | No |
| 4.4.1 | If so, furnish particulars: |  |  |
| 4.5 | Was any contract between the bidder and the municipality / municipal entity or any other organ of state terminated during the past five years on account of failure to perform on or comply with the contract? | Yes | No |
| 4.7.1 | If so, furnish particulars: |  |  |

CERTIFICATION

I, THE UNDERSIGNED (FULL NAME) …………..…………………………………….……..

CERTIFY THAT THE INFORMATION FURNISHED ON THIS DECLARATION FORM IS TRUE AND CORRECT.

I ACCEPT THAT, IN ADDITION TO CANCELLATION OF A CONTRACT, ACTION MAY BE TAKEN AGAINST ME SHOULD THIS DECLARATION PROVE TO BE FALSE.

………………………………………...		…………………………………………..……..

Signature 						Date

……………………………………….		…………………………………………..……..

Position						Name of Bidder

Js367bW

BID NO: FDDM/BID NO: 012/2023-24

T2.2.14

MBD 9

CERTIFICATE OF INDEPENDENT BID DETERMINATION

1	This Municipal Bidding Document (MBD) must form part of all bids¹ invited.

2	Section 4 (1) (b) (iii) of the Competition Act No. 89 of 1998, as amended, prohibits an agreement between, or concerted practice by, firms, or a decision by an association of firms, if it is between parties in a horizontal relationship and if it involves collusive bidding (or bid rigging).² Collusive bidding is a pe se prohibition meaning that it cannot be justified under any grounds.

3	Municipal Supply Regulation 38 (1) prescribes that a supply chain management policy must provide measures for the combating of abuse of the supply chain management system, and must enable the accounting officer, among others, to:

a.	take all reasonable steps to prevent such abuse;

b.	reject the bid of any bidder if that bidder or any of its directors has abused the supply chain management system of the municipality or municipal entity or has committed any improper conduct in relation to such system; and

c.	cancel a contract awarded to a person if the person committed any corrupt or fraudulent act during the bidding process or the execution of the contract.

- This MBD serves as a certificate of declaration that would be used by institutions to ensure that, when bids are considered, reasonable steps are taken to prevent any form of bid-rigging.

- In order to give effect to the above, the attached Certificate of Bid Determination (MBD 9) must be completed and submitted with the bid:

¹ Includes price quotations, advertised competitive bids, limited bids and proposals.

² Bid rigging (or collusive bidding) occurs when businesses, that would otherwise be expected to compete, secretly conspire to raise prices or lower the quality of goods and / or services for purchasers who wish to acquire goods and / or services through a bidding process.  Bid rigging is, therefore, an agreement between competitors not to compete.

MBD 9

CERTIFICATE OF INDEPENDENT BID DETERMINATION

I, the undersigned, in submitting the accompanying bid:

________________________________________________________________________

(Bid Number and Description)

in response to the invitation for the bid made by:

______________________________________________________________________________

(Name of Municipality / Municipal Entity)

do hereby make the following statements that I certify to be true and complete in every respect:

I certify, on behalf of:_______________________________________________________that:

(Name of Bidder)

- I have read and I understand the contents of this Certificate;

- I understand that the accompanying bid will be disqualified if this Certificate is found not to be true and complete in every respect;

- I am authorized by the bidder to sign this Certificate, and to submit the accompanying bid, on behalf of the bidder;

- Each person whose signature appears on the accompanying bid has been authorized by the bidder to determine the terms of, and to sign, the bid, on behalf of the bidder;

- For the purposes of this Certificate and the accompanying bid, I understand that the word “competitor” shall include any individual or organization, other than the bidder, whether or not affiliated with the bidder, who:

(a) 	has been requested to submit a bid in response to this bid invitation;

(b) 	could potentially submit a bid in response to this bid invitation, based on their qualifications, abilities or experience; and

(c)	provides the same goods and services as the bidder and/or is in the same line of business as the bidder

MBD 9

- The bidder has arrived at the accompanying bid independently from, and without consultation, communication, agreement or arrangement with any competitor. However communication between partners in a joint venture or consortium³ will not be construed as collusive bidding.

- In particular, without limiting the generality of paragraphs 6 above, there has been no consultation, communication, agreement or arrangement with any competitor regarding:

- prices;

- geographical area where product or service will be rendered (market allocation)

(c) 	methods, factors or formulas used to calculate prices;

(d)	the intention or decision to submit or not to submit, a bid;

(e) 	the submission of a bid which does not meet the specifications and conditions of the bid; or

(f)        bidding with the intention not to win the bid.

- In addition, there have been no consultations, communications, agreements or arrangements with any competitor regarding the quality, quantity, specifications and conditions or delivery particulars of the products or services to which this bid invitation relates.

- The terms of the accompanying bid have not been, and will not be, disclosed by the bidder, directly or indirectly, to any competitor, prior to the date and time of the official bid opening or of the awarding of the contract.

³ Joint venture or Consortium means an association of persons for the purpose of combining their expertise, property, capital, efforts, skill and knowledge in an activity for the execution of a contract.

MBD 9

- I am aware that, in addition and without prejudice to any other remedy provided to combat any restrictive practices related to bids and contracts, bids that are suspicious will be reported to the Competition Commission for investigation and possible imposition of administrative penalties in terms of section 59 of the Competition Act No 89 of 1998 and or may be reported to the National Prosecuting Authority (NPA) for criminal investigation and or may be restricted from conducting business with the public sector for a period not exceeding ten (10) years in terms of the Prevention and Combating of Corrupt Activities Act  No 12 of 2004 or any other applicable legislation.

…………………………………………………	……………………………………………………

Signature						Date

………………………………………………….	………………………………………………….…

Position 						Name of Bidder

Js9141w 4

VOLUME 3

CONTRACT

### C1.2  	CONTRACT DATA

### C1.2.1	SCHEDULE OF CONTRACT DOCUMENTS

THE FOLLOWING DOCUMENTS FORM PART OF THIS CONTRACT:

- “General Conditions of Contract for Construction Works Third Edition (2015)” prepared under the auspices of the South African Institution of Civil Engineers, The South African Association of Consulting Engineers and the Institution of Municipal Engineering of Southern Africa and the South African Federation of Civil Engineering Contractors.

- SABS 1200 – Standardized Specifications for Civil Engineering Construction (the applicable standardized specifications are listed in the Project Specification).

- Occupational Health and Safety Act. Act No. 85 of 1993.

- This volume containing Conditions of Tender, Special Conditions of Contract, the Project Specification, Bill of Quantities, Contract data, Agreement, Schedules, etc.

### C1.2.2	GENERAL CONDITIONS OF CONTRACT

The General Conditions of Contract that apply to this contract are:

General Conditions of Contract for Construction Works Third Edition (2015).

As prepared under the auspices of the South African Institution of Civil Engineers, South African Association of Consulting Engineers and the Institution of Municipal Engineering of Southern Africa and the South African Federation of Civil Engineering Contractors.

Copies of this document may be purchased from:

| - The Secretary SAICE East Wing Howick Gardens Waterfall Park BekkerStr Vorna Valley Midrand | - The Secretary SAACE St James House Hampton Park North 20 Georgian Crescent Bryanston Sandton 2021 | - The Secretary SAFCEC 12 Skeen Boulevard Bedfordview 2008 |
| --- | --- | --- |

It is deemed that the Contractor is in possession of, and has read and understood the “General Conditions of Contract” described above.

### C1.2.3	SPECIAL CONDITIONS OF CONTRACT

The following definitions and conditions apply to this Contract and the Employer undertakes that the only variations from the General Conditions of Contract, Third Edition (2015), are as follows:

#### CLAUSE

### DEFINITIONS, INTERPRETATIONS AND GENERAL PROVISIONS 1.1.1.15 The "Employer" means FEZILE DABI DISTRICT MUNICIPALITY 1.1.1.16 The "Engineer" means FLAGG CONSULTING ENGINEERS (PTY) LTD ##### ENGINEER AND ENGINEER'S REPRESENTATIVE 3.1.3 The duties and functions of the Engineer requiring the specific approval of the Employer before execution of any of these duties are as follows: i) Any variation of the form, quality of quantity of the Works or any part thereof which will result in the Tender Sum being exceeded irrespective of the magnitude of the over expenditure; ii) Any payment, which will result in the tender sum being exceeded irrespective of the magnitude of the over expenditure. ##### BASIS OF CONTRACT 4.2.2 In addition to what is stated in Clause 4.2.2, in matters relating to the safety of workmen or the public the Contractor shall comply with any instruction issued by the Employer’s Safety officer. Add Clause 2.6 to read as follows : 2.6 Occupational Health and Safety Act

4.4.6 Add the following to Sub-clause : 4.4.6 ##### “Should the employer make payment directly to a Nominated or Emerging Subcontractor in terms hereof, consequent on default on the part of the Contractor, the Contractor shall be deemed to have forfeited all his rights to receive payment of “handling charges”, “commission” and/or other fees and charges to which, in terms of the Contract he would otherwise have been entitled, in respect of the amount so paid by the Employer directly to the nominated Subcontractor. If the Subcontractor fails to pay his labourers then the Employer reserves the right to pay such labourers directly from the contract or to nominate the Contractor to pay such labour. The Subcontractor shall be deemed to have forfeited all his rights to receive payment in terms of the contract or any subcontract.”

##### COMMENCEMENT OF WORKS 5.3 Add Clause 5.3 to read as follows : ### The Contractor shall not start any work before receipt of the Engineer’s instruction; which instruction is subject to the submission by the contractor of documentation required as set out in the Contract Data. 5.9 Add Sub-clause 5.9.8 to read as follows : “The Engineer shall give the survey details to the Contractor, where after the Contractor shall be responsible to establish his own benchmarks, reference pegs and setting out of the Works.” “The Contractor shall take care not to disturb or destroy property beacons, trigonometrical survey beacons or setting out beacons. A registered Land Surveyor who shall certify such replacement shall replace property and trigonometrical survey beacons that have been destroyed or disturbed. The cost of replacing all beacons that have been disturbed or destroyed during the course of the Contract shall be borne by the Contractor.”

CONTRACTOR’S GENERAL OBLIGATIONS 4.5.1.2 Add the following at the end of Clause 4.5.1.2 : The Contractor shall pay particular attention to the contents of the following Acts : - Section 59 of the Industrial Conciliation Act No 28 of 1966 and any amendments thereto. NB: Unskilled labour in the building industry are subject to an agreement in terms of the said Industrial Conciliation Act. - Machinery and Occupational Safety Act No 6 of 1983 as amended. - Workmen’s Compensation Act No 30 of 1941.

#### CLAUSE

PROGRESS AND TIME FOR COMPLETION 5.12.2 Add the following to this sub-clause : Time is an essential element to the agreement. The Contractor will submit his claim for extension of time, either written at the normal site meetings, or in accordance with the conditions stipulated in the General Conditions of Contract. 5.12.2.2 Abnormal climatic conditions The Contractor must supply a rain gauge on site. The amount of rain must be recorded daily by the Engineer’s Representative and the Contractor for discussion at the site meetings. No extension of time of completion will be granted for normal rainfall, but extension of time in terms of clause 5.12 of the General Conditions will be calculated according to the following formula, separately for each calendar month or part thereof. This will be calculated for the whole time of completion including any extension thereof that may be granted: E = (Nw – Nn) + (Rw – Rn) if (Nw – Nn) > 0. 20 WHERE E = Extension of time in calendar days in respect of the calendar month under consideration. Nw = Actual number of days during the calendar month under consideration on which a rainfall of 10mm or more had been recorded. Nn = Average number of days in the relevant calendar month as derived from existing rainfall records provided in the project specification on which a rainfall of 10mm or more has been recorded. Rw = Actual rainfall in mm for the calendar month under consideration. Rn = Average rainfall in mm for the calendar month as derived from the rainfall records supplied in the project specifications.

The total extension of time shall be the algebraic sum of the monthly totals for the period under consideration. But if the grand total is negative, the time for completion shall not be reduced on account of abnormal rainfall. Extension of time for parts of a month shall be calculated by pro-rata values of Nn and Rn being used. The factor (Nw – Nn) shall be considered to represent a fair allowance for variations from the average number of days during which rainfall exceeds 10mm. The factor Rw – Rn shall be considered to 20 represent a fair allowance for variations from the average for the number of days during which rainfall does not exceed 10mm but when wet conditions prevented or disrupted work. This formula does not take into account any flood damage, which could cause further or concurrent delays and should be treated separately in so far as extension of time is concerned. Accurate rain gauging shall be taken at a suitable point on the site, and the contractor shall, at his own expense, take all necessary precautions to ensure that the rain gauges cannot be interfered with by unauthorized persons. Should Nw for any month be smaller than Nn, the following formula shall be used: E1 = (Nn – Nw) Therefore, the total extension of time for completion will be the difference between E and E1. Total extension of time = E – E1.

| #### CLAUSE |  |  |  |  |
| --- | --- | --- | --- | --- |
| 5.12.2.2 The following are the most reliable figures of Nn and Rn available and shall be used should no agreement be reached beforehand. SOURCE OF INFORMATION : WEATHERBURO, PRETORIA Rainfall district : MAFAHLANENG/TWEELING |  |  |  |  |
|  | ##### MONTH | ##### Nn | ##### Rn |  |
|  | January February March April May June July August September October November December | 3.6 3 2.4 1.4 0.7 0.2 0.3 0.4 0.9 2.6 3.2 3.9 | 103.4 91.8 73.6 38.9 19.9 7.2 8.9 13.8 31.2 77.9 99.5 110.1 |  |
|  | ##### YEARLY AVERAGE |  | ##### 676.2 |  |
| This formula does not take account of flood damage, which could cause further or concurrent delays and will be treated separately as far as extension of time is concerned. |  |  |  |  |
| 6.8.2 The CPAF should be calculated according to the formula and the conditions as set out in the Contract Price Adjustment Schedule on page 93 of the General Conditions for Construction Works, Second Edition, 2010. 6.8.3 Price adjustments for variations in the costs of special materials are allowed. 10.7.1 The determination of disputes shall be by arbitration. PROVISIONS 9.2. In additional to but without limiting the provisions of Clause 7.9 the following shall apply : “If the Contractor fails to execute the works in accordance with the provisions of the Contract the Engineer may give notice in writing to the Contractor to make good the failure, delay or default and should the Contractor fail within seven (7) days to commence effective action to remedy the failure, delay or default then and in such case, the Engineer shall without prejudice to any rights under the Contract, and without invalidating the Contract, be at liberty to take such work out of the Contractor’s hands and contract with any person or persons to complete such work. The cost to the Employer of so completing such work will be payable by the Contractor.” CESSIONS 6.10 Add the following to this sub-clause : - Cessions will only BE ALLOWED on payment of material, labour and management. - Any other requests for cessions must be submitted to the Municipal Manager for consideration. - Cessions will not be allowed on newly awarded tenders. Contractors / companies may only apply for a cession after half of the timeframe allowed for the completion of the project has lapsed. |  |  |  |  |

#### CLAUSE

ACT No 85 OF 1993 OCCUPATIONAL HEALTH AND SAFETY ACT The employer and the contractor hereby agree, in terms of the provisions of Section 37(2) of the Occupational Health and Safety Act, Act No. 85 of 1993, hereinafter referred to as “the Act”, that the contractor as an employer in its own right and in its capacity as contractor for the executions of the works, shall have certain obligations and that the following arrangement shall apply between them to ensure compliance by the contractor with the provisions of the Act, namely- - The contractor undertakes to acquaint the appropriate officials and the employees of the contractor with all relevant provisions of the Act, and the regulations promulgated in terms of the Act, and - The contractor undertakes that all relevant duties, obligations and prohibitions imposed in terms of the Act and regulations will be fully complied with, and - The contractor hereby accepts sole liability for such due compliance with the relevant duties, obligations and prohibitions imposed by the Act and regulations and expressly absolves the employer and the employer’s consulting engineers from being obliged to comply with any of the aforesaid duties, obligations and prohibitions in respect of the work included in the contract. - The contractor shall be obliged to report forthwith to the employer any investigation, complaint, or criminal charge which may arise as a consequence of the provisions of the Act and regulations pursuant to work performed on behalf of the employer, and shall, on written demand, provide full details in writing of such investigation, complaint or criminal charge. - The Contractor shall submit a complete Health and Safety Plan, in accordance with the Act prior to the commencement of any permanent work for approval by the engineer. Addendum C contains the pre contract Health and Safety Specification which must be used as a guideline by the Principal Contractor and his appointed Sub Contractors to compile the Health and Safety Plan for this project and forms part of the tender documentation. The Contractor must include as part of the Health and Safety Plan a procedure to create HIV/AIDS awareness amongst all of the workers involved in the project for the duration of the project, through the following strategies : - Awareness about HIV/AIDS must be raised through education and information on the nature of the disease, how it is transmitted, safe sexual behaviour, attitudes towards people affected and people living with HIV/AIDS, how to live a healthy lifestyle with HIV/AIDS, the importance of voluntary testing and counselling, the diagnosis and treatment of Sexually Transmitted Infections and the closest health Service Providers. - Informing workers of their rights with regard to HIV/AIDS in the workplace. - Providing workers with access to condoms and other awareness material that will enable them to make informed decisions about sexual practices.

C1.2.4	CONTRACT DATA: PROVIDED BY THE EMPLOYER & PROVIDED BY THE CONTRACTOR

The above Contract Data have been placed for convenience after Part C1.1Agreement and Contract Data page 30, for this tender stage.

PART C2: PRICING DATA

C2.1 	PRICING INSTRUCTIONS

Pricing instructions are incorporated in Part T1.2.1 Instructions to Tenderers; page 5 to 9.

C2.2 	SCHEDULE OF QUANTITIES

The Schedule of Quantities have been placed for convenience after Part T2.1 from page 36 for this tender stage and will be incorporated as part of the contract at project implementation stage.

### FEZILE DABI DISTRICT MUNICIPALITY

DRILLING AND EQUIPPING OF SIX NEW BOREHOLES AND REFURBISHMENT OF TWO EXISTING BOREHOLES IN MAFAHLANENG/TWEELING

BID NO: FDDM/BID NO: 012/2023-24

### PART C3: PROJECT SPECIFICATIONS

### SCOPE OF WORK

This project specification consists of two parts. Part C3.1 contains a general description of the project and the requirements that shall be adhered to. Part C3.2 contains the variations on and additions to the standardized specifications applicable to the contract.

# STATUS

All the Clauses in the General Conditions of Contract and the Special Conditions of Contract shall apply to the full extent of the contract and each distinct part thereof. The Project Specifications shall be read in conjunction therewith. The Project Specification is additional to and an extension to any other specification, and should any requirement or clause of the Project Specification conflict with other parts of the Specifications and/or General Conditions of Contract and/or Drawings, the requirements and stipulations of the Project Specifications shall apply. It shall be borne in mind that only the Parts of the Specification relevant to the Work, which is described in this Contract, be applicable on the Contract.

C3.1 	SCOPE OF WORK

C3.1.1	General Description of the Works

The work will consist of the Drilling and Equipping of Eight new Boreholes and refurbishment of two existing boreholes in Mafahlaneng/Tweeling to alleviate the shortage in bulk water distribution in Mafahlaneng, to the clean water distribution network of Tweeling and Mafahlaneng.

C3.1.2	Details of the Contract

C3.1.2.1	Pumping Mains

The following pumping main will be constructed as part of this project and can be observed on the drawings:

- 50mm HDPE Class PN12.5 – Total length as per BOQ

- 75mm HDPE Class PN12.5 – Total length as per BOQ

- Various boreholes pumping mains will also be constructed as part of this project. The position where the borehole pumping mains are to be connected was unknown at the time that the tender document was compiled. An on-site assessment will be done during construction of the project to determine the connection point of each borehole. Each borehole will preferably be connected to the closest reservoir for optimum water distribution purposes. Where connection to an existing reservoir is not possible, the engineer will determine a suitable connection point to an existing network pipe. A provisional sum has been allowed in the BoQ for connecting new borehole pumping mains to existing infrastructure.

C3.1.2.2	Fittings and Specials (All Steel Pipework for Boreholes):

Pipe Section exposed to the sun & Interconnecting pipework.

Material type	:	Mild Steel to SABS 719 from grade X42/300WA

External protection 	:	Hot dip galvanised coating

Internal protection 	:	Hot dip galvanised coating

C3.1.2.3       Boreholes

| Name | Y | X | Pump depth. (m) | Elevation differential (BH – RES) | Total BH Static Head (m) |
| --- | --- | --- | --- | --- | --- |
| CBH01E | 14225.289 | 3014549.711 | 85 |  | 86.75 |
| CBH01N | 14215.554 | 3014402.880 | 100 |  | 158.75 |
| CBH02E |  |  | 100 |  | 158.00 |
| CBH02N | 14634.947 | 301477.419 | 100 |  | 149.03 |
| CBH03N | 14811.311 | 3014525.773 | 100 |  | 141.93 |
| CBH04N | 14200.212 | 3013144.58 | 100 |  | 141.93 |
| CBH05N | 14401.463 | 3012567.998 | 100 |  | 141.93 |

Eight (8) boreholes will be equipped as part of this project. Each borehole will be equipped with a new submersible pump sized according to the required head and flow from the specifications below. Each borehole will be provided with an HDPE delivery pipe, electrical cable and pump extraction cable down the shaft of the borehole. New electrical cables will be provided from Eskom/Municipality connection to the MCC panel and from the MCC panel down into the borehole shaft. Each borehole will be equipped with the following delivery pipework at the borehole structure:

- Non-return valve

- Mechanical Water Meter with telemetry function.

- Water quality sampling tap.

- Pressure gauge.

- Plug fitted to galvanized fitting for pressure switch on electrical installations.

- Butterfly gate valves as indicated.

- Air valve when required based on the topography for each individual borehole.

Electromagnetic flow meters:

Electromagnetic flow meters shall be of the Krohne, Safmag Beta Meter type or similar approved will be acceptable.

Mechanical flow meters:

The contractor shall present to the engineer for approval the type of mechanical water meters to be installed on the project.

C3.1.2.4	Security Fence

The client has made provision for the costing of two types of fences namely:

- Steel palisade fencing (Option 1):

The fence shall be constructed of mild steel and protected by means of a fusion epoxy coating to a minimum thickness of 300-micron meter (Red oxide)

- Clear-VU fencing (Option 2):

The fence will be of the 358 Singleskin System developed for applications requiring for high degree of security. The fence will be vandal resistant with anti-cut robust wire and weld joint and anti-climb features. (Clear-VU of similar approved supplier)

C3.1.2.5	Concrete:

Concrete shall have a cube strength of 25 MPa at 28 days and shall be rendered workable (75mm slump) through selections of the correct cement / water ratio required by the aggregate or by the use of an approved plasticizer. The concrete shall contain a minimum of 350 kg of OPC per m³ for imperviousness and durability.

C3.1.2.6	Reinforcing Steel:

High tensile (450 MPa) reinforcing steel will be installed in all structural members (roof, wall, floor) to counter and limit crack formation to tolerable levels.

C3.1.2.7	Foundations:

Excavations will be founded on suitable material as indicated by the engineer and on the drawings. Over excavation will be backfilled with 10 MPa concrete to blinding level.

C3.1.2.8	ELECTRICAL REQUIREMENT

The electrical requirement is such that per borehole 6 kVA single phase supply will suffice.

The smallest connection Eskom can provide is a 16kVA pole mounted single phase transformer with 60Amp single pole circuit breaker. This is sufficient for a borehole pump to a max of three pumps on one transformer should it run simultaneously.

The transformer required will then be finalised in accordance with the grouping of the boreholes as has been arranged per table C3.1.2.2

Electrical Specification

Electrical specifications for all mechanical equipment are clearly indicated on all the drawings. Provisional sums have been allowed in the bill of quantities for all electrical items where specifications is not currently available due to lack of existing information available.

C3.1.2.9	WATER SAMPLE ANALYSIS AND PURIFICATION PROCESS DESIGN

Analysis of all the samples tested to SANS 241 indicate two main problems: bacteria and suspended solids. Further analysis indicates there are no other problems (based on the analyses received) than microbial contamination and colour/turbidity.

So hence the purification process described below will work in most of them. However, in order to do an accountable design, all the boreholes must be analysed and weight/flow data analyses done to determine what each reservoir will receive, and then base the design on the calculated values. If other short cuts are taken, it will not pass scrutinising.

What is required is an in-line flocculant dosing, with flocculation and a conservatively sized sand filter, followed by disinfection with chlorine (which can be done in-line). For each site it is assumed that the bore hole pump will pump through the filter and then into an elevated clear water tank. Up to 60m pressure can be handled straight through the filters to the elevated tank / demand reservoir.

Alternatively, where there are only one or two boreholes in the higher lying areas a typical treatment plant consisting of disinfection, coagulant and dual media filtration would work; where the streams go to R5 and estimated typical size would be 1000kl/day.

C3.3.3		PROJECT SPECIFICATIONS ELECTRICAL

C3.3.3.1	SCOPE

The scope of electrical work is as follows:

Design, supply, install and commission the following:

- MCC 1: Raw water pump station.

- Site wiring, according to the lay-out at tender stage

- Site lighting (based on the site lay-out)

- Small power and lighting in the raw water pump station.

MCC panels will be fitted with a volt meter to all phases and amp meter to each motor. Full specification to be provided with electrical tender document.

C3.3.3.2	POWER SUPPLY

The power supply consists of 3 Phase, 50 Hertz, 500kva supply, installed by other into the existing pump station building and laid up to the main distribution board.

It shall be required of the contractor under this contract to make the necessary connections of the supply cable to the terminals of the main distribution board.

C3.3.3.3	CABLING TO MECHANICAL ELEMENTS AND SITE LIGHTING

All cabling shall be suitable for underground installation, wire armoured P.V.C. cables to SABS 150: 1957 or as amended. Cable connections shall be kept to a minimum and when required made with “Scotch-cast” or similar approved patented means. All cables shall be sized for full load plus an allowance of 30%.

Cable trenches will be excavated by the contractor for the civil works.

C3.3.3.4	CIRCUITS

The following existing circuits shall be accommodated in the new control panel:

Circuit containing all the existing lights in the Structures.

Circuit containing 2 new Pole mounted 160w High Pressure Sodium Lamps.

Circuit containing ceiling mounted 2 x 1200mm 75w fluorescent tube lights for the Buildings.

C3.3.3.5	EARTHING

All cable sheaths and armouring, switchgear, etc, are to be earthed by use of amply rated bare copper earthing strings connected to suitably located earthpikes and shall comply with the requirements of SABS: 0142 –1981. The existing system shall be checked and upgraded if required.

C3.3.3.6	CABLING AND WIRING

All cabling and wiring shall comply with the requirements of the Local Authority as well as SABS: 0142 –1981: Code of Practice for the Wiring of Premises.

|  | Panel Numbering and Labels The tiers on each MCC shall be numbered consecutively from left to right, when facing the front of the MCC. The cubicles in each tier will then be allocated consecutive letters of the alphabet, starting with the letter A and reading from top to bottom. Each letter shall be prefixed with the tier number. The top of each rear access cover shall be clearly labelled with the tier number. Each cubicle shall be fitted with a circuit designation label on its front cover. In addition to the identifying label mounted on the front panel for each starter cubicle, a similar label shall be mounted at the rear of each cubicle to be visible when the rear covers are removed and shall indicate the tier number, cubicle letter and the circuit designation. Components such as circuit breakers. isolators, indicating lamps, switches, relays, Instruments, test blocks, fuses, etc" shall be clearly identified with engraved labels Indicating their function, Where a multiple drive cubicle is supplied, a label listing all the drives in that cubicle shall be provided on the door of that cubicle. Labels shall be of plastic "sandwich" board material, the legends being engraved through the front layer to the contrasting inner layer, The lettering shall not be less than 6 mm high in sans-serif capitals, black lettering on a white background shall be selected to ensure maximum legibility, All labels shall be secured by at least two bolts, or rivets per label, and shall be accurately level and on the centre line of their subjects, Glued labels, adhesive embossed plastic tape or paper labels are not acceptable, All label inscriptions shall be in English, and all label designation lists shall be approved by the Engineer prior to engraving. |
| --- | --- |
|  | Inspection and Testing All MCC's shall be inspected by the Engineer or his representative, when fully assembled and complete with ail equipment, prior to despatch from the suppliers' works, The following tests will be required, at the Inspectors' discretion, prior to despatch from the suppliers' works: - High Voltage pressure tests - Primary current injection tests of all protection relays - "Megger" insulation tests - Complete functional and operational tests, |
|  | Delivery and Erection The Contractor shall be responsible for the delivery to site, off-loading, erection, and cold commissioning of all the MCC's. |

LOW VOLTAGE SWITCHBOARDS

|  | General The switchboard(s) shall comply with BS 5486, IEC 439, the Occupational Health and Safety Act of 1993, and local authority's requirements. Switchboards shall be floor or wall mounting type with front access or free standing with front and/or rear access, as specified. The switchboard(s) shall be dustproof, vermin proof and adequately ventilated to prevent overheating of the equipment. Drawings of the switchboard(s) shall be submitted to the Engineer for approval prior to manufacture. Surface mounted cartridge type fuses for instrument protection, as specified, shall be mounted on the busbars. Current transformers (ratio and burden as specified) shall be of the pedestal type or as noted and shall be securely mounted in the switchboard. The completed switchboard(s) may be inspected by the Engineer at the manufacturer's works prior to despatch. The Electrical Contractor shall inform the Engineer timeously in writing when the switchboard(s) IS ready for inspection. |
| --- | --- |
|  | Construction The switchboard(s) shall be of robust construction consisting, in general, of a channel, box or angle iron frame covered with sheet steel panel(s) of 1,6 mm minimum thickness. The panel(s) shall be reinforced to prevent distortion and to ensure rigidity. The electrical equipment shall be flush mounted on a chassis within the switchboard. The panel shall be suitably slotted or drilled to allow the operating handles of the switchgear to protrude. Removable panels shall be provided for access to the wiring, busbars, and equipment. The panels shall be held in position by chromium plated coin slot. square key or knurled captive thumb screws. Switchboards shall have lockable doors where specified. Space for 50% spare ways, unless otherwise noted, shall be allowed on the switchboard for future equipment. Each spare outgoing way shall include sufficient space for future switchgear and associated instrumentation, like the equipped outgoing ways. All drilling, cutting or any other metalworking operations shall be completed prior to any paint process being undertaken. Prior to painting, all metal parts shall be prepared to SANS 064 clause 6.22 for high quality - finished commodities; medium weight phosphating may be employed. In the period 24 - 96 hours after phosphating, a high-quality zinc-chromate primer to SANS 679, Type 1, shall be applied, followed by two coats of high quality alkyd based enamel to SANS 630. Care shall be taken to cover all edges properly. The paint to be used shall have an impact resistance of 9 kg on a 9 mm mild steel plate and a scratch resistance of 1000 grams. After baking, the minimum film thickness of the paint shall not be less than 0,06 mm. The switchboards shall be finished in the colour specified on the outside and white on the inside. |
|  | Busbars Aluminium and copper busbars shall have joints of adequate contact area for the currentrating and to prevent joint relaxation by cold flow of the metal. Spring washers shall be used when bolting joints. All joints in the busbars shall be firmly bolted together with suitable high tensile steel bolts and nuts. Spring washers shall be used. Bolted joints shall be designed to maintain contact pressure permitting rated current at rated temperature and thermal expansion without buckling of busbars. Joints shall not loosen under vibration. Joints on aluminium busbars shall be suitably prepared. The manufacturer shall specify the tightening torque to be applied to bolted joints in busbars. All busbars shall be carried on insulated supports placed at intervals not exceeding 600 mm for main busbars, or 300 mm for busbars droppers. They shall be adequately identified in phase colours. Connections to busbars shall be made by means of bolted take-offs. Busbar insulator material shall be Tufnol of suitable grade, or equivalent, shaped, and spaced to provide protection against tracking, flashover or distortion of busbars. The insulators shall be tested in accordance with SANS 161. The moisture absorption resistance shall be in accordance with SANS 161. Incoming and outgoing busbar stubs, where required, shall be suitably insulated where they pass through the top panels of the switch board and shall be suitably and firmly supported within the board. Incoming and outgoing collector bars for cables in parallel shall be so arranged that the multiple cable ends can be connected to the collector bars with reasonably short tails to eliminate crossing of conductors. Busbar droppers to and from circuit breakers shall not be supported only by the circuit breaker terminals (or the circuit breaker cradle terminals) and the main bus bars but shall also have a suitable intermediate insulated support. Heavy out going cables shall be supported so that there is no undue strain on circuit breaker or circuit breaker cradle terminals. Where stub bars are used to accommodate large cable ends at the circuit breaker terminals, the Electrical Contractor shall ensure that the clearance between phases is adequate. |
|  | Switchgear General All switchgear shall be flush mounted behind removable panels with operating handles only projecting through suitable machine punched slots or holes. Equipment of normally surface-mounted types such as energy meters, time switches and relays, shall be mounted on suitable chassis behind hinged front panels. In the case of inserts to facilitate reading the meter. |

|  | Earthbar Each board shall be equipped with a copper earth bar of sufficient length to allow for the termination of all the incoming and outgoing earth conductors. The size of the earth bar to be as noted on the drawings. The earth bar shall be complete with adequate brass bolts and nuts. |
| --- | --- |
|  | Cable Entries and Terminations Cable gland plates shall be galvanised and of at least 3 mm thickness. The gland plate shall be bonded to the main earth bar with a copper earth strap having a cross-sectional area equivalent to that of the earth bar. When cables enter the top of the board a similar cable gland plate shall be incorporated in the top of the switchboard and shall be connected to the main earth bar in a similar manner. Spare entry holes in the top gland plates shall be provided with galvanised blank seals. Gland plates and cable end support bars must be placed at suitable heights having regard to the bending radii of the cables concerned and convenience in making off. The support bars should preferably be of a section like "Unistrut" and be fitted with sliding clamping bolts. The entire board shall be vermin proof and at the gland plate the vemnin-proofing shall consist of expanded metal of a suitable gauge secured to the gland plate and the framework of the board. |
|  | Wiring All internal wiring shall be laced or run in wiring channels and shall be clearly marked with numbered ferrules and colour coded. Stranded wire shall be used having a minimum area of cross-section of 2,5 mm2 and shall comply with SANS 150. Where circuit breaker terminals are designed to take stranded conductors, PVC insulated stranded conductors shall be used. The jumpers to each breaker shall be separately run and the individual conductors in each set separated from each other by a spreader secured to the conductor to prevent movement during fault conditions and to maintain conductor spacing. All equipment shall be clearly labelled as specified. The labels shall be of Ivorine, or plastic secured by screws or rivets. All switchboards shall be labelled as specified. Glass- or clear perspex- covered, framed legends shall be fixed to the boards or adjacent thereto. All fuse-switches, circuit breakers and other apparatus on switchboards shall be labelled to indicate their function. The incoming isolating switch or circuit breaker on each board shall be labelled "Main Switch". 10 mm high letters shall be provided on each switchboard indicating voltage present. All labels shall be in the language(s) specified. All masking tape and other temporary markings are to be removed on completion of the installation work. The Electrical Contractor shall provide separate diagrammatic charts showing essential features of the as-installed electrical system, including single line and riser diagrams on which equipment designation shall correspond with labels. |  |

|  | Notices The following notices in compliance with the Occupational Health and Safety Act of 1993, in the languages specified, shall be supplied, and installed by the Electrical Contractor. - Notice prohibiting unauthorised persons from entering the switch room or substation. - Notice prohibiting unauthorised persons from handling or interfering with electrical apparatus. - Notice containing directions as to procedure in case of fire. - Notice containing directions as to restoration of persons suffering from the effects of electric shock. - Danger notices (skull and crossbones). The notices defined above shall be mounted on the outside of the switchroom/substation door(s). All other notices shall be mounted in a conspicuous position inside the switchroom/substation. The notices shall comprise black embossed letters, at least 15 mm high, on a yellow backplate. |  |
| --- | --- | --- |
|  |  | Guarantee The tenderer shall give 12 months guarantee to replace free of charge any parts of the low voltage switchboard 'In which manufacturing defects may develop during this period. Such period shall commence from the date on which the switchboard is taken over by the Client |  |

TELEMETRY

|  | Scope This specification covers the specification of the data capture and communication equipment required in the Telemetry System. Aspects covered are: - The Control, Input and Output Modules. Power Source and Enclosures. - The Communication Media and Equipment. Surge Protection - Data Protocols. - The System Modes of Operation. Documentation, Commissioning and Training |
| --- | --- |
|  | Hardware Organisation General Only systems designed specifically for radio-based tele-control shall be considered for this project. Systems designed for network or twisted pair linkup and adapted for radio communications will not be accepted for this project. The use of a personal computer as a station controller will not be considered, A telemetry station shall consist of one CPU Module, selected Input and Output Modules, a power supply and a communications system, together in a cabinet. The CPU Module shall be equipped with a CPU watchdog timer circuit that will automatically restart the system in case of severe electrical disturbance. The telemetry CPU Module shall be auto-configuring. It shall determine automatically which I/O module is connected, data addressing, and mode of operation to run. It shall not be necessary to use a programmer/lap-top/PC to setup any outstation. Physical Layout The CPU and I/O Modules shall be mounted on standard DIN-rail. Rack-mounted modules that use high-density connectors onto a back-place will not be accepted for this project The radio, power supply/charger and batteries shall be securely fixed with brackets to the inside of the cabinet The radio shall connect to the CPU Module via a robust connector and a wiring harness. The I/O Modules shall connect to the CPU Module by ribbon cable in 'daisy chain' fashion. High quality connectors with eject latches and strain relief for reliability shall be used. Input and Output connections to the I/O Modules shall be via robust plug-in screw termination strip. The I/O Module shall be able to be unplugged and removed without unscrewing the field wiring. The PCB connectors shall be shrouded to ensure that they cannot be misaligned when plugged in. Barrier Modules shall be used to provide additional buffering or signal conditioning for the 110 Modules. These modules shall be separate, field replaceable items. They shall mount onto standard DIN-rail. Wire connections to the Barrier Modules shall use the same type of plug-in screw terminations as the I/O Modules. I/O Signal Lines Digital Status Input (for "dry contact" sensing) shall be active low and protected for accidental voltage input of up to 24 VDC. Cable lengths of up to 20 m unscreened and 100 m screened shall be accommodated. Optional barrier modules shall provide further signal buffering. Digital Status Inputs (for opto isolation) shall be able to accept input of any polarity from external power source of 12, 24, 36, 50 or 110 VDC. Isolation shall be rated at 1500 VAC and 1000 VDC continuous. Digital (Control) Output lines shall be active low, open collector transistors with a rating of 27 VDC (OFF) and 200 mA current sink (ON). Suitable protection shall be provided on the Module to protect the output transistors if relay coils are driven from the Digital Outputs. Relays on control outputs shall have contact rating of 8 A at 240 VAC. These shall be included as buffering for digital outputs where necessary. Analog Input lines shall accommodate 0 - 5 VDC, 0 - 10 VDC, 0 - 20 mA or 4 - 20 mA input signals. This may be achieved directly by the I/O Moduie, or via separate barrier modules. The resolution shall be 0.5 % (8 bit) or 0.1% (12 bit) bit. The 12-bit option shall have differential inputs (no common ground) with common mode voltage rejection of 20 VDC. Analog Output lines shall similarly accommodate 0 • 5 VDC, 0 - 10 VDC, 0 .20 mA or 4 - 20 mA output signals. The choice of output signal shall be independent of the choice of corresponding input signal. The output accuracy shall be better than 0,5 % (8 bit) or 0.1 % (12 bit). Counter Inputs shall be suitable for accumulating up to 65000 pulses (16 bits) at the outstation, at a rate of up to 50 pulses per second. Input shall be suitable for either semiconductor switch (e.g., open collector/drain from flow measuring device) or dry contact. Serial (RS 232) Interface The telemetry system shall be able to be interfaced to a Personal Computer, PLC, local controller etc. This shall be achieved via standard RS232 hardware link. The RS232 serial port shall be able to operate at 300, 1200, 2400, 9600 or 19200 baud. Handshake protocol should include XOn/XOff, CTS/RTS and none (direct). Power Supply Power from several sources must be able to be used to power a telemetry station. These will usually be one of the following: Mains Only: An industrial type power supply shall be used to provide 13,8 VDC for the station. The power supply output shall be rated at 50 % greater than the peak required by the system. Mains with Battery Backup: A battery shall be chosen to suit the backup time required with the calculated static load. A fully operational backup time of 8 hours is required unless otherwise specified. The charger shall be rated to completely recharge the battery within 10 hours while delivering the static load. Battery Choice Batteries less than 15 Ah capacity shall not be used due to the high peak discharge current during radio transmission. Nickel Cadmium batteries shall not be used. Sealed, gel type lead-acid batteries shall be used for capacities up to 65 Ah and may be housed in the same enclosure as the telemetry equipment. Vented lead-acid storage cells designed for standby applications shall be used for larger capacities, these liquid based storage cells shall be housed in a separate, vented enclosure. Enclosure A typical indoor station shall be housed in a wall mounted 1,6 mm mild steel electrical type enclosure. Finish shall be epoxy coated grey. Swing-frame and 19" rack type enclosures are expensive and will not be beneficial to the operation of the system on this project. Weather resistant enclosure to IP55 specification shall be available as an option and shall be included for wet environments ego pump rooms and valve chambers. For an outstation location where no building protection is available (e.g.: a reservoir, borehole, or pylon), a larger steel or fiberglass enclosure shall be used to protect the inner all-weather enclosure to IP55 protection. The outer enclosure shall provide vandal and weather protection, as well as ventilation around the inner enclosure. The assembly can be wall, base, or pole mounted. Communications Channel - The Telemetry system must be able to operate on: - Radio Channel (at 300 or 1200 baud FSK) - GPO Landline/Pilot cable (at 300/1200/2400 baud FSK) - Digital Radio, Microwave channel, Fibre optic and others (at up to 19200 baud). Radio System The telemetry system shall be suitable for use with digital radios, MDS 4710E/OEM or similar, single, or dual frequency simplex UHF radios. The UHF radios shall be able to operate in the 420 to 470 MHz range. Synthesized frequency radios will be preferred for this application. The digital radio shall have a RS232 port available for interface to the telemetry equipment. The radio shall be able to transmit at least 4800 bits per second over the air. The radio Output RF power shall be adjustable from 100 mW to 5 Watts. No custom-made radio or parts of radios shall be adapted for use on this project. Radios offered shall be approved by the relevant Local Authority for this application. Mast for Antenna A 6 m tubular mast shall be fixed to the wall with a heavy gauge galvanized offset bracket for 500 mm roof overhang. The mast shall be 50 mm diameter, minimum 2 mm thick aluminum, for coastal applications, or galvanized mild steel for inland areas. Antenna The antenna selections shall be chosen to suit the project. No antennas are to be ordered prior to approval by the Employer or the Engineer. Surge Protection Earthing Basic earthing of mast, antenna and equipment is to be provided by the Contractor, and should be included in the Tender as follows: - A 35 mm' bare copper conductor from the junction of the antenna and mast to a 1,2 m earth pin buried vertically into the ground at the closest point below the mast. - A 10 mm' bare copper conductor from the junction of the antenna and mast, to follow the co-ax cable, to the equipment enclosure. - A 35 mm' bare copper conductor from the equipment enclosure(s) and surge protection modules to the earth pin. All earth cables to be as short as possible. Overvoltage Protection The radio antenna input shall be protected using a Y wave shorted coax "stub" bonded to the earth point. Mains power input shall be protected by a surge protection device rated at 5 kA and shall be properly bonded to earth point. Analog and Digital input signals and communications lines coming into the telemetry enclosure from the field (e.g., reservoir level transducers, float switches, flow meters pilot cable, GPO lines etc.) shall be protected by a suitable surge protection device rated at 5 kA and shall be properly bonded to earth point. Maintenance facilities The telemetry system shall provide facilities to enable non-qualified personnel to be able to assess the proper operation of a station. Indications Display facilities should include the following: - Indicating LEDs on each digital input and output line, control relay, etc. - A display on the CPU module to view the system activity i.e., from whom it is receiving, to whom it is transmitting, what data has been decoded, error conditions and modes of operation. - A method shall be provided to view the current analog input and output values. - A pushbutton on the analog module, and the display on the CPU module may be used for this purpose. Test Transmissions A selector switch shall be provided to enable a Test Transmission to be sent and received from a selected outstation to assess the quality of communications. A handheld programmer should not be required for this facility. Serial Port A serial port (or RS232 module) shall allow a maintenance PC (e.g., lap-top) to be connected to monitor the entire communications system from any outstation. Suitable engineering level analysis software for this lap-top shall be included in this option to be offered. Spares The Tenderer shall allow for one complete spare module for each type used in this project (central and outstation) and the cost thereof shall be entered in the Bill of Quantities. Transmission Scheme Communications Algorithm The telemetry CPU shall monitor the radio's RF carrier detect line as a channel busy indication. Should the channel be continuously busy (with no valid data detected, ego radio squelch opened) then the CPU will switch automatically to the audio detect output of the modem and continue normal operation of data transfer. An anti-collision algorithm based on the RF/Audio detect lines shall be implemented to avoid 2 outstations transmitting simultaneously. The algorithm can be based on the (unique) Station Address for each outstation. Suitable lead-in time (pre-data PTI and audio tone) shall be allowed, to allow multiple repeater links to be keyed up, and the receiving modem can detect. Once keyed up (PTI) the outstation shall optimize radio time by concatenating commands into one transmission. Error Detection The telemetry system shall provide reliable and efficient information transfer. Error detection techniques and message protection shall be used to ensure maximum data integrity within the radio telemetry system, Error detection shall be per command using 16-bit Cyclic Redundancy Code (CRG) as checksum, as well as context (structure), The receiving station shall recalculate and verify the CRC, the received command shall be further checked for context, identification, and destination, and shall be rejected if any of this information is not consistent. No error correction system shall be incorporated for received data, Acknowledge Procedure The Telemetry System shall be able to acknowledge messages received on the radio link and be capable of re-transmitting a message if it is not acknowledged after a predetermined time-out period It shall be possible to select or de-select the acknowledge mode of operation. A station shall attempt 3 re-tries at transmitting a message, if it is not acknowledged, Addressing Every Telemetry System shall be allocated a System Number. This number shall be included in the data transmission for system identification purposes. The System Number shall be used to allow two or more telemetry systems to operate in the same vicinity on the same radio frequency channel, or to implement Digipeating. Each Telemetry Station shall be allocated a unique Station Address. This shall be setup by means of thumbwheel switches on the CPU Module. Station addresses from 00 to 99 shall be available. Each set of Inputs on an I/O Module shall be allocated a Data Encode Channel. Each set of outputs on an I/O module shall be given a Decode Channel. The Encode and Decode Channel numbers shall be included with the module's data in a command. Upon receipt of a data transmission, each station shall search for a match of the received Encode Channel to local I/O Module Decode Channel numbers, if a match is found, the data shall be transferred onto the corresponding set of outputs. Digital and Analog Control outputs shall thus be able to be sent between outstations. or from Central to Outstation Modes of Operation A telemetry station shall have three selectable modes of operation, namely INTERROGATION, CHANGE-OF-STATE, and TIMER, these modes of operation shall be selectable by Mode Select Switches on the CPU Module, Interrogation Mode A Master Station or SCADA Central shall interrogate all outstations. The station that is interrogated shall respond by transmitting all its I/O Module input data. to update central and all stations correspondingly. The SCADA softwara shall be able to interrogate stations under program control, based on user configuration (e.g., time or event based). Change-of-State Mode The Change-of-State Mode shall enable the station to transmit input information when any input data changes. e.g., a digital input changes state or an analog input change by more than a determined amount. The Change-of-State Modes selectable shall include the following options: Digital CAS enabled/disabled, digital inputs only, Analog COS enabled/disabled (analog cas is 10 % variance) Digital inputs shall be 'de-bounced' in software, requiring that a state exists for longer than 300 ms before it is regarded as a change-of-state. The actual values of digital debounce, variance (10 %). for analogue inputs are default values. Commands should exist in the protocol to adjust these for each input module when using a SCADA Central Station. Timer Mode A station shall be able to be set to transmit its input information at regular time-intervals. At least four selectable periods shall be provided (3, 10, 30, 90 minutes). Combinations A Station shall be able to have any combination of the above modes selected as a combined operating mode. Any specific mode selected shall not be mutually exclusive of other modes, thus allowing a level of redundancy to be programmed into the system to improve system reliability in adverse communications conditions. Time-Tagging The telemetry system shall have the facility to time-tag all events at the outstation and transmit this time-tag to the Central together with the event (e.g., Digital Change-of State or Analog Change-of-Value). The clock at the outstation shall be hardware based (with crystal), not software derived. Events shall be time tagged to 1 ms resolution. Accuracy of time-tagged events should be 20 ms between events at an outstation, and 100ms between events at different outstations. The Central Station shall pass this time-tagged event to the computer SCADA software. The SCADA must display these times (as opposed to the time of arrival of the event), The operator must be able to see which time-tags displayed are of remote origin, so that proper analysis of sequence of events between outstations can be evaluated. DIGIPEATING The telemetry system shall have the facility to repeat commands destined from or to a remote station, via another station (Digipeating, or Store-and-forward). The digipeat "map" shall be stored in EPROM (non-volatile memory) at relevant stations, and be able to be programmed with local programmer (e.g. lap-top) or remotely via the communications medium. The digipeat map shall allow for input / output data to be transferred from any remote site to any other remote site and / or Central Station, Commissioning and Training Factory Acceptance A Factory Acceptance Test shall be conducted at the successful tenderer's premises prior to dispatch of the equipment to site The Employer and his Engineer shall be invited to attend. Commissioning After installation and run-up, a commissioning and handover procedure shall be followed for the Contractor to demonstrate proper operation of the system, in accordance with the Factory Acceptance. Training The Contractor shall be required to train technical personnel of the Employer in the proper operation and maintenance of the system. A total of 2 people will be nominated by the Employer for this purpose. Training shall be done on the premises of the Employer. It is the Employees intention to obtain a very thorough understanding of the system. To this end, training shall be done in three ways: Formal hands-on training sessions of the operating personnel in system operation, covering all software and hardware operational aspects. Tenderers shall Indicate the time allowed for this purpose, but the minimum period acceptable will be 2-day session. During the installation phase, a person will be designated by the Employer to be closely involved with the Installation and commissioning process. The Intention is not to interfere with the Contractors' installation team, but to do observation to obtain the maximum possible information regarding the installation, to enable efficient maintenance to be undertaken by the Employer after final handover and expiry of the guarantee period. Software instruction for computerized SCADA Central Stations shall be of 2 days instruction. During these sessions operators will be familiarize regarding generation of reports by the system, setup of analogue limits, modification of displays, configuration of trend graphs as well as other operational requirements of the software. Documentation The Contractor shall provide 2 complete sets of manuals for all the systems and subsystems to be provided in terms of the contract. Hardware manuals shall be sufficiently detailed to enable the Employer's maintenance personnel to attend to maintenance functions. Drawings shall cover at least all aspects of physical subsystem assemblies, wiring diagrams and terminal connections. Software and operational manuals shall cover aspects of system start-up, setup, and operation. Instructions shall be clearly understandable by a reasonably skilled operator. Custom software is not favored and shall be avoided where possible. |

C3.1.3	Construction Programme

## C3.1.3.1	Commencement Date

The commencement date for the Contract programming purpose is July 2024.

#### C3.1.3.2	Format and Detail

The construction programme shall be in the format of a bar chart (Gannt Chart) and shall in addition to normal activities and items include the following detail;

- cash flow on a monthly basis,

- production rates for all activities,

- dependencies between various activities or items, and

- critical path for the execution of the works.

The format and detail of the programme shall be to the Engineer’s approval.

##### C3.1.3.3	Quality Control Plan

In addition to the normal construction programme the Contractor shall submit a quality control plan in accordance with SABS 0157 prior to commencement of any permanent work for approval by the Engineer. The Quality Control Plan shall make provision for regular reporting and reports shall be submitted to the Engineer on a monthly basis or more frequently if required.

#### C3.1.3.4	Provisional Programme

A provisional programme which complies with the above-mentioned requirements shall be submitted at tender stage. The provisional programme shall be based on an anticipated commencement date for the Contract programming purpose is July 2024.

C3.1.4	Features Requiring Special Attention

Limited suitable material is available for the selected layer works. Suitable material should be imported from commercial sources or from borrow pits; approved by the engineer.

The rate for importing from the approved commercial source and/or borrow pits (as proposed by the contractor) shall cover the cost of royalties if applicable and acquiring the suitable material including the applicable of forming access, removal of overburden, loading, transportation, offloading at point of placing, removal of access and replacing of overburden.

C3.1.4.1	Conformity with Expanded Public Works Programme (EPWP) Requirements

The project is funded by a government agency and is subsequently destined to conform with EPWP requirements of employment, training and capacity building in as great an extent as can efficiently be achieved.

Tenderers are required to submit details of their proposed conformance with EPWP requirements of employment, training and capacity building with their tenders. This should include details of;

- the extent to which labour intensive construction methods are applicable and will be employed and the number of employment opportunities which will subsequently be created for local labourers,

- the extent to which local sub-contractors will be employed with specific reference to conventional sub-contractors, sub-contractors employed on a management contractor basis and sub-contractors employed on a labour only basis where the main contractor will be responsible for logistics (eg materials and transport) and quality control and the sub-contractor will be responsible for the manpower component.

- the extent to which support staff (clerks, messengers, typists, security personnel, drivers and labourers for general maintenance) will be employed from the local community, and

- details of proposed education, training and capacity building programmes including the number of candidates to participate in the various programmes and the various institutions which will be contracted to present the training programmes.

The conformity with EPWP requirements will together with Contract Price be an important criterion for the evaluation and adjudication of the tender. In evaluating the tenders, any additional offer in regard to capacity building will be to the advantage of the tenderer.

The proposed conformance with EPWP requirements of employment, training and capacity building as submitted with the tender will become binding on the Contractor in terms of the Contract if his tender is accepted.

Guidelines for conformity with the EPWP requirements are contained in Annexure D and form part of this tender documentation.

### 3.1.7	APPLICABLE STANDARDIZED AND PARTICULAR SPECIFICATIONS

#### C3.1.7.1	Standardised specifications

SABS 1200 A	:	General

SABS 1200 AB	:	Engineer’s Office

SABS 1200 C	:	Site Clearance

SABS 1200 D	:	Earthworks

SABS 1200 DA	:	Earthworks (Small Works)

SABS 1200 DB	:	Earthworks (Pipe Trenches)

SABS 1200 G	:	Concrete (Structural)

SABS 1200 GA	:	Concrete (Small works)

SABS 1200 H	:	Structural Steelwork

SABS 1200 HA	:	Structural Steelwork (Sundry Items)

SABS 1200 HC	:	Corrosion Protection of Structural Steelwork

SABS 1200 L	:	Medium Pressure Pipelines

SABS 1200 LB	:	Bedding (Pipes)

SABS 1200 LC	:	Cable Ducts

C3.1.7.2	Particular Specification

In addition, the following particular specifications that are formed in the document shall apply:

SPECIFICATION PSAB	:	Engineers Office

SPECIFICATION PSC	:	Site Clearance

SPECIFICATION PSDA	:	Earthworks

SPECIFICATION PSDB	:	Earthworks (Pipe Trenches)

SPECIFICATION PSDM	:	Earthworks (Roads, Subgrade)

SPECIFICATION PSL	:	Medium Pressure Pipelines

SPECIFICATION PSLB	:	Bedding Pipes

SPECIFICATION PSLC	:	Cable Ducts

SPECIFICATION PSLE	:	Materials

SPECIFICATION PSG	:	Concrete (Structual)

SPECIFICATION PSGA	:	Concrete (Small Works)

SPECIFICATION PSHA	:	Structural Steelwork

SPECIFICATION PSHC	:	Corrosion Protection of Structural Steelwork

SPECIFICATION PSB	 :	 Building Works

C3.2  	STANDARDISED / PARTICULAR SPECIFICATIONS

VARIATIONS ON STANDARISED SPECIFICATIONS

Should any requirement of the Project Specification conflict with any requirement of the Standardized or Particular Specification, the requirement of the Project Specification shall prevail.

The standardised / particular specifications are included as an Annexure B for completeness and convenience.

PART C4:	SITE INFORMATION

C4.1  	SITE INFORMATION

C4.1.1	Site of Works and Access

The general layout of the project site and the extent of the works is shown on the tender drawings. Access to the site will be obtained through the access roads and internal streets of Cornelia.

Any additional temporary access routes, which the Contractor might require will be his responsibility and no separate payment other than that provided for in the Schedule of Quantities will be made for the construction, maintenance or removal of temporary access routes. The Contractor will remove all temporary access routes prior to completion of the Contract and rehabilitate the areas to their original state.

C4.1.2	Soil Conditions

The area have unsuitable material clay and rock. The perspective contractors may make arrangements to have trial holes dug in the area on their own accord.

C4.1.3	Existing Services

All existing services shall be indicated to the contractor where after he will assume full responsibility for maintaining these in good running order. It shall be understood that the production of the existing services shall in no way be impaired during the contract.

C4.1.4	Surveying and Cadastral Beacons

The Contractor shall be held responsible for the cost incurred in replacing or repositioning of any cadastral beacons, which may have been disturbed by his actions.

Under no circumstances shall unauthorized persons replace cadastral beacons and the Engineer shall be informed immediately of any disturbed beacons. The Engineer shall arrange for the replacement of any beacons by a competent Land Surveyor.

C4.1.5	Facilities available on site

C4.1.5.1	Electricity

The Contractor shall make his own arrangements with the Mafube Local Municipality for electricity supply.

C4.1.5.2	Water

The Contractor shall make his own arrangements with the Mafube Local Municipality for water supply.

C4.1.6	Site Facilities Required

C4.1.6.1	Temporary Offices, Furniture and Equipment for the Resident Engineers

The facilities that have to be provided for the Resident Engineer consist of the following:

    - one office, fully equipped, that may be shared with the contractor’s site agent,

    - two carports,

    - survey assistants, materials and instruments,

for his use whenever required.

C4.1.6.2	Temporary Housing, Sheds, Etc. for the Contractor

The Contractor shall provide at his own cost all housing and sheds of a temporary nature necessary for the convenience of his workmen and for storage of tools, plant and materials in positions to be approved by the Engineer. As soon as they are no longer required, the housing and sheds shall be removed and the site shall be restored to a clean and tidy condition. The Contractor shall also limit the movement of his equipment and personnel to the areas on site which have been pointed out by the Engineer.

C4.1.6.3	Sanitary Facilities

The Contractor must provide adequate sanitary facilities and sewerage disposal in accordance with the Mafube health regulations.

### ANNEXURE A

PRO FORMA DOCUMENTS

## FORM OF GUARANTEE

BID NO: FDDM/BID NO: 012/2023-24

WHEREAS The FEZILE DABI DISTRICT MUNICIPALITY. (hereinafter referred to as "the Employer")

entered into, a Contract with …………………………………………………………………………………………….

(hereinafter called "the Contactor") on the ………… day of …………………… 20………regarding the project Drilling And Equipping of Six New Boreholes And Refurbishment of Two Existing Boreholes in Mafahlaneng /Tweeling and WHEREAS it is provided by such Contract that the Contractor shall provide the Employer with security by way of a guarantee for the due and faithful fulfilment of such Contract by the Contractor; AND WHEREAS ……………………………………………

has/have at the request of the Contractor, agreed to give such guarantee; NOW THEREFORE WE, ………………………………………………………………………… do hereby guarantee and bind ourselves jointly and severally as Guarantor and Co-principal Debtors to the Employer under renunciation of the benefits of division and excussion for the due and faithful performance by the Contractor of all the terms and conditions of the said Contract, subject to the following conditions:

1.	The Employer shall, without reference and/or notice to us, have complete liberty of action to act in any manner authorized and/or contemplated by the terms of the said Contract, and/or to agree to any modifications, variations, alterations, directions or extensions of the Completion Date of the Works under the said Contract, and that its rights under this guarantee shall in no way be prejudiced nor our liability hereunder be affected by reason of any steps which the Employer may take under such Contract, or of any modification, variation, alterations of the Completion Date which the Employer may make, give, concede or agree to under the said Contract.

2.	This guarantee shall be limited to the payment of a sum of money.

3.	The Employer shall be entitled, without reference to us, to release any guarantee held by it, and to give time to or compound or make any other arrangement with the Contractor.

4.	This guarantee shall remain in full force and effect until the issue of the Certificate of Completion in terms of the Contract, unless we are advised in writing by the Employer before the issue of the said Certificate of his intention to institute claims, and the particulars thereof, in which event this guarantee shall remain in full force and effect until all such claims have been paid or liquidated.

5.	Our total liability hereunder shall not exceed the sum of …………………………………………………
	………………………………………… (R …………………………).

6.	The Guarantor reserves the right to withdraw from this guarantee by depositing the Guaranteed Sum with the beneficiary, whereupon the Guarantor's liability hereunder shall cease.

7.	We hereby choose our address for the serving of all notices for all purposes arising here from as

……………………………………………………………………………………………………………………

IN WITNESS WHEREOF this guarantee has been executed by us at ………………………………………on this ………day of …………………………………… 20………

As witnesses:						Signature

1.	………………………………………………	…………………………………………

2.	………………………………………………	………………………………………………………
Duly authorized to sign on behalf of ……………………………………………………………………………………

Address : ………………………………………………………………..…………………………………………………

### RETENTION MONEY GUARANTEE

ISSUED TO: FEZILE DADI DISTRICT MUNICIPALITY (hereinafter referred to as “the Employer”)

ON BEHALF OF: …………………………………………………………(hereinafter referred to as “the Contractor”)

In connection with BID NO: FDDM/BID NO: 012/2023-24

WHEREAS the Employer and the Contractor have agreed that the Contractor may provide a guarantee in lieu of the whole or portion of the retention monies provided for under the Contract; …………………………………..

NOW THEREFORE we, the undersigned, undertake, in accordance with the following provisions, to pay to the Employer such amounts as the Employer may, from time to time, demand from us.

- Each demand by the Employer shall be in writing signed by the Employer and delivered to us at ………

…………………………………………………… or such other address be in 	…………….. as we shall in writing notify to the Employer and shall be accompanied 	by a certificate complying with Clause 2, signed by the Engineer in office as such in terms of the Contract.

2.	The Engineer's certificate referred to in Clause 1 shall certify

a)	that he is the Engineer in office as such in terms of the Contract,
b)	that the Contractor is in breach of his obligations under the Contract, and
c)	that the amount demanded, which amount the certificate shall specify,

i)	does not exceed the amount of retention monies which, but for this guarantee, would have been retained by the Employer in terms of the Contract at the date of the certificate, less the aggregate of the amounts of retention money actually retained by the Employer and the amounts previously paid by us to the Employer in terms hereof, and

ii)		does not exceed a genuine estimate of the cost to the Employer of having the breach referred to in paragraph (b) remedied less the aggregate of any amounts withheld by the Employer from payments due to the Contractor in terms of the Contract by reason of the breach referred to, and any amount of retention money actually held by the Employer save to the extent that the same had been deducted from any previous demand in terms hereof.

3.	We shall within …… days after our receipt of a demand complying with the provisions of Clauses 1 and 2 	make

payment to the Employer of the amount demanded at 	 or at such other

address in 	 as the Employer shall in writing notify to us.

4.	Subject to compliance with the provisions hereof, our liability to make the payments herein referred to shall be unconditional and shall not be affected or diminished by any disputes, claims or counterclaims between the Employer and the Contractor.

5.	Our aggregate liability under this guarantee is limited to R

6.	This guarantee shall expire on the date on which the last of the retention monies, which but for this guarantee would have been retained by the Employer, becomes payable to the Contractor.

7.	This guarantee is not transferable and must be produced for endorsement if any part payment is made and must be returned to us against final payment of our aggregate liability or on the date of the expiry of the guarantee in terms of Clause 6, whichever is the earlier.

Signed in the presence of the subscribing witnesses:

At 		for and on behalf of

on this ………… day of ………………………. 20 ……….

Signature :

Capacity :

Address :

As witnesses:

1.

2.

BID NO: FDDM/BID NO: 012/2023-24

# FORM OF BOND FOR UNUSED MATERIALS ON SITE

EMPLOYER: THE MAFUBE LOCAL MUNICIPALITY

CONTRACTOR

DESCRIPTION OF CONTRACT

……………………………………………………………………………………………………………………………….

We the 	 (Bank or Company) do hereby
bind ourselves as surety in solidum and co-principal debtors to recompense the Employer in the event of his not acquiring ownership of materials for whatever reason, or in the event of his lawfully being required to make payment of any sum of money to any third party in order to obtain or retain ownership or full and free possession of the said materials, in circumstances where the Employer has paid the Contractor for the said materials on Site in terms of Clause 62(1)(b) of the General conditions of Contract, and for all losses, damages and expenses that may be suffered or incurred by the Employer as a result of such payment for the said materials on Site, renouncing all benefits from the legal exceptions ordinisseu excussionis et division is "No value received" and all other exceptions which might or could be pleaded against the validity of this guarantee, with the meaning effect of which exceptions we declare ourselves to be fully acquainted;  provided that the liability of the undersigned under this guarantee is limited to and shall not exceed

(R 	)
will lapse after issue of the Completion Certificate in terms of the Contract, unless the surety is advised in writing by the Employer before issue of the said Certificate of his intention to institute claims and the particulars thereof, in which event this guarantee shall remain in force until all such claims are paid or settled.

FOR AND ON BEHALF OF THE SURETY:…………………………………………………………………………….

SIGNATURE: ……………………………….

AT

1.

2.

NAME OF SURETY:

ADDRESS:

APPOINTMENT – GSR 11(1)

# BUILDING WORK SUPERVISOR

The Occupational Health and Safety Act 85/1993.

GENERAL SAFETY REGULATION 11(1)
Every employer who performs building work shall charge a full-time employee, designated in writing by the employer, with the duty of supervising the performance of such building work.  Provided that if such employer himself has the experience contemplated in sub regulation (2) and supervises the work himself, such charging and designation need not be done.

GENERAL SAFETY REGULATION 11(2)
An employee contemplated in sub regulation (1) shall be a person who has had at least 2 years’ experience in the type of building work for which he is to be designated.

GENERAL ADMINISTRATION REGULATION 1
“Building work” means any work in connection with:
(a)	the erection, maintenance, alteration, renovation, repair, demolition or dismantling or addition to a building;
(b)	the installation, erection or dismantling of machinery;
(c)	the construction, maintenance, demolition or dismantling of any bridge, dam, canal, road, railway, street, 
	runway, sewer or water reticulation system or work on any similar project; or
(d)	the moving of earth, clearing of land or making of an excavation or work on any similar project.

## DESIGNATION

Therefore in accordance with General Safety Regulation 11(1) and (2) and General Administrative Regulation (1) referred to above:

I, ………………………………. DESIGNATED OFFICIAL FOR ……………………………………………………. do hereby designate ……………………………………… as a Building Work Supervisor over his demarcated areas of responsibility ……………………………………………………………………………………………………
…………………………………… (state demarcation e.g. structure, finishes, etc)

for the SITE / WORKPLACE:	CONTRACT.………………………………………………………………...……...

SITUATED AT :				.………………………………………………………………...……...

DATE : …………………………………	SIGNATURE :	.……………………………………………………………

### ACCEPTANCE OF DESIGNATION

I, …………………………………… hereby accept this appointment as a BUILDING WORK SUPERVISOR and confirm that I am conversant with the relevant statutory provisions and regulations of the relevant Act in regard to the carrying out of building work.

SIGNATURE :	.…………………………………………………………………..….……………………………..

DESIGNATION:	.………………………………………………………………….………..………………………..

DATE :		.………………………………………………………………….…………..……………………..

### DISTRIBUTION

1.	Original displayed at plant division / on site.
2.	Copy to central files.

# OCCUPATIONAL HEALTH AND SAFETY ACT 9/96/1993

# MANAGEMENT

## DESIGNATION

Chief Executive Officer with certain duties,

16(1)	Every chief executive officer as far as is reasonably practicable ensure that the duties of his employer as contemplated in this Act, are properly discharged.

- With derogating from his responsibility or liability in terms of subsection (1), a chief executive officer may assign any duty contemplated in the said subsection, to any person under his control, which person shall act subject to the control and directions of the chief executive officer.

- The provisions of subsection (1) shall not, subject to the provisions of section 37, relieve an employer of any responsibility or liability under this Act.

I, ………………………………. CIVIL ENGINEER for …………………………….. do hereby assign my duties to ……………………………………. to ensure that the duties of the employer are carried out.

DATE :	………………………………………………………………….……………………………..…..

SIGNATURE :	………………………………………	DESIGNATION : ………………………….……..

### ACCEPTANCE OF DESIGNATION

I, …………………………………… hereby accept this and confirm that I am conversant with the requirements of the OH&S Act and agree to carry out the duties as set out for the employer.

DATE :			.………………………………………………………………….…………………….…………...

SIGNATURE :	………………………………………	DESIGNATION : …………………….…………..

### DISTRIBUTION

1.	Original displayed on site.
2.	Copy to central files.

### ANNEXURE B

### STANDARDISED / PARTICULAR SPECIFICATIONS

### STANDARDISED / PARTICULAR SPECIFICATIONS

SABS 1200 A : GENERAL

PSA 1	MATERIAL (Subclause 3.1)

All material required for this contract shall bear the official standardization mark.

PSA 2.1.2	Restrictions on Employee Accommodation

No housing is available for the Contractor's employees, and the Contractor shall make his own arrangements to house his employees and transport them to site.

The Employer will place at the disposal of the Contractor an area to enable him to erect his site offices, workshops, stores, and any temporary housing the Contractor may wish to erect for his personnel. The temporary housing and ablution facilities shall comply with the requirements of the local Authority.

PSA 2.2	CAPACITY OF PLANT AND EQUIPMENT (Clause 4)

Add as Clause 4.3:

The Contractor shall supply plant and equipment in sound working condition and of adequate capacity to complete the Works well within the period or periods specified or stated in the appendix to the tender.

In addition, he shall have available on the Site adequate standby plant to ensure that operations designed to be executed continuously are not disrupted because of breakdown of any plant provided for such operations.

PSA 3	CONSTRUCTION

PSA 3.1	DETAILED SETTING OUT (Subclause 5.1.1)

The Contractor shall be solely responsible for the execution of the works to the correct line and level.

The Contractor shall carefully set out the works, employing a capable surveyor to the lines and levels gleaned from information provided.

The tolerance allowed in setting out shall be 10mm either way.

Work set out by the Contractor shall be checked by the Engineer where after any errors be rectified by the Contractor.

The Contractor shall provide at least three days' notice of such a check to the Engineer. The Contractor shall supply any material and labour required for the control survey work by the Engineer including the supply of and placing the necessary pegs, sight rails, etc.

Any assistance, including checking, rendered to the Contractor by the Engineer shall not be held as relieving the Contractor of his responsibility in this respect. Should any portion of these works be constructed incorrectly, the Contractor shall at his own expense rectify the work to the satisfaction of the Engineer.

The Contractor shall be held solely responsible for the protection of all benchmarks, reference pegs and level pegs.

The Contractor shall establish at least three benchmarks at selected points.

PSA 3.2	WATCHING, BARRICADING, LIGHTING AND TRAFFIC CROSSINGS

(Subclause 5.2)

Add the following to this subclause:

The Contractor shall ensure that he complies with all the requirements of the authorities concerned with respect to the safety of the works and labourers, including the provision and wearing of protective clothing. Any negligence or non-compliance of any of these requirements shall be viewed in a serious light and shall be sufficient reason for the Engineer to order the immediate suspension of the total extent of the Works.

The Contractor shall provide for artificial lighting for any part of the Works that may be required for the proper execution of the work.

PSA 3.3	PROTECTION OF OVERHEAD AND UNDERGROUND SERVICES (Subclause 5.4)

Add the following to the subclause:

Before commencing any excavation, the Contractor shall verify the position of all known or suspected obstacles by inspection of the site, examination of drawings or, where necessary by the excavation of trial holes. Any damage caused to existing services and works shall be repaired as expeditiously as possible by the Contractor at his own expense, and shall be reported immediately to the Engineer.

Where permanent protective works are ordered by the Engineer, such works shall be valued as a variation. The Engineer will supply the Contractor with such information as may be available concerning obstructions and services, but whilst such information is given in good faith, it shall not relieve the Contractor of any of his liabilities, obligations and risks under the Contract.

The Contractor shall be responsible for any damage to such public services and existing works in the execution of this Contract and shall reimburse the Public Authority or the Owner concerned for any repairs required or compensation for damage awarded.

Any alteration to public services shall be carried out by the Authority concerned.

The Contractor shall provide the necessary assistance during any operations necessary in connection with the removal, alteration or safeguarding of any public service.

The relevant authority and Engineer shall be informed of any damages without delay.

PSA 3.4	DEALING WITH WATER ON WORKS (Subclause 5.5)

Add the following to the subclause:

The Contractor shall be responsible for the dewatering of excavations and the full and adequate protection of the works against damage by storm or water from any source whatever. He shall construct all necessary diversion works and drains to deal adequately with and bypass all water and carry out any necessary pumping of water and supply all tarpaulins or other covers which may be required to protect any section of the work during heavy rain or storm together with any other labour work and material which, in the opinion of the Engineer is necessary to keep the work dry and safe at all times.

Full risk and cost of dealing with water shall be borne by the Contractor.

PSA 3.5	POLLUTION (Subclause 5.6)

Add the following to the subclause:

The Contractor shall maintain all access roads and the area where the offices, stores and workshops are situated to the satisfaction of the Engineer. It shall be kept damp to limit dust and inconvenience or disturbance to the residents in the neighbourhood of the Works to a minimum.

PSA 3.6	DEGREE OF ACCURACY (Subclause 6.2)

Delete this subclause and replace with the following:

The Contractor shall construct each of the various parts of the Works to the degree of accuracy specified in the relevant standardized specification.

PSA 4	TESTING

The cost of all testing to be carried out by the Contractor in terms of the requirement of the relevant SABS 1200 standards shall be included in the rates for the various work items listed in the Schedule of Quantities. No separate payments shall be made in this regard.

PSA 5	MEASUREMENT AND PAYMENT

PSA 5.1	MEASUREMENT (Subclause 8.1.1)

Add the following to this subclause:

In no case will any dimensions be allowed or any quantities be included in the measurement for payment which shall exceed the dimensions required by the contract, or as ordered in writing by the Engineer in the case of extra work.

PSA 5.2	PAYMENT (Subclause 8.2)

Add the following to this subclause:

The quantities as shown in the Bill of Quantities, are estimated quantities and are used for comparing tenders and awarding of the contract. It shall be noted that only the actual work executed or materials supplied will be measured and paid for, therefore billed quantities may be increased or decreased as allowed for in the General Conditions of Contract.

The entire works shall be measured on completion by the Engineer and paid for at the relevant rates, according to the actual quantity of each item of work executed.

The Contractor shall have no claim for loss of profit on unexecuted works.

PSA 5.3	MEASUREMENT AND PAYMENT FOR SCHEDULED FIXED-CHARGE AND VALUE RELATED ITEMS (Subclause 8.3.1)

Add the following to this subclause:

The tendered amount shall include the costs for the premiums of the surety for unused materials on site.

SABS 1200 AB : ENGINEER’S OFFICE

## PSAB :	ENGINEER'S OFFICE

PSAB 1	MATERIALS

PSAB 1.1	NAMEBOARDS (Subclause 3.1)

Add the following to the subclause:

Notwithstanding the provisions of Subclause 3.1 of SABS 1200 AB, the standard nameboards complying with the recommendations of the South African Association of Consulting Engineers shall be provided. Details of the nameboard will be available from the Engineers.

PSAB 1.2	OFFICE BUILDINGS (Subclause 3.2)

Delete this subclause and replace with the following:

The Contractor shall provide the following furnished offices for the use of the Engineer and the Client. The office shall consist of one room with the following floor area:

Engineers office	 - 16m2

The clear height of the office between floor and ceiling shall be 2,5m minimum. All windows shall be of the type than can be open over the full window area.

The office shall be weatherproof, shall have a concrete floor and shall be provided with a ceiling and a lining to the walls, or equivalent insulation, with an acceptable type of door with a secure lock, and two opening windows of glazed area at least 3m2. The office shall be well ventilated and shall be so insulated as to provide comfortable working conditions. The internal furnishings shall include:

a)	one trestle table, 2m long x 1m wide x 0,9m high, with a smooth top;

b)	one table or desk having a top of size at least 1,5m x 0,9m and at least one lockable drawer;

c)	one high stool;

d)	two chairs;

e)	a lockable upright steel cabinet with three shelves or a steel filing cabinet with four drawers;

f)	shelving of total length 3m and of nominal width 300mm;

g)	an acceptable blind on each window,

h)	a wash-hand basin;

i)	acceptable lighting;

j)	provision for heating in winter and cooling in summer;

k)	one conference type steel table with folding legs of size at least 4,0m x 0,9m.

l)	The Contractor shall also supply a toilet for the exclusive use of the Engineer.

PSAB 1.3	CAR PORTS (New Subclause 3.2 (k))

The Contractor shall provide two permanent car ports for the use of the Engineer. The car ports shall be so constructed that the vehicles parked under them will at all times be shaded from direct sunlight. The car ports shall be at least 20m2 in area and shall have a hard stand of crushed stone.

PSAB 2	SURVEY EQUIPMENT (Subclause 5.5)

The Contractor shall provide the following survey equipment on the site from the commencement to the completion of the Works:

1.	1 Tachometer capable of reading 20 seconds of arc;

2.	1 Engineer's level and level staff;

3.	2 Tachometer staffs graduated metrically;

4.	1 Steel tape of length 30m.

The tachometer may be shared by arrangement between the Contractor and the Engineer's Representative, but the remaining instruments shall be provided for the exclusive use of the Engineer's Representative. The Contractor shall keep the equipment continuously insured against any loss, damage, or breakage and he shall indemnify the Engineer and the Employer against any claims in this regard. Upon completion of the whole of the Works, the ownership of the equipment shall revert to the Contractor.

The Contractor shall maintain the equipment in good working order and keep it clean throughout the contract period.

PSAB 3	SURVEY ASSISTANTS (Subclause 5.5)

The Contractor shall make available to the Engineer two suitably trained survey assistants for use on and about the SITE at all reasonable times for the duration of the Contract.

SABS 1200 C: SITE CLEARANCE

PSC 1	MATERIALS (Clause 3)

PSC 1.1	DISPOSAL OF MATERIAL (Subclause 3.1)

Add to this subclause :

Material obtained from clearing and grubbing and from the demolition of structures shall be disposed of in a borrow pit indicated by the Engineer and shall be finished to the satisfaction of the Engineer.

PSC 2	CONSTRUCTION (Clause 5)

PSC 2.1	INDIVIDUAL TREES (Subclause 5.2.3.2)

Add to this subclause :

Should the Contractor remove or damage any tree marked to be preserved, a penalty of R10 000.00 per tree shall be payable.

SABS 1200 DA: EARTHWORKS (SMALL WORKS)

PSDA 1	CLASSIFICATION OF EXCAVATED MATERIAL (Subclause 3.1.2)

Delete this sub clause and replace with the following:

Distinction shall be drawn, for payment purposes, between excavation in hard and soft material. All excavation for the foundations of structures shall be classified in accordance with the following classification.

Hard Material

Boulders of 0,5 cubic meter or more in volume;

or

Material which cannot be excavated except by drilling and blasting or the use of pneumatic tools or mechanical breakers.

Soft Material

All material not classified as hard material shall be classified as soft material.

The Engineer shall rule under which one of the above categories any excavation shall be classified and paid for.

PSDA 2	FREEHAUL (Subclause 5.2.6.1)

The freehaul distance within which the Contractor will be required to move material without separate compensation shall be 12 km. Overhaul will be paid for the moving of material beyond that distance.

PSDA 3	MEASUREMENT AND PAYMENT (Subclause 8)

PSDA 3.1	BASIC PRINCIPLES (Subclause 8.1.1)

Change the following in this subclause :

The freehaul distance will be 12 km and not 2.0 km.

SABS 1200 DB : EARTHWORKS (PIPE TRENCHES)

PSDB 1	CLASSIFICATION OF EXCAVATED MATERIAL (Subclause 3.1)

Distinction shall be drawn, for payment purposes, between excavation in hard and soft material. All excavation for pipe trenches shall be classified in accordance with the following classification.

PSDB 1.1	Soft excavation

Soft excavation shall be excavation in all existing fill material as well as excavation in material which can be efficiently removed by any of the following plant.

A bulldozer having a mass, including the mass of the ripper if fitted of 35 ton and having a flywheel power of approximately 220 kW.

PSDB 1.2	Hard excavation

Hard excavation shall be excavation in material, which cannot be efficiently ripped by plant as described in PSDB 1.1.1. This excavation generally includes material such as formation of unweathered rock which can only be removed after blasting or boulders of 0,5 m3 or larger in volume.

The Contractor shall be at liberty to use any method he wishes to excavate any class of material, but the method of excavation shall, however, not dictate the classification of the excavation.

The Engineer shall decide under which one of the above classes any excavation shall be classified and paid for. In the first instance the classification shall be based on inspection of the material to be excavated and the method of excavation proposed by the Contractor. In the event of disagreement between the Contractor and the Engineer, the Contractor shall, if required, make available such mechanical equipment as specified in order to test the reasonable removability or otherwise of the material. The decision of the Engineer as to the classification shall thereafter be final and binding.

The Contractor shall immediately inform the Engineer as and when the nature of the material being excavated changes to the extent that a new classification for further excavation is warranted. Failure on the part of the Contractor to timeously advise the Engineer shall entitle the Engineer to classify, in his sole discretion, such excavation as may have been executed in material of a different nature.

PSDB 1.3	SOILCRETE

The tendered rate shall include payment for the construction of the soilcrete complete and according to specifications including Portland Cement used at a rate of 7% of the dry density of the soil used and the placing of rocks to support the soilcrete at the end of the trenches.

PSDB 2	CLASSIFICATION OF EXCAVATION BY HAND (New Subclause 3.8)

PSDB 2.1	Soft excavation

Soft excavation shall be excavation in material that can be efficiently removed from the trench using a pick and shovel but not requiring prior breaking using mechanical equipment such as pavement breakers.

PSDB 2.2	Intermediate excavation

Intermediate excavation shall be excavation in material that requires prior breaking using mechanical equipment, such as pavement breakers with clay spades, before being removed from the trench.

PSDB 2.3	Hard rock excavation

Hard rock excavation shall be excavation in material other than 3.8.1 and 3.8.2 above which by nature of the material requires prior breaking using mechanical equipment, such as pavement breakers with moil points, before being removed from the trench.

PSDB 3	FREEHAUL (Subclause 5.6.8)

The freehaul distance within which the Contractor will be required to move material without separate compensation shall be 12km. Overhaul will be paid for the moving of material beyond that distance.

PSDB 4	MEASUREMENT AND PAYMENT (Subclause 9)

The freehaul distance will be 12km and not 2km.

SABS 1200 L: MEDIUM PRESSURE PIPELINES

PSL 1	MATERIALS

PSL 1.1	VALVES (Subclause 3.10)

Delete this clause and replace with the following:

Valves shall comply with the requirements of SABS 664. All valves shall be tested hydraulically to the specified pressure. During testing the valves shall meet two conditions: firstly with the pressure applied with the valve completely open and thereafter to either side of the gate with the valve completely closed.

All valves shall be coated with a protective layer of paint or solution applied in an approved manner. All valves shall close in an anticlockwise direction when viewed from above on the spindle. All cap tops supplied on the range of valves, shall be of the same size in order that one size valve key may be used.

PSL 2	CONSTRUCTION

PSL 2.1	DEPTH AND COVERING (Subclause 5.1.4)

Delete this clause and replace with the following:

PSL 2.1.1	Except where permitted in PSL 2.1.2 hereafter, water pipes shall be positioned in such a way as to maintain a minimum cover of 1500mm from the finished surface to the top of the pipe.

Where stormwater pipes and/or sewer pipes cross the water pipe, the minimum free distance between the outside of any of the pipes and the outside of the coupling of the water pipe shall be 150mm. Should, at the specified minimum cover, the free distance be less than 150mm, the water pipe will be lowered to the required level ensuring the free distance for a minimum distance of 1,0m, either side of the centre line of the stormwater- or sewer pipe, beyond which the pipe will be sloped back to the required level according to PSL 2.1.1 as detailed in subclause 5.1.4.2 of SABS 1200 L.

PSL 2.2	CONNECTION AT EXISTING PIPES

Add the following to this clause as subclause 5.11:

All the consumers concerned as well as the Engineer and the Statutory Authority shall be notified in writing at least one week before the existing water supply is interrupted. Arrangements for the interruption of the water supply shall be made in advance with the Statutory Authority and the Contractor shall not be entitled to lodge any claims as a result of problems caused by non-compliance. Under no circumstances shall employees of the Contractor be allowed to interrupt the water supply at any time.

All activities during the interruption of the water supply shall be planned and coordinated beforehand and all the preparations possible shall be completed before the interruption to minimize the inconvenience to the consumers. The Engineer has the authority to stop or to postpone the interruption and the Contractor will not be entitled to any claims in this regard, should the Engineer be of the opinion that the interruption was prolonged more than necessary as a result of bad planning by the Contractor.

PSL 3	STANDARD HYDRAULIC PIPE PRESSURES

PSL 3.1	TEST PRESSURES AND TIME OF TESTING (Subclause 7.3.1)

Add the following to subclause 7.3.1.2:

Test pressures on all pipes shall be 1,5 times its working pressure and the following test pressure shall be applied:

Class 9: 1 350 kPa,Class 12 : 1 850 kPa

PSL 4	MEASUREMENT AND PAYMENT

PSL 4.1	SUPPLY, LAY AND BED PIPES COMPLETE WITH JOINTS (Subclause 8.2.1)

Add the following to this subclause :

Rates for pipes and fittings shall include all joints and couplings that may be required. Additional payment will be made for class to class joints.

SABS 1200 LB : BEDDING (PIPES)

PSLB 1	MATERIALS (Clause 3)

PSLB 1.1	BEDDING (Subclause 3.3)

Delete this subclause and replace with the following :

Bedding for rigid pipes shall be as for Class C (see Drawing LB-1) and bedding for flexible pipes shall be selected granular material and selected fill material (see Drawing LB-2) except where shown otherwise on the drawings.

Bedding cradle for Class C bedding shall be of selected granular material (see 3.1)

The material for the selected fill blanket shall in all cases comply with the requirements of 3.2.

PSLB 1.2	SUITABLE MATERIAL NOT AVAILABLE FROM TRENCH EXCAVATIONS (Subclause 3.4.2)

Change the freehaul distance in this subclause from 0,5 km to 2,0 km.

PSLB 2	MEASUREMENT AND PAYMENT

PSLB 2.1	FREEHAUL (Subclause 8.1.6)

Change this subclause to the following :

The freehaul distance is 12,0 km.

PSLC		CABLE DUCTS

PSLC 1	INTERPRETATIONS

PSLC 1.1	ABBREVIATIONS

Delete the words “Department of Post and Telecommunications” and insert the words “Telkom SA Limited”.

# PSLC 2	MATERIALS

# PSLC 2.1	DUCTS

Add the following:

The Contractor shall use the materials supplied to him by Telkom in the most economical manner. Materials lost or damaged through neglect on the part of the Contractor or his workmen shall be made good by the Contractor or the value thereof will be deducted from any monies due to him.

The Contractor shall cart all materials supplied by Telkom to the place of work and shall, on completion of the work, return all surplus material to Telkom.

# PSLC 2.2	BACKFILL

Delete the wording of this subclause and substitute:

Material to be used for backfill shall be subbase quality material complying with the requirements of Clause 3.2.1 of SABS 1200ME, and shall be compacted to a minimum of 90% of modified AASHTO density. At road crossings the ducts shall be encased in concrete or in soilcrete as specified in PSLB 3.1.

# PSLC 2.3	CABLE DUCT MARKERS

Delete the wording of this subclause and substitute:

The positions of cable ducts shall be marked on the kerbs or channels as described in PSLC 3.2.

PSLC 3	CONSTRUCTION

# PSLC 3.1	ROAD CROSSINGS

Delete the last sentence of this subclause and substitute:

The ducts shall be laid to the lengths shown on the drawings or as directed by the Engineer.

# PSLC 3.2	POSITION TO BE MARKED

Delete the wording of this subclause and substitute:

The position of each duct crossing shall be marked by imprinting a letter into the wet concrete of cast in situ kerbs or channels directly above the position of the duct. The indentations shall be 10mm wide and 6mm deep and the tool used shall be of an approved shape and design. The letter used to denote the various types of duct shall be as follows:

“F”	100mm high for Fire Hydrants

“P”	75mm high for Telkom ducts

“E”	75mm high for electricity cable ducts

“W”	75mm high for water reticulation pipes.

In the case of the letter “F” for fire hydrants the inside of the indentation shall be painted red using an approved type of paint.

Where it is not possible to mark the positions of the ducts by indentations in freshly placed concrete, the positions shall be marked on the kerbs and/or channels by attaching specially manufactured marker plates to the kerbs and/or channels using an approved epoxy adhesive. The plates shall be constructed of durable, corrosion resistant materials and shall have a yellow background with black lettering in the case of ducts for Telkom, electricity and water, and a yellow background with red lettering in the case of ducts for fire hydrants. The types of materials and the sizes of the plates and lettering shall be approved by the Engineer.

The positions of the ducts shall be marked on both sides of the road as directed by the Engineer.

PSLC 4	MEASUREMENT AND PAYMENT

PSLC 4.1	GENERAL

Add the following:

Measurement and payment shall distinguish between items that are to be carried out using conventional construction methods and items that are to be carried out using labour intensive construction methods.

PSLE 3	MATERIALS

PSLE 3.1	CULVERT UNITS AND PIPES

- Precast Concrete Pipes

All concrete pipes shall be reinforced and shall have ogee joints.

- Skewed Ends

Skew ends shall be cut on site and an approved epoxide coating shall be applied to the cut ends immediately after cutting.

- Add the following new sub-item to subclause 3.1:

- Pipes for groundwater drains:

Pipes for groundwater drains shall have the specified internal diameter, which shall not be less than 100mm, and shall be perforated pitch fibre pipes complying with SABS 921.

The size of the perforations in perforated pipes shall in all cases be 8mm diameter +/1 1.5mm  and the number of perforations per meter shall not be less than 26 for 100mm pipe and 52 for 150mm pipe. Perforations shall be placed in two rows for 100mm pipes and four rows for 150mm pipes, as shown on the drawings.

Slotted pipes shall have a slot width of 8mm with the tolerance of 1.5mm in width. The arrangement of slots shall be to the Engineer’s approval but the total slot area shall not be less than specified for perforations.

# PSLE 3.3	BEDDING MATERIAL

Add the following sub-item:

# PSLE 3.3.3	Permeable Material

Permeable filter materials for ground water drains shall consist of sand and/or crushed stone of suitable gradings. Use may also be made of geofabric material.

Permeable materials shall conform to the following requirements:

- Sands shall be clean, hard sand obtained from approved borrow sources.

Depending on the particular conditions of each case the required sand shall be either coarse, medium or fine grades.

When suitable sands are not available from borrow sources, the Engineer may require that they be procured from commercial sources outside the Site.

- Crushed stone shall be graded crushed stone conforming to the following requirements:

Percentage passing:

26.5mm sieve				100

13.2mm sieve				60 – 85

Fine grade:

Minimum of 15% passing 3.35mm

Maximum of 15% passing 1.18mm

Coarse grade:

Minimum of 15% passing 6.70mm

Maximum of 15% passing 2.36mm

The aggregate shall be evenly graded between these limits. The aggregate crushing value of the stone shall not exceed 30 when tested in accordance with TMH 1 Test Method B1.

The Engineer shall indicate the grades of sand and crushed stone to be used to suit each case.

# PSLE 3.4	MANHOLES, CATCHPITS AND ACCESSORIES

# PSLE 3.4.1	Bricks

Notwithstanding the provisions of subclause 3.4.1 the bricks to be used on this 	contract shall be “Engineering Bricks”.

PSLE 5	CONSTRUCTION

PSLE 5.1	TRENCH BOTTOM

## PSLE 5.1.1	Pipe Culverts

Amend the description of subclause 5.1.1 to include groundwater drains.

## PSLE 5.2	BEDDING AND LAYING

Add the following subclause:

## PSLE 5.2.6	Construction of groundwater drains

A layer of permeable material of the class and thickness as shown on the drawings shall be placed on the bottom of the trench and lightly tamped and finished to the required gradient.

Pipes of the type and size required shall then be firmly bedded on the permeable material true to level and grade, coupled where required and the trench backfilled with further permeable material to such height above the pipes as shown on the drawing or directed by the Engineer. The permeable material shall be lightly compacted and finished to the required level.

Further layers or finer permeable material shall then be placed, lightly compacted and finished to an even surface as directed by the Engineer, in layers not exceeding 100mm and compacted to at least the same density as the surrounding material. The trench must be specially protected against the ingress of water before completing the impermeable layer.

Permeable material must be placed in layers of not more than 300mm at a time and lightly compacted. The total thickness of each type of permeable material must be carefully controlled, and when placing the thinner layers, suitable spaces must be used for this purpose. When placing successive layers the lower layer must not be walked on or disturbed more than can be avoided. Care shall be taken to prevent the contamination of permeable material during construction of the groundwater drains and all permeable material contaminated by soil or silt shall be removed and replaced by the Contractor at his own expense.

Where plain butt joint pipes are used they shall be laid firmly together to prevent infiltration of backfill material. Perforated and slotted pipes shall be joined by couplers. Perforated pipes shall be laid with the perforations at the bottom, as instructed.

The higher end of groundwater pipe drains shall be sealed off with a cap or loose concrete cap of Class 20/19 concrete as shown on the drawings and at the lower end the pipe drain shall be built into a concrete head wall providing a positive outlet or connected to stormwater pipes or culverts.

## PSLE 8	MEASUREMENT AND PAYMENT

## PSLE 8.1	GENERAL

Add the following:

Measurement and payment shall distinguish between items that are to be carried out using conventional construction methods and items that are to be carried out using labour intensive construction methods.

## PSLE 8.2	SCHEDULED ITEMS

Add the following items:

## PSLE 8.2.14	Pipes in groundwater drains

Perforated pitch fibre pipes complete with couplings:

a)	100mm internal dia. 	Unit : m

b)	150mm internal dia. 	Unit : m

The rate shall include full compensation for the procuring, furnishing, laying and jointing the pipes and fittings as specified.

PSLE 8.2.15	Geofabric material (Description of type and grade) 	Unit : m2

The tendered rate shall include full compensation for furnishing, procuring, cutting, wastage, placing and protecting the geofabric as specified.

## PSLE 8.2.16	Permeable material

a)	Sand from approved borrow source 	Unit : m3

b)	Sand from commercial source 	Unit : m3

- Crushed stone :

i)	 Fine grade 	Unit : m3

ii) Coarse grade 	Unit : m3

The tendered rate shall include full compensation for procuring, transporting, furnishing and placing the material as specified.

PSLE 8.2.17	Items for concrete caps and concrete outlet structures shall be measured and paid for in accordance with the provisions of the relevant sections of SABS 1200G or SABS 1200GA.

### PSLE 8.2.18	Demolish and dispose of existing stormwater structures

a)	Plain concrete 	Unit : m3

b)	Reinforced concrete 	 Unit : m3

c)	Brickwork 	Unit : m3

The provisions of Clause PSC 3.1 shall apply.

### PSLE 8.2.19	Remove and stack existing stormwater pipe

(diameter stated) 	Unit : m

The unit of measurement shall be the meter of pipe of specified diameter removed and stacked at a site designated by the Engineer. The tendered rate shall include full compensation for the removal, transporting and stacking of the pipe at the designated site, but shall exclude the cost of excavation and backfill.

### PSLE 8.2.20	Remove and dispose of existing stormwater pipe

(diameter stated) 	Unit : m

The unit of measurement shall be the meter of pipe of specified diameter removed and disposed of at the spoil site. The tendered rate shall include full compensation for the removal, transportation and disposal of the pipe at the spoil site, but shall exclude the cost of excavation and backfill.

### PSLE 8.2.21	Alteration to existing structure

a)	description of alteration 	 Unit : No

b)	etc. 		Unit : No

The unit of measurement shall be the number of existing structures altered as scheduled.  The tendered rate shall include full compensation for altering the structures as described and shall include for all excavation, labour, plant, materials, accessories, etc. required to complete the work.

### PSLE 8.2.22	Extra-over Item 8.2.1 for building pipe into existing structure

(pipe diameter stated) 	Unit : No

The unit of measurement shall be the number pipes of specified size built into existing structures. The tendered rate shall include full compensation for the extra work involved in breaking into the existing structure and building in of the pipe.

### PLSE 8.2.23	Extra-over Items 8.2.8 and 8.2.9 for constructing structure

over existing pipe (type of structure and diameter of pipe stated) 	 Unit : No

The unit of measurement shall be the number of structures of specified type constructed over existing pipes. The tendered rate shall include full compensation for the extra work involved in constructing the structure over the existing pipe and shall include for cutting out and disposal of the relevant section of the existing pipe.

PSLE 8.2.24	Brick up ends of pipes (thickness of brickwork

and size of foundation specified 	 Unit : m2

The unit of measurement shall be the square meter of brickwork of specified thickness. The tendered rate shall include full compensation for all the labour, plant, materials and incidentals required to brick up the ends of the pipes and shall include for the concrete in the foundation for the brick wall.

PSG		CONCRETE (STRUCTURAL) (SANS 1200 G)

PSG2		Interpretations

PSG2-1	Exposure condition (Subclause 2.4.1)

All concrete on the Works shall be as specified for severe exposure condition.

PSG2-2	Strength concrete (Subclause 2.4.2)

Unless otherwise specified on the drawings or in the Schedule of Quantities, all structural concrete shall be Grade 35MPa/19mm.

PSG2-3	Joints (Subcause 2.4.3)

Notwithstanding Subclause 2.4.3, "designated joints" will only be joints that are shown on the drawings.  Any other joints that are required by the Contractor as a result of his construction constraints or for any other reason, whether approved by the Engineer or not, will not be considered to be designated joints as defined in Subclause 2.4.3, i.e. they will be considered to be "non-designated" joints.

No vertical joints will be allowed in the reservoir walls.

PSG3		Materials

PSG3-1	Cement (Subclause 3.2)

All cement used in the works shall be Portland cement CEM II of strength class 42,5 complying with SANS EN 197-1.

PSG3-2	Storage (Subclause 3.2.3)

Cement shall be used in the order in which it is received.

Unless approved by the Engineer, cement kept in storage for longer than 8 weeks shall not be used in the Works.

Any cement that contains lumps that cannot easily be crumbled to powder between the fingers, may not be used.

PSG3-3	Water (Subclause 3.3)

Only potable quality water from an approved source may be used for mixing concrete.  Water from a river or stream may however be used for curing.

PSG3-4	Aggregates (Subclause 3.4.1)

The maximum aggregate size shall be 25mm.

Aggregates may be obtained from local sources subject to testing of its suitability by an approved laboratory and approval by the Engineer.

Aggregates shall be tested periodically for reactivity, the cost of which shall be deemed included in the rate tendered for concrete.  A design mix will have to be made and the results submitted to the Engineer for approval 14days prior to casting the first concrete.

PSG3-4.1	Aggregates for grouting

Notwithstanding the requirements of Subclause 3.4.1, the grading of the fine aggregate (sand) and coarse aggregate (stone or pea gravel) to be used for grouting shall conform to the gradings given in Tables 1 and 2 respectively, below.

| TABLE 1 - SAND |  |  | TABLE 2 - STONE OR PEA GRAVEL |  |
| --- | --- | --- | --- | --- |
| Test sieve nominal aperture size, mm | % Passing (by mass) |  | Test sieve nominal aperture size, mm | % Passing (by mass) |
| 9,5 4,75 1,18 0,3 0,15 | 100 95 - 100 45 - 65 5 - 15 0 - 5 |  | 9,5 4,74 2,36 | 100 95 - 100 0 - 5 |

PSG3-4.2	Fine Aggregates for concrete

Fine aggregate for concrete shall comply with table 3 below.

| TABLE 3 – SAND |  |  |
| --- | --- | --- |
| Test sieve nominal aperture size, mm | % Passing (by mass) |  |
| 4.75 2.36 1,18 0,6 0,30 0.15 0.075 | 90-100 75 - 100 60 - 90 40 - 60 20 – 40 10 – 20 5 - 20 |  |

PSG3-4.3	Aggregates on roof

Quartzite stone chips with a nominal size of 25mm shall be placed on top of the reservoir roof in a 75mm layer.

PSG3-5	Pulverised fly ash (FA)

PSG3-5.1	General

Concrete containing a percentage of FA shall be termed FA concrete.

All concrete used shall be FA concrete unless otherwise shown on the drawings or ordered by the Engineer.

FA concrete shall conform to the requirements of SABS 1200 G for concrete and the additional requirements specified below.

PSG3-5.2	Source and quality

Fly Ash shall be procured from an approved source and shall be of a consistent quality conforming to SABS 1491 Part II.  In particular it shall be tested for and shall conform with the following:

- the loss on ignition shall not exceed 5%

- the percentage by mass retained on 45 micron screen shall not exceed 12,5%.

PSG3-5.3	Cementitious material

The cementitious material used for FA concrete shall consist of a mixture of between 75% and 80% by mass of ordinary portland cement and of between 25% and 20% by mass of FA.

In addition all concrete used for construction of water retaining structures shall contain an admixture that waterproofs by crystallization (Xypex or similar approved) at a rate in accordance with manufacturer’s recommendation.

PSG3-6	Concrete using reactive aggregates (Subclauses 3.2 and 3.4)

The Contractor shall provide the Engineer with sufficient data to enable him to assess the degree of alkali-aggregate reactivity of the aggregates to be used for concrete.

Where reactive aggregates and other quartzite aggregates are used for concrete, the Contractor shall, in order to ensure that the concrete is not subject to alkali-aggregate reaction, design his mixes and/or use cement with a sufficiently low alkali content such that the total equivalent sodium oxide content of the concrete is less than 1,8 kg/m3.

(NOTE:  The equivalent sodium oxide content (alkali content) is measured as (Na20 + 0,658 K20).  For cement it is expressed as a percentage by mass, for concrete it is expressed in kg/m3).

In the case of other aggregates that are less reactive the Engineer will determine the type and degree of precautionary measures to be adopted.

PSG3-7	Dolomitic aggregate (Subclause 3.4)

Coarse and fine dolomitic aggregate shall be used where required in terms of PSLD3-2.  When tested in accordance with the method specified in Appendix C of SABS 677, not more than 25% by mass of the dolomitic aggregate shall be insoluble in hydrochloric acid.

PSG3-8	Samples (Subclause 3.4)

At least one month before commencement of concrete work the Contractor shall supply at his own cost representative samples to the Engineer of the aggregates he intends using, together with certificates from an approved laboratory indicating that the aggregates comply with the specifications.  Approximately 50 kg of each sample of aggregate shall be supplied.

PSG3-9	Use of plums (Subclause 3.4.2)

The use of plums will not be permitted.

PSG3-11	Admixtures (Subclause 3.5.1)

The use of admixtures will be subject to the approval of the Engineer.  The information listed in Subclause 3.5.1 shall be provided.

In addition all water retaining structures will include admixture as specified in PSG 3-5.3.

PSG3-12	Materials for movement joints

PSG3-12.1	General

The various jointing materials, the manufacturers of the materials and the methods of application shall be as approved by the Engineer.  Materials shall be stored and protected to avoid damage, degradation, distortion or contamination.

The joint materials shall be resistant to ultraviolet light and to biological degredation.

PSG3-12.2	Waterstops

Waterstops shall be of approved manufacture and of the pattern and the material and widths scheduled and specified and shown on the drawings.  They shall comply with the tolerances specified in Subclause 6.1. They shall conform to Specifications CKS 388 or 389, for natural rubber or PVC respectively.

All intersections between waterstops shall be prepared by mitring and welding/vulcanising intersection pieces in the factory in accordance with the manufacturer's instructions and to approval of the Engineer.  Only straight lengths of waterstop may be field welded using the appropriate jigs and tools.

Where required, waterstops shall have eyelets so that they may be tied securely to the adjacent reinforcement.  "Rearguard"-type waterstops shall have flanges or cleats that grip effectively.

PSG3-12.3	Fillers

Closed cell expanded polyethylene fillers shall be precut to suit the application with a tear-out strip for forming the specified recess for the sealant.  If so required the filler shall be glued into position with an approved epoxy glue.

PSG3-12.4	Bondbreakers, primers and sealants

The bond breaker (if specified) shall be self-adhesive PVC tape (or equal, approved material) with a width the same as the joint recess into which it is to be applied.

The primer, if required for the sealant, shall be fully compatible with the sealing compound that is to be used.

The elastomeric sealant shall be either a two-component polysulphide liquid polymer base complying with the requirements of SABS 110 or a polyethylene based polyurethane "pouring grade" for horizontal or near horizontal joints or "gun grade" for vertical/overhead joints and joints steeper than 1 in 10 to the horizontal.  All elastomeric sealants shall comply with BS 4254 Type A1 and shall have a movement tolerance of 25%.

PSG4		Plant

PSG4-1	Mixing plant and vibrators (Subclauses 4.3 and 4.4)

Stand-by mixers and vibrators of adequate capacity and with an independent power unit shall be maintained on site for immediate use in the event of breakdown of the regular mixers or vibrators or failure of the power supply.

PSG4-2	Formwork ties (Subclause 4.5.3)

The use of sleeves for formwork ties through the walls of water-retaining structures will not be permitted.  Ties, when cast in, shall have some form of positive anchorage to prevent any rotation when loosening formwork.

For watertight concrete structures the shutters shall be fastened using an approved imbedded fastening system.  Open ferrules will not be permitted in the reservoir.

PSG4-3	Formwork: chamfers and fillets

All exposed external angles in concrete work shall have 20 mm x 20 mm chamfers unless otherwise specified or ordered, but the top edge of a slab that is to receive an applied finish shall not be chamfered.

Internal corners in concrete work need not have fillets unless such fillets have been specified on the drawings or ordered by the Engineer.

PSG4-4	Water-bath

A temperature-controlled water-bath with a capacity to cure two hundred cubes shall be provided on site.  The water-bath shall be located under cover.

PSG5		Construction

PSG5-1	Reinforcement

PSG5-1.1	Fixing (Subclause 5.1.2)

Fixing of reinforcing bars by welding and heating of bars will not be permitted.

PSG5-1.2	Spacers

Spacers of approved design include approved plastic or other proprietary spacers, or purpose made precast mortar blocks.

Where mortar blocks are used they shall be properly shaped so as not to slip out of position and shall be made of the same mix as the mortar of the concrete in which they are to be placed.  The mortar shall be well compacted by approved means into the moulds to result in blocks with a density of at least 2 300 kg/m3 and which are free from honeycombing.  The mortar blocks shall be cured in water for at least 7 days.  Blocks which have not been manufactured and cured strictly in accordance with these requirements or which are in any other way considered unsatisfactory by the Engineer, will be rejected and shall be removed from the Site.

PSG5-1.3	Cover (Subclause 5.1.3)

In Subclause 5.1.3(a) amend the words "bar or stirrup" to read: "bar, secondary reinforcement, stirrup, tying-wire knots or wire ends".

Tying wire may not encroach on the specified minimum cover by more than a single strand thickness.

PSG5-2	Formwork

PSG5-2.1	Classification of finishes (Subclause 5.2.1)

Rough formwork Degree of Accuracy III may be used on the outside faces where concrete is more than 500mm below the final ground level.

PSG5-2.2	Special smooth finish

All concrete surfaces that will be exposed above the final ground levels shall have a special smooth finish to a Degree of Accuracy I.  The formwork used shall be high-grade, unblemished and regular in size.  Formwork ties shall be placed in a regular pattern.  The special smooth finish shall be an off-shutter finish to the concrete such that no after treatment is required other than at the positions of formwork ties.

PSG5-3	Concrete

PSG5-3.1	General (Subclause 5.5.1.1)

The concrete mix design for strength concrete must be prepared in an approved laboratory and the results of actual test mixes must be submitted for approval together with 7-day and 28-day strength test results.  Special attention is drawn to the fact that the concrete mix must provide a very dense and impervious concrete.

The concrete shall also be tested for water sorptivity, oxygen permeability, chloride conductivity, depth of cover and shrinkage.

No concrete shall be cast until the mix designs have been approved by the Engineer.  The Engineer may call for revised mix designs at any stage during the Contract.

Any mix for use in the wall or floor of a water-retaining structure shall have a water/cement ratio not exceeding 0,5, shall contain not less than 325 kg cement per cubic metre of concrete and the proportions of the various aggregates shall be such as to produce a density of at least 2 400 kg/m3.

In order to facilitate increasing the workability of concrete in the fresh/plastic state, to ensure watertightness without increasing the water/cement ratio, the Engineer may approve the use of an additive.

The workability of concrete shall be assessed by means of the slump test.  The slump of each batch of concrete shall be taken and recorded directly before casting.

PSG5-3.2	Chloride content (Subclause 5.5.1.4)

With reference to Table 4, efflorescence will not be acceptable on any exposed concrete surface.

PSG5-3-3.	Strength concrete (Subclause 5.5.1.7)

Unless otherwise specified on the drawings or in the Schedule of Quantities, all structural concrete shall be Grade 35 MPa watertight concrete.

PSG5-3.4	Batching (Subclause 5.5.2)

Batching of strength concrete shall be by mass.  Prescribed concrete may be batched by volume.

PSG5-3.5	Ready-mixed concrete (Subclauses 5.5.3.2 and 7.3)

Concrete from a central concrete production facility other than on the construction site will be permitted and, apart from test results in terms of 7.3.1, 7.3.2 and/or 7.3.3, test results obtained by such a production facility as part of its quality control system will be accepted for evaluation in terms of Subclause 7.3.4, provided they are stored and cured on site.

PSG5-3.6	Placing of concrete (Subclause 5.5.5)

Structural concrete shall not be cast directly against the side of any excavation without the use of formwork unless prior approval has been obtained in writing from the Engineer.

Concrete used in pipe trenches for encasement may be cast directly against the side of the excavation.  Concrete for thrust/anchor blocks shall be cast directly against the side of the excavation.

The casting procedure shall be submitted to the Engineer for approval at least 14 days prior to the start of casting.

After vibration, the concrete shall be spaded in corners, in angles and against forms to release air bubbles which may have been trapped in these positions.

PSG5-4	Construction joints (Subclause 5.5.7)

PSG5-4.1	General

The edge of joints, exposed to view in the finished structure, shall be formed with suitable beads to provide a straight edge true to line and level.

All joints, other than expansion, contraction and other movement joints, shall be treated as follows:

As soon as practical, but not before 15 hours after placing, the construction joint surface shall be prepared to receive fresh concrete.  This preparation, as specified in 5.5.7.3(a) to (d), shall be such as to remove all laitance or inert material which may have formed and the specified chipping or sand blasting shall be such as to produce a roughened surface all over.

When concreting is interrupted concrete surfaces shall be protected from the sun as specified in Subclause 5.5.8(d) or by means of hessian kept damp until concreting is resumed.  The Engineer is to be informed immediately when an interruption occurs in the casting of the concrete.

All constructional joints (both designated and non-designated, see PSG2-3), (i.e. all joints other than movement, contraction and expansion joints) shall be dealt with as specified in Subclause 5.5.7.3.

Unless construction joints between designated joints shown on the drawings are authorized by the Engineer in writing, concrete in the floor and wall shall be cast continuously between the designated joints shown on the drawings.

PSG5-4.2	Formed joints

Each joint shall be formed as shown on the drawings, complete with shear key rebates, waffle formwork, V-feature, waterstops, "Flexcell" or equal, approved joint filler, dowel bars and their PVC tubes, etc. as indicated.

- Construction joints in walls and footings

Walls of the reservoir shall not have vertical joints.

All construction joints in the reservoir walls and footing shall be cast with waterstops.  Waterstops shall be galvanised iron or 2mm thick HDPE strips.  Payment shall be per linear meter.  The rate shall include supply and casting in of the waterstop.

- Construction joints in roof slabs

Construction joints in the roof slab are permitted.  The position of these joints shall be approved by the Engineer.  These joints shall be cast against a vertical shutter leaving a 15mm deep by 20mm wide recess which is sealed with one part poly-sulphide sealer on completion.  The sealer used and method of application shall be to the Engineer’s approval.  No additional payment shall be made for these joints.

- Construction joints in floor

Construction joints in the floor are only permitted where indicated on the drawings.

- Expansion and contraction joints

Expansion and contraction joints shall be constructed as detailed on drawings using PVC or rubber water stops.  Water stops extruded from recycled material shall not be permitted.

Prior to bandaging, concrete surfaces shall be scabbled with a mechanical scabbler and water jetted with a 120 bar water jet. All joints shall be butt jointed and patched over.

The waterproofing bandage shall comprise of two elements:

(i)	A 2 mm thick Hypelon strip (350 mm wide for expansion joints and 250 mm wide for contraction joints)

(ii)	A 1 mm x 60 mm stainless steel strip with polythene backing bond breaker to the detail shown on the drawing.

The bandage shall be applied by coating the concrete and underside of the hypelon bandage with an epoxy adhesive.  The stainless steel strip is first positioned over the joint and the bandage with epoxy adhesive placed over the stainless steel strip.  All trapped air shall be eliminated by hand rolling the bandage until the epoxy is fully cured.

Payment shall be per linear meter.  The rate shall cover all costs for the supply and application of water stops and bandaging including the installation of the stainless steel strip.

Expansion and contraction joints shall be formed true to line in smooth formwork.

All surfaces shall be thoroughly cleaned of all accretions of concrete or other foreign matter by scraping or other approved means.

Particular care shall be taken to compact the concrete around water stops, edges, etc.

PSG5-4.3	Non-designated joints

Any non-designated joints shall be identical to designated joints, as shown on the drawings, which would be used in similar positions and perform the same function.

PSG5-4.4	Joints between footings or floors and walls or columns

Construction joints between foundations, footings or floors and walls, columns or piers connected to them, shall not be made flush with the supporting surface, but shall be made at a distance above the footing or floor shown as on the drawings or approved by the Engineer.  The "kicker" shall be cast as an integral part of the foundation, footing or floor.

PSG5-4.5	Application of primers and adhesives

The concrete to which the primer or adhesive is to be applied shall be dry and shall be cleaned of all dust, grit, grease, surface laitance and foreign matter by compressed air and/or water, solvents, or other suitable approved means.  The Contractor shall provide on Site an approved moisture meter to measure the degree of dryness of the joint.  This meter shall be made available to the Engineer for testing.  The joint shall be approved for the application of the primer and adhesive if the moisture content of the concrete is less than or equal to 5%.  It may be necessary to dry the concrete surfaces locally by means of a gas torch or other approved manner.

PSG5-4.6	Contraction and expansion joints

Contraction and expansion joints shall be formed true to line in smooth formwork.

Contraction and expansion joint surfaces shall be thoroughly cleaned of all accretions of concrete or other foreign matter by scraping or other approved means.

Particular care shall be taken to compact the concrete around waterstops, edges, etc., using adequate approved tools and experienced, reliable workmen.

Rebates for seals shall be formed to required dimensions and lines, or cut true to line and size by skilled workmen with special tools, after floating the surface and before the final set of the cement has taken place.  All rebates, etc., shall be adequately protected against damage until the completion of the work; accidental damage which in the opinion of the Engineer will impair the performance or appearance of the joint, shall be made good by reconstructing the work as directed by the Engineer.  Rebates for seals shall be grit blasted or wire brushed on all faces to remove surface laitance and thoroughly cleaned with soft brushes and/or compressed air jets, and, if necessary, dried by blow-lamp or other approved means before priming.

PSG5-4.7	Installation of waterstops in joints

Waterstops shall be held in the formwork so as to prevent air pockets forming underneath them.  Special precautions shall be taken to the approval of the Engineer, to ensure that all flexible watestops are in perfect contact with well compacted void-free concrete.  The Contractor shall provide satisfactory supervision of such vital operations.

PSG5-4.8	Installation of joint filler in expansion joints

Joints in the filler shall be neatly butted so as to exclude mortar from the joint.  Edges of filler strip against waterstops, concrete, formwork, projections, etc., shall also be closely fitted to exclude mortar, so that there is no resistance (other than the compression of the filler) to the expansion movement for which the joint is designed.

Joint filler shall be fixed to the first cast of concrete with an approved adhesive and as directed by the Engineer.

PSG5-4.9	Application of joint seals

Rebates shall be cleaned as required by PSG5-4.5 and shall be inspected and approved by the Engineer's Representative before filling.

Joint sealants and primers shall be applied strictly in accordance with the manufacturer's instructions. Flow and non-slumping grades shall be used for horizontal and vertical joints respectively.

Only skilled workmen, experienced in this type of work shall be employed to apply the sealant.

Immediately after the compound is applied the joint shall be protected against damage until completion of the Contract.

PSG5-5.1	Curing and protection (Subclause 5.5.8)

The applicable curing method shall be agreed upon with the Engineer.

Where the Contractor fails to cure for the minimum prescribed period according to the prescribed method, no payment shall be made for the relevant pour of concrete.

PSG5-5.2	Adverse weather conditions (Subclause 5.5.9)

No placing of concrete shall take place if the ambient temperature is below 5oC, or exceeds 32oC, or is likely to drop below 5oC or rise above 32oC during the casting period or within eight hours after casting is completed.

If concrete is to be cast during times of high ambient temperature or hot drying winds, the Contractor shall be responsible for taking the necessary steps to keep the placement temperature as low as possible.  Such steps include the spraying of the coarse aggregate with water, the painting of silos with reflecting aluminium paint, the insulation of tanks and pipelines, and the protection of concrete ingredients against the direct rays of the sun.  The area of the pour shall be shaded before and during concreting and the concrete shall be shaded from the time of mixing until eight hours after placing.

Windbreaks shall be erected if necessary.

PSG5-6	Concrete surfaces (Subclause 5.5.10)

PSG5-6.1	Screeded finish

After placing and compacting, the concrete on a top (unformed) surface shall be struck off with a template to the designated grades and tamped with a tamping board to compact the surface thoroughly and to bring mortar to the surface, leaving the surface slightly ridged but generally at the required elevation.  No mortar shall be added, and noticeable surface irregularities caused by the displacement of coarse aggregate shall be made good by re-screeding after the interfering aggregate has been removed or tamped.

PSG5-6.2	Wood-floated finish.  (Subclause 5.5.10.1)

Where wood-floating is ordered or scheduled, the surface shall first be given a finish as specified in PSG5-6.1 and, after the concrete has hardened sufficiently, it shall be wood-floated, either by hand or machine, only sufficiently to produce a uniform surface free from screeding marks.

PSG5-6.3	Steel-floated finish

Where steel-floating is specified or scheduled, the surface shall be treated as specified in PSG5-6.1 except that, when the moisture film has disappeared and the concrete has hardened sufficiently to prevent laitance from being worked to the surface, the screeded surface shall be steel-trowelled under firm pressure to produce a dense, smooth, uniform surface free from trowel marks.

PSG5-7	Watertight concrete (Subclause 5.5.11)

The floors, walls and roof of the reservoir shall be considered to be watertight concrete and Subclause 5.5.11 shall apply.

PSG5-8	Defects (Subclause 5.5.14)

All defects shall be repaired as soon as possible after the formwork has been removed and the Engineer has inspected the concrete.  A statement of the method to be used for each repair shall be submitted to the Engineer for his approval before any work is carried out.  The Engineer may prohibit the further placing of concrete in the particular area concerned until he is satisfied that the repair has been satisfactorily executed.

All honeycombing shall be repaired by cutting back to solid concrete and patching with a suitable epoxy mix to the approval of the Engineer.

PSG5-9	Concrete records (Subclause 5.5.15.a)

For each casting the contractor shall keep records of:

- Time elapsed between mixing and casting of concrete

- Time elapsed between batches cast

- Slump test results of each batch

PSG5-10	"No-fines" concrete

A nominal aggregate size of 19 mm shall be used in the manufacturing of "no-fines" concrete.  No fines concrete shall be laid under where specified and shall consist of coarse aggregate, cement and water only.  No fine aggregate shall be used.

The concrete shall be mixed in the following proportions:

Cement		:	50 kg

Aggregate		:	0,40 m3

Water			:	22,5

The specified depth of the no-fines concrete shall be cast in one pour.

Between 24 h and 48 h after the no-fines layer has been laid it shall be covered with a 1:4 cement and mortar layer 20 mm thick.  The mix shall be comparatively dry to ensure that it does not penetrate and block the cavities in the no-fines concrete.  The surface shall be steel floated to form a plane surface.  The mortar skim shall be cured in the same manner as concrete for a period of not less than 2 days.

Payment shall be per cubic metre of no-fines concrete placed.  The rate shall include compaction and skimming to the approval of the Engineer.

PSG5-11	Items to be cast in or grouted into concrete

PSG5-11.1	Casting pipes and specials in concrete

Where entry holes for pipes/specials have been provided in the walls, the Contractor shall be responsible for the concreting in of such pipes/specials regardless of whether or not these have been supplied by himself.

The Contractor is responsible to ensure watertight fittings in the concrete to the Engineer’s approval.

PSG5-11.2	Fixings for equipment supplied under separate contract

a) The Contractor will be responsible for the forming of pockets if applicable to holding down bolts for equipment supplied under a separate contract.  Holding down bolts will be supplied by and positioned by others.

b)After casting of the concrete all shuttering shall be removed and the sides of the bolt holes and surface on which the machine base is to be placed shall be scabbled to remove all defective concrete, laitance, dirt, oil, grease and loose material.

c) Upon completion of the positioning and alignment of equipment and when instructed by the Engineer the Contractor shall in collaboration with the mechanical contractor, grout up pockets and baseplates by filling pockets and voids under the baseplates with an approved non-shrink grout.

PSG5-11.3	Fixings for items supplied under this Contract

Holding down bolts or other fixings required for the installation of items supplied under this Contract shall be provided by the Contractor.  These fixings shall be cast in or grouted into pockets or installed by other means as approved by the Engineer.

Where anchor bolts are used which are installed into holes drilled into concrete or masonry these shall be of a type approved by the Engineer.  All such bolts used shall be manufactured from stainless steel or a metal with a resistance to corrosion equal to that of grade 304 stainless steel.  The metal used for bolts shall be compatible with galvanized mild steel.

Anchor bolts shall have minimum pull-out forces and minimum ultimate lateral loads at least equal to those specified below:

| Specified Anchor Size | Minimum Pull-out Force (kN) | Minimum Ultimate Lateral Load (kN) |
| --- | --- | --- |
| M6 | 10,35 | 7,60 |
| M8 | 13,70 | 11,15 |
| M10 | 19,44 | 15,95 |
| M12 | 31,85 | 26,90 |
| M16 | 50,45 | 45,80 |
| M20 | 60,50 | 71,20 |

PSG5-12	Supervision

Prior to carrying out any concrete work, the Contractor shall obtain the approval of the Engineer in respect of:

- Structural programme

- Description of casting sequence

- Concrete plant details

- Materials to be used in concrete

- Details of concrete

- Construction joints

PSG7		Testing

PSG7-1	Frequency of sampling

(Subclause 7.1.2) One sample shall consist of three concrete test 	cubes.

For each sample taken the position in the structure shall be recorded where the batch represented by that sample is placed.

Sampling of concrete of a particular grade shall be as specified in Subclause 7.1.2 with the following frequency of sampling referred to in Subclause 7.1.2.2 being amended to read as follows:

"A minimum 2 samples for 10 m3 (or less) of pour shall be taken for each grade cast on any day.”

PSG7-2	Early-Strength Testing (Subclause 7.2.4)

7 day tests shall be performed on 1 sample for 10 m3 (or less) of pour.  These results shall be submitted to the Engineer as soon as possible after testing.

PSG7-3	Watertightness test

The watertightness of the reservoir shall be tested as follows:

The roof shall be tested on completion by using a hose or sprinkler system to obtain a sheet floor over the whole area of the roof for a period of not less than 6 hours.

The clear/potable water retaining structures shall be disinfected before testing of the walls.

The entire inside surface of the reservoir including columns and roof shall be thoroughly hosed down with water and brushed until properly cleaned off all dirt and other foreign matter.

Chlorinated water shall be stored until the free chlorine level has dropped to an acceptable level.  Excess dirt swept from the floor into the sump may be discharged subject to written approval being obtained from the Local Authority.

For testing the liquid retention, the structure shall be initially filled with potable water to the normal maximum level with the water at a uniform rate of not greater than 2 m in 24 hours.

When first filled, the water level should be maintained by the addition of further water for a stabilizing period while absorption and autogenous healing take place.  After a stabilization period of 21 days, refill (top up) and record the water level at 24 hour intervals for a test period of 7 days.  During this 7 day test period the total permissible drop in level, after following for evaporation and rainfall, should not exceed 10 mm.

Notwithstanding the satisfactory completion of the test, any evidence of seepage of the liquid to the outside faces of the liquid retaining walls and the soffit of the roof shall be assessed by the Engineer against the requirements of the specification.

In the event of any leakage or dampness being evident at any stage of the filling or testing or in the event of the Engineer considering the final degree of watertightness to be unsatisfactory, the Contractor when ordered by the Engineer shall discontinue such filling or testing and shall, at his own expense, take approved steps immediately to rectify the leakage and to make the work thoroughly sound to the complete satisfaction of the Engineer.  If a lining is used for this purpose, it shall be sufficiently flexible and not be in any way detrimental of the water quality.  All such work of rectification shall be continued assiduously until a satisfactory test is obtained, which shall prove to the Engineer that watertightness has been obtained.

If required by the Engineer, the structure shall be retested before the expiry of the Defects Liability Period.  Any re-testing that may be required shall be at the Contractor’s expense.

The Works will not be certified complete until the structure has been proved by testing to be watertight to the satisfaction of the Engineer.

PSG7-4	Grouting

The Contractor shall, where so ordered, carry out a site test for each grouting procedure and each grouting gang to be used.  The tests shall be carried out on a dummy bedplate similar in configuration to that which is to be grouted, but not exceeding 1 m2 in area unless otherwise ordered.  When the dummy bedplate is dismantled, the underside shall show a minimum grout contact area of 80% with reasonably even distribution of the grout over the surface grouted except that, in the case of expanding grout, the minimum grout contact area shall be 95%.  The test shall show evidence of good workmanship and materials and the results shall be to the satisfaction of the Engineer.

The Contractor shall, when so ordered, make standard test cubes from various grout mixtures and also subject them to compression tests to determine whether the specified strength has been achieved.  Test procedures shall comply with the relevant requirements of Subclauses 7.2.1 to 7.2.3.

PSG7-4	Concrete properties

Acceptance criteria for concrete properties are stated below.

PSG7-4.1	Water sorptivity and oxygen permeability

| Table PSG 7.3.6.1 Water Sorptivity and Oxygen Permeability |  |  |
| --- | --- | --- |
| Acceptance Category | Test No. / Description / Unit |  |
|  | Water Sorptivity (mm/h) | Oxygen Permeability (log scale) |
| Concrete made, cured and tested in laboratory | 6 | > 10.0 |
| Full acceptance of in-situ cast concrete | < 8 | > 9.15 |
| Conditional acceptance of in-situ cast concrete (with remedial measures) | 8 - 15 | 8.75 – 9.15 |
| Rejection | > 15 | < 8.75 |

PSG7-4.1	Chloride conductivity

| Table PSG 7.3.6.2 Chloride Conductivity (severe to very severe conditions) |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Concrete | 100% PC |  | 10% CSF |  | 30% FA |  | 50% GGBS |  |
| Curing Period | 28d | 90d | 28d | 90d | 28d | 90d | 28d | 90d |
| Full wet cured | 1.25 | 1.00 | 0.50 | 0.45 | 1.50 | 0.40 | 1.25 | 1.00 |
| Moist cured (3 – 7d) | 1.75 | 1.60 | 0.60 | 0.55 | 2.25 | 1.25 | 2.25 | 2.00 |

PSG7-4.3	Concrete cover

| Table PSG 7.3.6.3 Concrete Cover |  |  |  |
| --- | --- | --- | --- |
| Test Description | Specified Cover (mm) | Acceptance Range |  |
|  |  | Minimum | Maximum |
| Concrete cover to reinforcement | 20 – 30 | As specified | As specified + 5 mm |
|  | 30 - 80 | As specified | As specified + 10 mm |

PSG8		Measurement and payment

PSG8-1	Formwork (Subclauses 8.1.1)

PSG8-1.1	Edges of blinding layer or “no-fines” concrete

No separate payment will be made for formwork to the edge of the blinding or “no-fines” concrete (refer to PSG5-10) layer.  The rates tendered for concrete to the blinding or “no-fines” concrete layer shall cover the cost of such formwork.

PSG8-1.2	Kickers									Unit:  m2

Formwork to the edges of kickers will be measured as plane (or circular) vertical (not as narrow widths).

PSG8-1.3	Chamfers and fillets (Sublauses 8.1.1.1 and 8.1.1.2)

No additional payment will be made for chamfers and fillets up to 40 mm wide.  Larger fillets and chamfers will be measured by length in accordance with Subclause 8.2.5.

PSG8-2	Reinforcement (Subclauses 8.1.2.2 and 8.1.2.3)			Unit:  tonne

Notwithstanding the method of measuring and paying for reinforcement specified in Subclauses 8.1.2.2 and 8.1.2.3, reinforcement will be measured and paid for as scheduled.

PSG8-3	Concrete (Subclause 8.1.3.3)  					Unit:  m3

The rates for concrete shall also cover:

a)	the use of dolomitic aggregate where prescribed,

b)	the cost of the preparation of design mixes by an approved laboratory and submission for approval by the Engineer (see PSG5-3.1),

c)	the cost of non-designated joints (see PSG2-4),

d)	screeded finish of unformed surface as specified in PSG5-6.1,

e)	inclusion of admixtures where specified, and

f)	necessary admixtures to ensure watertight concrete.

PSG8-4	No-fines concrete							Unit:  m3

No-fines concrete (refer to PSG5-10) will be measured by volume.

The rate shall cover the cost of supplying materials, constructing and placing in position the no-fines concrete, and shall include for the steel floated 20 mm mortar skim.

PSG8-5	Unformed surface finishes   (Subclause 8.4.4)			Unit:  m2

The rates for unformed surface finishes shall cover the cost of providing the respective surface finish as specified in PSG5-6.

PSG8-6	Joints (Subclause 8.5)

Only designated joints as shown on the drawings will be measured for payment according to the length of each type of joint constructed (see PSG2-3).  The rate shall cover the cost of all materials, labour and plant required to construct each type of joint specified on the drawings, including the cost of all shuttering, treatment of the joint as specified in Subclause 5.5.7.3, the provision of chamfers as specified where concrete is exposed, as well as testing and repairing where necessary.

Non-designated joints will not be measured for payment.

PSG8-7	Formed joints								Unit:  m2

Formed joints will be measured by the plane area of the joint.

The rates shall cover the cost of all operations and materials specified in Subclause 5.5.7 and

PSG5-4.2, and detailed on the drawings such as joint filler, dowel bars and tubes, bitumen coats, etc., but excluding waterstops or waterbars.

Waterstops and waterbars will be measured by length separately for each type.

PSG8-9	Holding down bolts							Unit:  No.

Fixing of holding down bolts will be measured by number.  The rate shall cover the cost of all things necessary to ensure that the bolts are effectively and rigidly held in position during casting, complete with sleeved pockets, all as detailed on the drawings.

PSG8-10	Grouting									Unit:  m3

Grouting of base plates and equipment bases will be measured by the volume of grout used.

The rate shall cover the cost of the supply and floating in of grout under the plates to ensure solid and complete filling of the gap.

PSG8-11	Items cast in concrete						Unit:  No.

Items cast in concrete will be measured by number separately for each type of item.

Notwithstanding Subclause 8.2.6, the rate shall cover the cost of fixing in position and casting in the item as construction proceeds, irrespective of whether the Contractor chooses to fix the item in the formwork and cast it in directly or to box out a hole and grout the item in subsequently.

The item will be measured and paid separately.

PSG8-13	Precast concrete cover planks					Unit:  m2

Precast paving slabs will be measured by the area paved.

The rate shall cover the cost of compacting the area, application of weed-killer, supplying, laying and bedding the slabs, grouting the joints and filling any gaps, all as specified.

PSG8-14	PFA concrete

Measurement and payment for PFA concrete shall be as specified in Subclause 8.1.3.

The tendered rate shall cover all costs in connection with the supply, storage, handling on site and mixing in of PFA.

PSG8-15	Water tightness test							Unit:  Sum

The watertightness test will be paid by a lump sum separately for each structure.

The sum shall cover the cost of all labour, equipment and materials to carry out the tests, as specified in PSG7-3, to rectify faults and to achieve a test result to the satisfaction of the Engineer.

The sum shall include for all water required over and above that required for one filling of the water retaining structure based on the assumption that water will be available in time through the potable water pipeline that shall be laid alongside the main sewer as part of this Contract.

A provisional item is provided for an extra payment to the above to allow for the water not being available through the pipeline in time and the Contractor has to make his own other arrangements for providing water for testing.  Such an arrangement shall only come into effect on the Engineer's instruction.

PSG8-16	Black plastic bond breaker						Unit:  m2

A 500 micron black plastic continuous layer is to be laid above the no-fines concrete under the reservoir floor.  The side and end laps shall not be less than 600mm.

Payment shall be by the square meter laid.  Care shall be taken not to rip or tear the sheeting.  All repairs shall be at the Contractor’s expense.

PSG8-17	Teflon Sliding Bearings						Unit:  m

Neoprene (Kilcher or similarly approved) Teflon sliding bearings shall be placed on the top of the reservoir wall prior to casting the roof slab.  The top of the wall shall be cast to a smooth steel float finish.

Payment shall be per linear metre for the preparing and placing of the bearings.  The rate shall include the supply, laying, jointing and masking of the bearings to the polystyrene strip.

PSG8-18	Poly-urethane sealants						Unit:  m

A one part polyurethane sealant shall be used in the outside joint between the reservoir roof and walls to the details shown and shall be finished off neatly leaving a smooth regular finish.

Payment shall be per linear metre.  The rate shall include the supply, preparation, sealing and finishing.

PSG8-19	Precast coping								Unit:  m

Precast coping to reservoir roof perimeter complete installation shall be paid per linear meter.

PSG8-20	Stone chips								Unit:  m3

Stones shall be quartzite with a nominal chip size of 25mm.  Chip stones shall be paid in cubic meter laid.

PSG8-21	Manhole covers							Unit:  No.

Manhole covers shall be paid per unit.

PSG8-22	Commercial Laboratory						Unit:  Prov Sum

A Provisional Sum for the services of a commercial laboratory has been included in the Bill of Quantities for the Engineer’s Acceptance Testing.  The use of this laboratory is for additional testing required over and above the testing specified in SANS 1200 G and the variations to SANS 12002 G specified above.  Testing shall only be paid on written instruction for additional testing from the Engineer.

The procedure for sampling and manufacturing, storing, curing and testing cubes shall be in accordance with SABS 863.

PSGA :	CONCRETE (Small Works)

PSGA 1	PLANT (Clause 4)

PSGA 1.1	FINISH OF CONCRETE (Subclause 4.4.2)

Change this subclause as follows :

The quality of the finished concrete surface shall be as follows :

All off-shutter concrete from 150 mm underneath the ground level	Smooth.

Unseen concrete up to 150 mm underneath the ground level	Rough.

PSGA 2	CONSTRUCTION (Clause 5)

PSGA 2.1	FIXING OF REINFORCEMENT (Subclause 5.1.2)

Add to this subclause :

No welding shall be allowed.

PSGA 3	CONCRETE (Clause 5)

PSGA 3.1	STRENGTH CONCRETE (Subclause 5.4.1.5)

Add to this subclause :

The following classes of concrete shall be used in the following positions:

Class 15/20	Blinding, mass concrete, encasement of pipes, etc.

Class 20/20	Strip foundations for brick walls and mass foundation.

Class 30/20	All structural concrete, including concrete floors and paving.

The Contractor shall design trial mixes in accordance with SABS 0100, Part II 1980, Appendix B. The target strength of the trial mix shall be determined using K equal to 1,7 and a standard deviation 5MPa for a "good" degree of site control. The average 28-day cube strength of the trial mix shall equal or exceed the target strength. The Contractor shall submit the trial mixes and the 7 and 28 day test results to the Engineer for approval. No concreting may proceed until the trial mixes have been approved.

PSGA 3.2	READY MIXED CONCRETE (Subclause 5.4.1.6)

Delete the subclause and replace with the following:

Ready-mixed concrete will be allowed on the site, provided the nominal mix proportions given in SABS 1200 GA Clause 8.4.1, apply. The prior approval of the Engineer is however required.

PSGA 3.3	BATCHING (Subclause 5.4.2.3)

Aggregates

Add to this clause.

Volume batching is permitted for concrete pours of up to 5,0m3. All greater quantities shall be weigh batched to an accuracy of 2%.

PSGA 3.4	MIXING (Subclause 5.4.3(e))

Delete this subclause and replace with the following:

(e)	Concrete shall be placed within thirty minutes of the start of mixing.

PSGA 3.5	CONCRETE SURFACES (Clause 5.4.8)

Add the following:

Concrete surface finishes required shall be indicated on the drawings and shall be classified as follows:

a)	Rough : This shall  comprise a lightly ridged surface as struck off with a tamping board. Degree of Accuracy III is required. This finish shall provide a good key for subsequent finishing with a screed or bituminous carpet.

b)	Smooth wood float : The surface shall be wood floated to a uniform surface free of trowel marks and to Degree of Accuracy II.

c)	Smooth steel float : The surface shall be accurately struck off and floated and finished with a steel float to a smooth and uniform surface, free of trowel marks, to Degree of Accuracy I.

Rubbing with a carborundum stone will be permitted but no plastering to correct imperfections will be permitted.

PSGA 3.6	CONSTRUCTION JOINTS (Clause 5.4)

Add to this clause :

Concreting shall be carried out continuously up to the locations where joints are shown on the drawings or up to approved locations. Joints shall be constructed in accordance with the details shown on the drawings.

The Contractor shall continue concreting through meal breaks or after normal working hours in order to complete work up to a construction joint and no extra payment shall be made to the Contractor for working overtime.

If, because of an emergency (such as a breakdown of the mixing plant or the occurrence of unsuitable weather), concreting has to be interrupted, concrete shall be finished off at the place of stoppage in the manner that will least impair the durability, appearance, and proper functioning of the concrete.

PSGA 3.7	JOINT SEALING (Clause 5.4)

Add to this clause :

Joints shall be formed as indicated on the drawings, using bitumen impregnated fibre board or closed cell expanded polyethylene compressible joint filler complying with AASHTO Specification M153.

Joints shall be sealed as indicated on the drawings, using rubberised bitumen joint sealant for concrete pavement complying with BS5212. Where indicated on the drawings joint sealant shall be backed by a Polythene Tape bondbreaker.

The use of the joint former and joint sealing materials and all joint sealing shall be carried out by workmen experienced in the use of the materials and shall be strictly in accordance with the instructions and recommendations of the manufacturer and supplier.

PSGA 3.8	MECHANICAL VIBRATION (Subclause 5.4.6.3)

Delete this subclause and replace with the following:

Only mechanical vibrations shall be accepted for the compaction of the concrete. Any other method of compaction shall only be accepted with the written approval by the Engineer.

PSGA 3.9	WATERTIGHT CONCRETE (Subclause 5.4.8.2)

Add to this subclause :

Manholes and the stormwater channel shall be watertight and no water leakage will be allowed at the joints.

PSGA 4	TOLERANCES (Clause 6)

PSGA 4.1	GENERAL (Subclause 6.1.1 and 6.4)

All concrete, excluding blinding and mass concrete, shall comply with the specified tolerances, except where a different tolerance is shown on the drawings, in which case the specification on the drawing shall prevail.

PSGA 4.2	TOLERANCES (Clause 6.4)

Degree of accuracy required is : (II).

PSGA 5	TESTS (Clause 7.1.1)

PSGA 5.1	FACILITIES AND FREQUENCY OF SAMPLING (Clause 7.1.1)

Facilities

Add the following :

The Contractor shall be fully responsible for sampling and testing the concrete at the frequency specified.

PSGA 5.2	FREQUENCY OF SAMPLING (Clause 7.1.2.2)

Add the following :

At least one sample sufficient for 3 cubes and a slump test shall be taken from each day's casting and from at least every 20m3 of concrete of each grade placed. More frequent slump tests shall be taken should the consistency of the concrete be seen to vary.

PSHA		STRUCTURAL STEELWORK (SUNDRY ITEMS).  (SANS 1200 HA)

PSHA3	Materials (Clause 3)

Where the words "Structural Steelwork" appear in the heading and in other relevant Clauses, amend to read "Aluminium, Stainless Steel and Structural Steel".

PSHA3-1	Stainless steel

All stainless steel items shall be Grade 304L material.

PSHA3-2	Structural steelwork (Subclause 3.1)

Structural steelwork shall comply with Grade 43 of BS 4360.

PSHA3-3	Aluminium

All aluminium items shall be grade M57S material anodized in accordance with SABS 199 Grade 25.

PSHA3-4	Bolts and nuts (Subclause 3.3)

All bolts, nuts and washers within water retaining structures or exposed to the rain, or with a diameter of 10 mm or less, all anchor bolts of any size in concrete or brickwork and all bolts of any size used in conjunction with stainless steel items, shall be manufactured from Grade 304L stainless steel.

All other bolts, nuts and washers with a diameter of 12 mm or greater shall be hot dip galvanized to SABS 763.  Nuts shall be tapped before galvanizing, taking into consideration the extra clearance necessary to allow for the thickness of galvanizing on the bolts.  If, after installation, there is any indication that galvanising has been stripped from either the nut or the bolt, both nut and bolt shall be removed and replaced.

PSHA3-6	Cast iron steps

Cast iron steps shall conform to BS 1247:11975 for general purpose.  Steps shall be fixed to walls by means of chemical anchoring.  The necessary precaution shall be taken to ensure watertightness of the walls.

PSHA3-7	Roof air vents

Roof air vents shall be 100mm diameter mild steel pipe shaped as indicated on the relevant detail drawing.  The face of the roof vents shall be covered with FC20 or equivalent expanded metal screen welded to the face of the pipe.  The vents shall be hot dip galvanised.

PSHA3-8	Rainwater outlets

Rainwater outlets shall be made of 150x125 box sections.  Box gutter outlets shall be hot dip galvanised.

PSHA3-9	Access ladders

Access ladders shall be constructed and installed as per detail drawings.  Access ladders shall be fixed to the walls using chemset bolts.  The necessary precaution shall be taken to ensure watertightness of the walls.

PSHA3-10	Manhole locking bars

Manhole locking bars shall

PSHA3-10	Vermin proof flaps

Vermin proof flaps shall be made of stainless steel.

PSHA4	Plant (Clause 4)

The Engineer may request at any time the mill certificate of the steel supplier.

All components shall be pre-fabricated in an Engineer approved steel fabrication yard.  No site fabrication or welding will be permitted.

PSHA5	Construction

PSHA5-1	Welds

All welds shall be fully continuous and not less than 6mm across the throat.

PSHA5-2	Bolts

All bolts and nuts shall be hexagonal type Grade 8.8 with threads of coarse pitch series and shall be hot dip galvanised in accordance with the requirements of SANS ISO 1461.

Before assembly, all bolts shall be coated with an approved nickel based Anti-seizure/corrosion protection compound.

Two washers shall be used with every bolt and nut to prevent damage to coatings.

PSHA7	Testing (Clause 7)

All welds shall be crack tested using die indicators.

PSHA8	Measurement and payment

PSHA8-1	Corrosion protection (Subclause 8.3.6)

Notwithstanding the requirements of Subclause 8.3.6, corrosion protection (painting and galvanizing) will not be measured separately, the prices tendered for the steel items being held to include for the cost of corrosion protection as specified.

PSHA8-2	Cast iron steps								Unit:  No.

Cast iron steps shall be paid per unit.  The rate shall include supply and installation of the steps where indicated.

PSHA8-3	Roof air vents								Unit:  No.

Roof air vents shall be paid per unit.

PSHA8-4	Rainwater outlets								Unit:  No.

Rain water outlets shall be paid per unit.

PSHA8-5	Vermin proof flaps							Unit:  No.

Vermin proof flaps shall be paid per unit.

PSHA8-6	Manhole locking bars							Unit:  No.

Manhole locking bars shall be paid per unit.

PSHC		CORROSION PROTECTION OF STRUCTURAL STEELWORK

(SANS 1200 HC)

PSHC5	Construction

PSHC5-1	Structural steel

All structural steel members shall be hot dip galvanized.

PSHC5-2	Floor panels, handrails, ladders and the like

The open grid and chequer plate flooring panels and frames, handrails, ladders and similar items shall be hot dip galvanized in accordance with the requirements of Subclause 5.9.

In addition handrails shall be degreased, primed and painted yellow with two coats of recoatable polyurethane to a minimum total dry film thickness of 70 micrometers after installation.

PSHC6	Tolerances

PSHC6-1	Film thickness tolerances

PSHC6-1.1	Individual coatings

At least 90% of all thicknesses measured shall comply with the minimum thickness of the system specification.  Up to 10% of all readings may be below the specific minimum thickness, but no reading shall be less than 70% of the specified minimum thickness.

PSHC6-1.2	Total dry film thickness

Not more than 10% of readings shall be less than the minimum specified and no reading shall be less than 90% of the specified minimum.  For immersion conditions no reading shall exceed the mean specified thickness by greater than 60% of the minimum, unless a concession is granted by the Engineer.

PSHC8	Measurement and payment

PSHA8-1 shall apply.

PSM	STREETS (General)

No changes.

PSW :	BUILDING WORK

PSW 1	SCOPE

This specification covers the supply of material and the construction of brickwork, waterproofing, carpentry and joinery, floor coverings, ironmongery metalwork, plastering, tiling, plumbing and drainage, glazing and painting as required and described on the drawings and in the bill of quantities.

PSW 1.1	GENERAL

PSW 1.1.1	SABS Specifications and codes of practice

Reference in this document to South African Bureau of Standards specifications and codes of practice shall be deemed to be references to the latest issues of such specifications and codes, as may be amended from time to time. Where possible, all articles, materials or items described as conforming to the SABS specifications must bear the SABS mark.

PSW 1.2	MANUFACTURERS' INSTRUCTIONS

Unless the Engineer otherwise directs, all materials shall be used, mixed, applied, fixed, etc. strictly in accordance with their manufacturers' printed instructions.

PSW 1.3	MATERIALS AND WORKMANSHIP

Materials shall be of the best quality and all work shall be done well and to the entire satisfaction of the Engineer who shall inspect the works.

The terms "approved" and "directed" shall mean the approval and direction of or by the Engineer.

PSW 1.4	SAMPLES

The contractor shall furnish without delay such samples as may be called for by the Engineer, who may reject all materials and workmanship not corresponding with the approved samples.

PSW 1.5	HANDING OVER

Rates shall include for protecting finishings, facing materials, components, fittings, equipment, etc., from staining or damage, and for handing over the works including any existing structures etc., affected by the works, in a clean and perfect state to the satisfaction of the Engineer.

### ANNEXURE C

OCCUPATIONAL HEALTH AND SAFETY

### FEZILE DABI DISTRICT MUNICIPALITY

DRILLING AND EQUIPPING OF SIX NEW BOREHOLES AND REFURBISHMENT OF TWO EXISTING BOREHOLES IN MAFAHLANENG/TWEELING

BID NO: FDDM/BID NO: 012/2023-24

OHS 	OCCUPATIONAL, HEALTH AND SAFETY

# SECTION A: INTRODUCTION

# 1.1 	Introduction to the Health and Safety Specification

The Construction Regulations (7 February 2014, R.84) places the responsibility on the Client to prepare a baseline risk assessment and a suitable, sufficiently documented and coherent site specific Health & Safety Specification, which informs the appointed contractor of all the health & safety requirements pertaining to the associated works on the construction site as well as risks not successfully eliminated during design.

# 1.2 	Purpose of the Risk Assessment

The purpose of the risk assessment is to identify risks and hazards to which persons may be exposed.

Base line risk assessment prepared by Agent of the Client attached. - Annexure 1

# 1.3 	Purpose of the Health and Safety Specification

The purpose of the Health and Safety Specification is to assist in achieving compliance with the Occupational Health & Safety Act 85/1993 and the promulgated Construction Regulations (7 February 2014, R.84) in order to manage health and

safety risks and to reduce incidents and injuries. This specification shall act as the basis for the drafting of the construction Health & Safety Plan by the Principal Contractor and all subsequent Health & Safety Plans by Contractors.

The Health and Safety Specification sets out the intention of the Client and Designer. It also includes arrangements made by the Client, Health and Safety Agent or consulting Project Manager to ensure that the parties involved in the project cooperate and co-ordinate their activities, to remove or minimize the risks to health and safety of those who are involved in the construction project, or who may be affected by the work activities.

This document sets out the requirements, under a number of sections of Health and Safety Legislation, for the successful health and safety management of the project by the Principal Contractor in accordance with the requirements set out in this Health and Safety Specification. The Principal Contractor will be expected to integrate his own health and safety policy and arrangement documents into their Health & Safety Plan.

The format is in line with the requirements of Regulation 5. of the Construction Regulations (7 February 2014, R.84), for a Health and Safety Plan to be developed before the commencement of construction.

# 1.4 	Implementation of the Health and Safety Specification

The Construction Health and Safety Plan must be handed to the appointed Health and Safety Agent prior to the commencement of works. The Principle Contractor must submit the signed “Acknowledgement of receipt” (- Annexure 2) of this Health and Safety Specification on the date of issue or return to the Client or their representative with tenders. No Principle Contractor may commence with construction work until their Health and Safety Plan has been reviewed and approved by the appointed Health and Safety Agent.

1.5 	Health and Safety Targets

The following health and safety targets have been set for achievement during the period of this project.

- The achievement, by the Principal Contractor, of an incident-free project, as far as possible, with the prevention of all incidents, and the achievement of a nil “lost time injury” rate.

- The workforce’s co-operation in ensuring that health and safety is everybody’s responsibility.

- A proactive approach to health and safety by the construction management team.

- That safe working will be a condition of employment in all contractors’ organizations.

# 1.6 	DEFINITIONS

"CLIENT" 	Shall mean Mafube Local Municipality

“H&S” 		Health, Safety & Environment

“Contractor” 	Refer to the Mandatory who is employed on the Project and includes his own sub contractors who he further employs.

“Employer” 	Means any person who is employed by or works for an employer and who receives or is entitled to receive any remuneration or who works under the direction or supervision of that employer.

“Mandatory”	Includes an agent, a Contractor or a subcontractor for work, but without derogating from his status in his own right as an employer or a user.

“Principal Contractor”

Is the main Contractor, joint venture partners or consortium who employs or provides work on the Project.

“Project” 	Refers to the contract and has reference to the premises or any part thereof where the work which has been contracted for is to be performed.

# 1.7 	Reference Documents, Standards and Related Procedures Health and Safety

- The Occupational Health and Safety Act (No. 85 of 1993) and Regulations there under

- The Construction Regulations (7 February 2014)

- All other relevant Health and Safety Legislation

- Method statements supplied by consultant or designer

- National Building Regulations

- SANS 10089-2 & 3, SANS 10085, SANS 10108, SANS 10400, SANS 1200, SANS 10142

- JBCC

1.8. 	Costing Health and Safety

It is the responsibility of the Principle Contractor to make sufficient provision for OHS requirements and the following should be taken into consideration:

- Training:

First Aid

Safety Rep

Scaffold Erectors

All Operators

Safety Officer

- Equipment and PPE:

Clothing

Safety Shoes

Gloves

Respiratory masks

Goggles/safety glasses

Road signs

Symbolic Safety Signs

First Aid equipment, kit and box.

Fire extinguishing equipment

Safety Harnesses

- Medical fitness certificates for all employees – Const. Reg. (7 February 2014)

# SECTION B: HEALTH AND SAFETY PROJECT SPECIFIC SPECIFICATIONS

# 1. 	OBJECTIVE

This agreement in entered into by the parties in order to identify and stipulate the arrangements and procedures between the Client and Contractor in order to ensure that the Contractor and their sub-contractors comply with all the H&S requirements along with all applicable legislation on the Project.

1.1 	INSURANCE

1.1.1 	The Contractor and its subcontractors warrant that they have the following insurance cover which shall remain in force whilst on the Project, or which shall remain in force for the duration of the contractual relationship between the Client and Principal Contractor, which ever period in the longest;

a) 	Compensation Registration covering all occupational injuries and diseases and the cover must be paid up for the duration of the Project. Proof of this cover must be provided to the Principal Contractor in the form of a Letter of Good Standing from either the Compensation Commissioner or relevant insurance fund managers.

b) 	Adequate Public Liability insurance cover in relation to the work undertaken.

c) 	Any other insurance cover that will adequately make provision for any losses and/or claims arising from its subcontractors and/or their respective employees and/or omissions whilst on the Project.

1.2 	ADMINISTRATION

1.2.1 	The Contractor shall ensure that it has an updated copy of the applicable legislation on the Project at all times and that this copy is accessible to all employees. The Principal Contractor will also keep an updated copy on the Project for viewing by any Contractor.

1.2.2 The Contractor and its subcontractors shall ensure that a H&S File is implemented and maintained for the duration of the Project. This file must contain all relevant documentation pertaining to H&S related issues such as, appointments, risk assessments, accident procedures, incident investigations, training records, registers, check lists, safety meeting minutes and other H&S related documentation.

1.2.3 	All comments contained in this section require specific measures to be incorporated into the construction Health and Safety Plan. The Principal Contractor may not allow work to commence on site before an adequate construction Health and Safety Plan is developed. The plan must contain the method statements, procedures and scope of works for the project. Further risk assessments and method statements must be carried out where the works may change, due to design changes. The construction phase Health and Safety Plan, developed by the Principal Contractor must also take into account current health and safety legislation and associated codes of practice.

1.2.4 	The Contractor and its subcontractors shall also permit a representative from the Principal Contractor to view and inspect the file from time to time as determined by the Project requirements.

1.3 	SUPERVISION / APPOINTMENTS

1.3.1 	The Contractor and its subcontractors shall ensure that all work performed is done under the supervision of trained and competent persons.

1.3.2 The Contractor and its subcontractor shall appoint a Construction Manager in terms of the applicable legislation. This appointed person will be responsible to ensure that all H&S requirements are implemented and adhered to on the Project.

1.3.3 	Attached to this agreement is a blank copy (-Annexure 3) of a standard Construction Manager appointment form, which must be completed and submitted with this agreement.

1.3.4 The Contractor’s appointed Construction Manager will also be required to attend all scheduled H&S meetings of the Project.

1.3.5 The Contractor and its subcontractors shall further ensure that all other legislative appointments are implemented and maintained for the duration of the Project and that those employees appointed have the necessary training and experience to meet those requirements.

# TRAINING

1.3.6 The Contractor and its subcontractors shall ensure that all its employees are adequately trained and experienced to perform their work. Where semi-skilled employees are employed, adequate supervision must be available to maintain standards of work and to ensure compliance with H&S standards on the Project.

1.3.7 The Contractor and its subcontractors shall ensure that all employees undergo a formal H&S Induction prior to commencing on the Project. Proof of this induction must be submitted along with this agreement.

1.3.8 The Contractor and its subcontractors shall ensure that all its employees are in possession of valid licences and / or certificates of the correct code where machinery or plant is utilised. Proof of these licences and / or certificates will be kept in the Contractors H&S File.

1.4 	ACCIDENT PROCEDURES

1.4.1 The Contractor and its subcontractors shall ensure that a sufficient number of trained first aiders are available on site for the duration of the Project. The number and Level of training will be determined by legislative and Project requirements. A guideline however may be a Level 1trained first aider at all times on site during construction work.

1.4.2 The Contractor and its subcontractors shall ensure that suitable first aid facilities are provided for the work to be performed. The number of first aid facilities and type of equipment will also be determined by the legislative and Project requirements.

1.4.3 Should the Contractor or it subcontractors utilize the Principal Contractors first aid facilities then this needs to be agreed upon in writing. Cost of first aid equipment will then be charged to the Contractor at the discretion of the Principal Contractor.

1.4.4 The Contractor and its subcontractors shall ensure that a suitable Accident Procedure is drawn up for the duration of the Project. This Accident Procedure must be submitted to the Principal Contractor and must contain the names of all emergency contact persons and contact numbers.

1.4.5 The Contractor will be responsible to inform the (relevant authorities i.e. Department of Labour,etc) of any Serious or Reportable Incidents which may occur in terms of the applicable legislation. All correspondence to the (Relevant Authorities) regarding these incidents must be copied and submitted to the Principal Contractor.

1.4.6 The Contractor shall ensure that a monthly report is submitted to the Principal Contractor and shall contain the following:

a) 	Man-hours worked for the relevant month (including subcontractors)

b) 	No of work-related injuries for the relevant month.

1.5 	HEALTH & SAFETY REPRESENTATIVES

1.5.1 The Contractor and its subcontractors shall ensure that an adequate number of health and safety representatives are appointed and trained, as per the requirements of the applicable legislation and / or Project H&S requirements. As a guideline one Health and Safety Representative should be appointed for every 20 employees.

1.5.2 The Contractor and its subcontractors shall ensure that regular internal H&S meetings are conducted and attended by the appointed Health & Safety Representative. The frequency of these meetings must be determined by the work activities performed along with the duration of the Project, however at least once a month.

1.5.3 The Contractor and its subcontractors shall keep record of these meetings in the H&S File along with the attendance records.

1.5.4 The Contractor Supervisor or his Health and Safety Representative will attend the main Project H&S meetings.

1.6 	MEDICAL FITNESS CERTIFICATES

1.6.1 The Contractor must ensure that all his or her employees have valid medical certificates of fitness specific to the construction work to be performed and issued by an occupational health practitioner.

1.7  	MACHINERY

1.7.1 	The Contractor and its subcontractors shall ensure that all the plant, machinery and equipment they wish to utilize on the Project is of sound order and fit for the purpose for which it is intended and that it complies with all applicable legislative requirements.

    - The Contractor and its subcontractor shall ensure that all plant, machinery or equipment is suitably guarded by means of insulation, fence, screening, or guarding. Further to this, all safety equipment in relation to plant, machinery or equipment is in a suitable and working condition.

1.7.3 	The Contractor and its subcontractor shall ensure that all employees operating or utilising such plant, machinery or equipment are suitably trained, experienced and are aware of the dangers involved.

1.7.4 	The Contractor and it subcontractors shall not permit uncertified employees from working on moving or electrically alive machinery. Isolation Procedures shall be adhered to by all.

1.7.5 	Devices to start and stop machinery must be clearly labelled and in working order on al plant, machinery and equipment. Warning signs of relevant dangers must also be clearly visible.

1.8  	HOUSEKEEPING / CLEANLINESS

1.8.1 The Contractor and its subcontractor shall ensure that the area where the work is performed is at all times maintained to reasonably practicable levels of cleanliness. Further to this the following must be addressed:

a) 	adequate care is taken to ensure correct storage and stacking of articles and material,

b) 	regular refuge removal is maintained,

c) 	the working area around machinery is clean and demarcated.

d) 	no articles or material are disposed from any height without the necessary precautions taken.

1.8.2 	The Principal Contractor reserves the right to clean up after any Contractor who fails to adhere to these housekeeping requirements and to charge the Contractor accordingly.

1.9 	GENERAL H&S REQUIREMENTS

The Contractor and its subcontractors shall ensure that:

1.9.1 	All employees are issued with the appropriate PPE and that they are trained in the correct use thereof.

1.9.2 	Employees are medically certified to work on height and to operate Plant and Machinery.

1.9.3 	All security measures implemented on the Project are adhered to and that random searching may be carried out.

1.9.4 	All signs and notices implemented on the Project are adhered to and not damaged in any way.

1.9.5 	Suitable firefighting equipment is made available and employees are trained in the safe use thereof.

1.9.6 	No large volumes of flammable substances are stored and suitable precautions are taken to store those that are.

1.9.7 	Suitable measures are in place with regards to sanitation, changing facilities, eating facilities, and drinking water.

1.9.8 	Measures are taken to reduce any environmental impairment with regards to noise, ground, air and water pollution.

1.9.9 	Suitable lighting is provided in all darkened working areas.

1.9.10 	No employees are permitted to enter / work on the Project while under the influence of any intoxicating substances.

1.9.11 	No machinery, article, substance, plant or PPE belonging to the Principal Contractor is used without permission.

1.9.12 	No illegal immigrants are employed by the Contractor or subcontractor while on the Project.

Without derogating from the generality of the above requirements and notwithstanding the applicable legislation the Contractor and its subcontractors shall ensure the following:

a) 	The provision of a safe and healthy working environment,

b) 	The provision of safe and healthy systems of work, plant and machinery,

c) 	The identification of the prevalent hazards to health and safety and the precautionary measures to be taken,

d) 	The provision of the necessary information, instructions and training,

e) 	The enforcement of the established precautionary measures,

f) 	Informing employees on their scope of authority,

g) 	Informing employees on their scope of authority,

h) 	Making employees conversant with the identified hazards and precautionary measures,

i) 	Ensuring that no employee is victimized as a result of adhering to these requirements.

The Client reserves the right to request immediate correction of any non-compliance identified in terms of this agreement by any Contractor and its subcontractors during the performance of the work on the Project. The Client further reserves the right to stop any work that does not comply with the H&S standards and without the cost to the Client. This agreement places the onus on the Principal Contractor to contact the Client/Agent in the event of the inability to perform as per this agreement.

1.10.  		ADDITIONAL REQUIREMENTS

Compliance to the Occupational Health and Safety Act 85 of 1993 or other applicable Legislative Requirements, is a legal requirement and all Contractors and subcontractors are required to adhere with the Legislation and its regulations to avoid prosecution by the Authorities. Over and above the Legal requirements, Contractors will be required to comply with the specific requirements of this document and client H&S requirements.

Contractors will provide to the Principal Contractor, before work commences, a written Health, Safety and Environmental Plan, which is to be approved by the Principal Contractor. The Contractor shall ensure the implementation and adherence to the Health, Safety and Environmental Plan by its Employees and subcontractors.

The Principal Contractor will ensure that all subcontractors employed on the Project maintain H&S files and submit such documentation to the Contractor on completion of their contract. Subcontractor H&S files will be handed over to the Principal Contractor by the Contractor on the completion of the contract work performed by the Contractor.

The Client/Agent reserves the right to stop any Contractor or his subcontractor from performing his activities if the Contractor or his subcontractors is found not adhering to the specified H&S Plan, contravening any Legal requirements, or not adhering to the Clients H&S Specifications for Contractors, or if the Contractor or his subcontractor is found performing his work activities unsafely.

1.10.1 	Requirements

Contractors are responsible to comply with the Legislation and Contractual Requirements of the Principal Contractor and Client. However various systems will be implemented to ensure compliance by all Contractors on the Project. Contractors will be included in al H&S meetings and will receive copies of all H&S related documentation pertaining to their operations. Routine inspections and monthly audits will include Contractor operations. Formal action will be taken against Contractors failing to comply with the Project H&S requirements. The formal action could lead to financial implications and / or permanent removal from the Project.

1.10.2 	Mandatory Agreement / Contractor Specification – Section 37(2)- Annexure 4

This document is deemed to be accepted once it has been issued unless written response is received within 5 (five) working days of issue. Contractors are required to sign this Contractor Safety Specification, which includes the Mandatory Agreement (OHS Act 85 of 1993 – Section 37(2)

Agreement) with the Principal Contractor. This Agreement covers various aspects such as Insurance, Administration, Supervision, Training, Accident procedures, H&S Representatives, First Aid, Housekeeping and General H&S requirements. Contractors will not be allowed to commence work, unless both Parties have signed this Agreement and all required documentation is on site.

- Annexure 5

1.10.3. 	Contractor Supervisor Appointment & Functions

Attached to this Mandatory Agreement is a blank Construction Manager (– CR8(1)] Appointment Form. The Contractor shall appoint a trained and competent person in writing to oversee their respective operations. As with this Mandatory Agreement no work will commence until the Appointment form is received and the appointed person is qualified to be the Construction Manager for the Contractor on the Project.

1.11 		GENERAL ADMINISTRATION

# 1.11.1 	Letter of Good Standing – Compensation Commissioner (COID Act 130 of 1993).

The Contractor will supply an updated copy of their Letter of good Standing with either WCA or FEMA to the Client before work commences on the Project. Therefore, all employees who may be injured or suffer any disease associated with the work activities, will be covered in terms of the COID Act 130 of 1993.

# 1.11.2 	Notification of Construction Work

As standard procedure, formal written Notification of all new Projects in the Republic of South Africa are submitted to the Department of Labour. Copies of the notification are kept on the Project H&S file. Additional copies are available on request. The Principal Contractor will do this notification.

# 1.11.3 	Monthly Project Man-hour & Injury Report

The Contractor is required to submit a formal Monthly Report of the Hours worked and Injuries sustained to the Clients Agent.

# 1.11.4 	Safety File

The Contractor will have and maintain a H&S file where all Administrative requirements will be kept. At the end of the Contractor’s contract the Contractor will hand over his completed H&S file to the Principal Contractor who will submit all documentation to the client.

# The Construction Health and Safety Plan should include details of the following:

- The positioning of the site access and egress points to ensure that any nuisance or risk to the occupants of the building and adjacent properties is minimised and controlled. This should be away from the adjacent occupied and sensitive premises.

- The location of temporary site accommodation to ensure that adjacent sensitive properties are not subjected to any nuisance arising from the use of the facilities.

- The location of unloading, layout and storage areas to reduce and minimise excessive manual handling of construction materials, damage to building and adjacent property and the security of the plant, equipment and materials.

- Requirements to maintain access for emergency service vehicles during works are necessary as well as the temporary relocation of existing firefighting equipment.

- The planning of traffic and pedestrian routes to ensure adequate protection for members of the public and site employees and operations.

- The use of suitable barriers, signs and the appointment of a flag person should be adopted to provide the required level of protection.

- The arrangements for the reception of prospective visitors.

- The site emergency plan should be taken into consideration when developing the Principle Contractor’s own emergency plan.

The following should be contained in the Contractors H&S File:

- Copy of the Occupational Health and Safety Act (85 of 1993)

- Updated Letter of Good Standing with WCA or FEM - Const. Reg. 7(1)(c)(iv)

- Clients Safety Specification

- Risk Assessments

- Fall Protection Plan

- Environmental Management Plan

- All Policy’s

- All notices issued by DoL.

# Records specific to the Project:

- Risk Assessments - Const Reg. 9

- Fall Protection plan - Const Reg. 10

- Mandatory Agreement - Sect. 37

- Safety Inductions of Employees - Const Reg. 7(7)

- Incident Recording & Investigation - GAR 9(1)

- Incident Reports - GAR 8(1)

- Health and Safety Rep. Inspections - Sect. 18

- Issue of PPE - GSR 2

- Safety Meeting Minutes - Sect. 19

- Letter of Good Standing from FEM or WCA - Const. Reg. 7(1)(c)(iv)

- Safety Toolbox Talks - Sect. 8, Const Reg.9(3)

- First Aid Box Contents - GSR 3(3)(a)

- First Aid Treatments - GSR 3(1)

- Training certificates of employees and Medical fitness certificates for employees working at heights.

- Training certificates and Operator Medical certificates for Operators of Plant, Machinery and Vehicles

- Medical fitness certificates issued by an Occupational Health Practitioner- Const. Reg. 7(8)

- Registers (as per list under section for Registers)

# Appointments

- Appointment of Manager - Sect 16(2)

- Construction Manager - Const Reg. 8(1)

- Assistant Construction Manager - Const Reg. 8(2)

- Risk Assessor - Const Reg. 9(1)

- Fall Protection Supervisor / Planner - Const Reg. 10(1)(a)

- First Aider - GSR 3(4)

- Incident Investigator - GAR 9(2)

- Health and Safety Representative - Sect. 17(1)

- Electrical Machinery Operator/Inspector - Const Reg. 24(e)

- Scaffold Supervisor - Const Reg. 16(1)

- Formwork Supervisor - Const Reg. 10(a)

- Fire Equipment Inspector - Const Reg. 27(h)

- Construction Vehicle Operator / Inspector - Const. Reg. 23(1)(d),(k)

- Stacking Supervisor - Const. Reg. 28(a)

- Lifting Tackle Inspector - DMR 18

- Material Hoist Inspector - Const Reg. 19(8)

- Lifting Machine Inspector - DMR 18

- Demolition Supervisor - Const Reg. 14(1)

# 1.11.5 Registers & Checklists.

In order to ensure that all plant, equipment, systems and procedures are maintained in accordance to Legislative requirements, formal inspection Registers and Checklists have to be compiled. These Registers and Checklists are then complete by the appointed persons, who are designated in writing.

The completed forms are kept on the Contractors H&S file and then archived after Project completion.

The following is a list of Registers and Checklists required to be completed for the applicable activities and at intervals as per the requirements of the Occupational Health and Safety Act 85 of 1993:

- Portable Electrical Equipment

- Hand Tools

- Construction Vehicle

- Scaffolding

- Form & Support work.

- Fire Extinguishers

- Construction Vehicles and Mobile Plant Equipment

- Explosive Power Tools

- Hazardous Chemical Substances

- Cranes

- Slings, Chains & Hooks (Lifting Tackle)

- Compressors

- Ladders

- Hoists

- Gas Welding / Flame Cutting

- Safety Belt / Safety Harnesses

- Distribution Boards

- First Aid Boxes

- Contact details with certified ID copies of all workers on site

- List of all subcontractors on site with contact details CEO and Construction Manager on site.

1.12 	SAFETY INDUCTION AND IDENTIFICATION

1.12.1 	The Contractor will ensure that all his employees and visitors will first go to the Principal Contractors Project Safety Officer or Site Agent for a Site Safety Induction or will explain and  have the General H&S Induction form signed by all employees / Visitors, before the persons will be allowed onto the Construction Site. The Contractor will keep a copy of all the signed General H&S Induction forms on his H&S file and will issue the Principal Contractor with copies of all signed forms within 24 hours of new employees or visitors arriving on site. Failure to comply will result in a fine imposed onto the Contractor.

1.12.2 	The Contractor will first take new employees to the Principal Contractor Project Safety Officer or Site 	Agent for a Site Safety Induction or will explain and have the form signed by the new employee, before 	the employee will be allowed to start work.

1.12.3 	The Contractor will ensure that his employees are issued with some sort of identification i.e. Contractor name on Overalls, Hardhats or ID cards will be acceptable

1.13 	RISK ASSESSMENTS AND SAFETY TALKS (TOOLBOX TALKS)

1.13.1.	Base line Risk Assessment compiled by Client Agent attached. Contractor must compile and document the necessary Work Procedures and Method Statements that would control the activities to a degree that would be compliant with legislation and the requirements of this specification.

1.13.2 	The Contractor must perform Risk Assessments of hazards and risks associated with the scope of work relevant to the Contractors appointment, shall be assessed, safe methods of work identified; safe working conditions and a healthy work environment will be provided.

The following risk assessments by the Principle Contractor are to be considered:

- All task oriented risks – particularly working from height, services    decommissioning and/or modification, etc.

- Equipment risks

- Physical risks

- Chemical risks

- Ergonomic risks

The following method statements and/or procedures must be available before work starts on site:

- Establishment of site welfare, first aid and emergency procedures (fire and security, etc).

- Welfare facilities to take into account demolition and/or contaminated soil removal if required.

- Noise and dust control during construction process.

- Arrangements for emergency fire, security and first aid facilities.

- Arrangements for emergency service vehicles access to the premises.

- Traffic management arrangements to protect site staff, public and road traffic from construction works and when loading and offloading of materials and equipment.

- Protection to overhead and underground services.

- Arrangements for dealing with emergency situations, particularly during demolition, deep excavations, overhead and underground services.

- Public protection arrangements.

- Method statement for demolition of structures including fall protection and/or asbestos handling plans.

- Contaminated waste materials handling (health and environmental issues) and records of waste removal.

- Selection and maintenance of plant and equipment.

- Selection of competent contractors.

Following a high-level risk assessment done in terms of risks posed by construction activities 	to the Client, customers or staff, and 3rd party assets, members of the public and 	the 	environment, the recommendations therein need to be included in the Principle 	Contractor’s Health and Safety Plan as follows:

- Proper hoarding of demolition and construction area (sound construction, height & safety distance from works)

- Danger tape around all excavations

- Visible signage (e.g.” No unauthorised entry”, “Warning construction in progress”) and access control for demolition and construction area.

- All construction vehicles and plant to be properly maintained with daily inspections/checks done

- Safe routes established for pedestrian and vehicular traffic

- Use of competent contractors with competent supervisors

- No night work by contractors

- All employees to wear reflective vests when working close to public roads or where plant and vehicle movement take place

- Hard hat area declared with visible signage

- Structures adequately supported during demolition and construction

- Induction training of all contractors and visitors

- Lifting equipment to be of suitable design to carry load and offloading operations supervised

- All scaffolding erected as per SANS 10085

- Emergency response measures to be adapted to accommodate construction works

- Certificate of safe installation issued by electrical contractor before demolition and after commissioning

- Traffic control for construction area. Person controlling traffic or working close to traffic to wear hi-visibility jacket/vest

- Underground services to be identified within area of excavation works and necessary precautions established prior to commencement of works

- Hand excavation done in the event that underground services cannot be determined

- Permit to work system to be used with supervision by safety officer, when required

- Contaminated soil stockpiled on prepared surface as per Environmental Management Plan

- Segregation and disposal of contaminated soil to be done under controlled conditions as per Environmental Management Plan

- Asbestos removed and disposed of by an accredited contractor

- Machinery maintained as per OHS Act and manufacturer's spec

- All machinery and vehicles to be isolated at the end of each day and located within the hoarding if not removed from site

1.13.3 	All Risk assessments shall be communicated to the employees of the Contractor by the Contractor before work starts.

1.13.4 	When activities change the Contractor will be required to revise the risk assessment to suit the changed conditions and re communicate the revised risk assessment with the employees;

1.13.5 	Copies of all risk assessments will be issued to the Principal Contractors Project Safety Officer or Site Agent for review and these will include copies where the Contractor’s employees have signed confirmation of receiving the risk assessment information.

1.13.6 	The Contractor is required to have a Weekly Safety Talk (Toolbox Talk) with his employees to inform them of safety issues related to their scope of work. The employees of the Contractor will sign acknowledgement of receiving the training an copies of the documents shall be kept on the Contractor H&S File and copies will be issued to the Principal Contractor Project Safety Officer or Site Agent.

1.13.7 	Risk Assessor Appointment & Functions. The risk assessment process will be co-ordinated by a Contractor Appointed Risk Assessor. This person will oversee all risk assessments. Further to the above, the Contractor will ensure that all Appointed Contractor Supervisors convey the information on the risk assessment to the respective work crews and the contractor employees sign an Attendance Register.

1.14 	APPOINTMENTS – SUPERVISORY

1.14.1 	All legal and client requirements regarding appointments will be adhered to on the Project. In all cases the person being appointed will have the necessary training and / or experience for the appointed position.

1.14.2 	The Contractor will have an H&S Appointment Structure in place. The CEO will delegate certain responsibilities down to appointed employees; however, he will remain ultimately responsible.

1.14.3 	Delegation of Duties – Section 16(2). The Contractor CEO will appoint his Managing Director and Contracts Director who will oversee that all legal, client and company H&S requirements are implemented, adhered to, and enforced.

1.14.4 	Construction Work Manager CR8 (1). The Contractor will appoint a Construction Manager for the contract to supervise the construction process and thus ensuring that all legal, client and company H&S requirements are implemented, adhered to, and enforced. The appointed person will have the authority to appoint all other persons as may be required on the Project.

1.14.5 	Assistant Construction Managers CR8 (2). Assistant Construction Managers may be appointed to assist the Construction Manager. Although their duties will be the same as the Construction Work Supervisor, the Construction Manager will remain accountable for any supervisory duty which the Assistants fails to conduct.

1.15 	PROJECT H&S OFFICER

1.15.1 	Requirements CR8 (5). Contractors shall co-operate with such an appointed Principal Contractor Project Safety Officer and will adhere to his / her requests and recommendations.

1.15.2 	Appointment & Functions. The function of the Project Safety Officer is to assist advice and enforce all H&S issues related to the Project. The duties of the Project Safety Officer will include but will not be limited to stop any Contractor who in his / her opinion works unsafely or poses a threat to any other person.

1.15.3	 Monthly Inspection Report. The appointed Principal Contractor Project Safety Officer will be required to formally inspect the Project on a monthly basis and all findings will be recorded and distributed to the all appointed supervisors, client and or client agents, contracting companies and relevant Divisional H&S Departments. The Principal Contractor Safety Officer will also be required to do monthly audits on the Contractor Safety files and H&S Plans.

1.16 	H&S REPRESENTATIVES & COMMITTEE MEMBERS

1.16.1 	OHS Act 85 of 1993 – Sect 17 & 19. As per the legal requirements, the Contractor will appoint H&S Representatives & H&S Committee Members on the Project. These persons will be nominated by the Contractor workforce and will thus represent the workforce in all H&S related issues. A minimum of one H&S Representative will be appointed for every 20 employees. All H&S Representatives will be members of the Project H&S Committee and will meet on a monthly basis with the Project management to discuss H&S related issues.

1.16.2 	Appointments & Functions. The appointed H&S Representatives and Committee Members shall be formally trained in their functions and responsibilities. These will also be clearly defined on their appointment forms.

1.16.3 	Monthly Inspection Report. Each H&S Representative is required to complete a formal inspection report for their respective work areas. These reports are then tabled at the monthly safety meetings for review, however should the need arise a H&S Representative may at any time complete an inspection report and forward it directly onto the appointed Construction Manager. These monthly reports are kept in the Contractor Safety File and then archived after the completion of the Project.

1.17 	H&S MEETINGS

1.17.1 	Monthly H&S meetings with all H&S Representatives and other committee members will be conducted for the contract. Depending on the scope of work, monthly H&S Contractor meetings will also be conducted to discuss H&S related matters.

1.17.2 The Project H&S meetings are formalised with a standard agenda; however, each Project may adapt the standard agenda to meet either client requirements or joint venture requirements.

Minutes must be kept for each meeting and distributed to each member. As will all H&S documentation these are filed on the Principal Contractor Safety files for viewing by either client or officials from the Department of Labour.

1.17.3 	All persons attending H&S meetings are required to sign a standard attendance register as proof of attendance.

1.17.4 	Contractor Supervisor Meetings. It might be required by the Client/ Agent to have a safety meeting with the supervisors of the Contractors when the need arises or if the Client/Agent sees fit to have meetings.

1.18 	ACCIDENT PROCEDURES

1.18.1 	Standard Accident Procedure. Fully equipped first aid boxes along with applicable signage must be placed in prominent areas on the Project. All accident investigations will be conducted by either the Project Contractor Safety Officer, appointed investigator or appointed Contractor H&S Representative.

1.18.2 	First Aider Appointment & Functions. The Contractor will appoint a trained Level 1 First Aider. A minimum of one trained First Aider with his First Aid Box must be available for every 50 employees. Each trained First Aider must be appointed in writing and responsibilities should be in writing on the appointment form.

1.18.3 	Name List of First Aiders. To promote the awareness of the trained First Aiders, their names and work areas shall be displayed in all prominent areas.

1.18.4 	Emergency Evacuation Procedure. A Standard Emergency Evacuation Procedure must be developed by the Contractor in accordance with the Emergency Evacuation Procedure of the Principal Contractor. A Client’s specific Evacuation Procedure will take preference over the standard evacuation procedure. Details of the Emergency Evacuation Procedure will be displayed in all prominent work areas.

1.18.5 	To promote the awareness of the emergency numbers the lists will also be displayed in all prominent areas.

1.18.6 	Employees Report of Accident Forms. In the unfortunate case of a person being injured and requiring medical attention the standard “Employers Report of Accident” form will be completed accordingly. Sufficient blank copies will be kept at the Contractors offices. As per the accident procedures copies will be sent to the medical practitioner and relevant company Head Office. A copy will also be kept on the Contractor Safety file

.

1.18.7 	Investigation Form (Annexure 1). Each incident involving medical attention from either a doctor or hospital will be fully investigated on an Annexure 1 form. This form entails input from all parties namely the investigator, H&S Committee and Project management. Each investigation will be reviewed at the monthly H&S meeting. Once actioned the Annexure 1 form will be kept on the Contractor H&S file. If required the client will be notified immediately and a copy handed over.

1.18.8 	Serious & Reportable Incidents. The Contractor will immediately inform the Client/Agent and the Principal Contractor of any serious or fatal accidents which occur. In the case of Fatality, the Contractor will also inform the Authorities (Department of Labour and SAPS) for their investigation.

2.  	CONSTRUCTION ACTIVITIES

# 2. 1 	Portable Electric Tools

No Contractor will allow any employee to work with unsafe or damaged portable electric tools. All tools will be inspected before it is issued to employees. Any Contractor who does not conform to this requirement will be fined and the tool confiscated until it is made safe to use by the Contractor. All rotating parts will be sufficiently guarded to protect employees. Tools may only be used by competent / trained persons.

# 2. 2 	Scaffolding

No Contractor will allow any employee to work on unsafe or damaged scaffolding. Scaffolding will be inspected daily and after inclement weather by a competent appointed person.

No work will be allowed on scaffolds during inclement weather conditions. Scaffolds will be fitted with a sign at the access to the Scaffold to indicate if it is safe or unsafe to use. Scaffolds will be constructed to SANS 10085 standards and OHS Act 85 of 1993 regulations.

# 2. 3 	Ladders

No Contractor will allow any employee to work on unsafe or damaged ladders. No person will be allowed to stand and work on the last 2 rungs of any ladder. When the ladder is longer than 3 m then another person will hold the ladder in place at the bottom and the ladder will also be tied to a solid structure at the top where possible. Ladders will be inspected visually before shifts starts and monthly on a register.

# 2. 4 	PPE (Personal Protective Equipment)

Compulsory PPE is Hardhats, Safety boots and overalls. Any other PPE required will be determined by the Risk Assessment. PPE will be issued to employees free of charge and a signed register will be kept by the Contractor to prove that PPE has been issued to the employee. Only full body harnesses will be allowed to be used by employees who are working on any unprotected heights. These harnesses must carry the SABS stamp of approval. PPE will comply with relevant SABS and OHS Act 85 of 1993 regulations.

# 2. 5 	Fall Protection Plan

A detailed fall protection plan will be submitted by the Contractor to the Client for approval. A competent person will be appointed in writing to control and oversee all work being conducted by the Contractor.

All employees working on heights will be required to undergo a Medical Fitness test with an Occupational Health Practitioner, every 12 months as per the OHS Act 85 of 1993, Construction Regulations. Contractors working on heights will take precautions to prevent tool and equipment from accidentally falling from heights onto persons below. Where it can be prevented no person will work above other employees unless there is sufficient guarding protecting the employees below.

# 2. 6 	Housekeeping

Housekeeping of the Contractors work area will be the responsibility of the Contractor. Housekeeping will be done throughout the day to prevent any material or tool obstructing the walkways of the employees.

Cleaning of the work area will be done throughout the day and a final clean-up near the end of the shift. If the contractor does not comply with the daily cleaning of this area, the Clients Agent reserves the right to hire a cleaning team and to charge the Contractor for the cost of the cleaning team.

# 2. 8 	Stacking and Storage

Lay down areas will be kept neat and tidy. Areas will be barricaded and all equipment, material or tools will be stored neatly inside this area. Stacking of equipment or material will be one on level solid surfaces.

Overhanging of material will not be allowed.

Flammable liquids will be stored in a well ventilated store room with a Fire extinguisher placed on the outside of the store. Gas cylinders will be secured in a trolley while work is being done on the site and will remain upright at all times. Gas cylinders will be stored upright inside a well ventilated area, empty and full cylinders will be stored apart from one another. The Torch, pipes and regulators will be stored detached from the cylinders and will be kept in a storage box.

# 2. 9 	Operators of Machinery

Operators of machinery will be required to complete a daily pre-start checklist before work commences.

Operators must be in possession of a valid Medical Certificate issued by an Occupational Health Practitioner and the operator will be in possession of a Competency Certificate for the machine he / she operates. Drivers of trucks or any other Vehicle or Plant travelling on Public Roads must also be in possession of a valid PDP licence. It will remain the responsibility of the Operator of a Vehicle / Plant /Machine to report all oil leaks to the supervisor and to have the Vehicle / Plant / Machine fixed as soon as possible. Where there are Life Threatening Faults the Vehicle / Plant / Machine will not be used until it has been sufficiently repaired.

# 2. 10 	Cranes and Lifting equipment

Cranes and Lifting equipment will comply with OHS Act 85 of 1993, Driven Machinery Regulations (DMR)18. Operators of mobile cranes must be in the possession of a valid PDP licence, medical certificate and training certificate. Mobile cranes must have a valid load test certificate and must be inspected monthly by a competent person on register. All lifting equipment / tackle must have a valid load test certificate and will be inspected monthly by a competent person on register. At no stage will gas cylinders be lifted by a crane unless the cylinders are in a cradle designed to carry equipment. Cranes will be directed by a Banks man / Supervisor with sufficient communication with the crane. It will remain the responsibility of the operator to ensure that the loads are not slewed over other employees and that the mobile crane slew is barricaded with tape while the crane is in operation. Where there is a Life-Threatening Fault, the Crane Operations will not start until the faults have been sufficiently repaired and the Crane was issued with a certificate to prove the crane has been fixed and where applicable, a new load test was conducted.

# 2. 11 	Flame cutting and welding

Gas cylinders will be in a trolley while work is being done on site and will remain upright at all times. Gas cylinders will be stored upright inside a well-ventilated area, empty and full cylinders will be stored apart from another. The Torch, pipes and regulators will be stored detached from the cylinders and will be kept in a storage box. Electric welders will have insulated electrical cables, electrodes and an effective earth system. Areas where welding is taking place must be barricaded with welding screens and sufficient warning signs have to be erected to protect other employees from the glare and sparks. Operator will be trained and experienced in welding. A Fire extinguisher will be in the area of work where any spark producing activity takes place. Contractors who fail to comply with legal regulations and the stipulations of this document will face legal action which can be instituted by the Principal Contractor or the Client.

# 2. 12 	Eating facilities and storage

Every Contractor will be required to have a sheltered eating facility with storage space for food.

# 2. 13 	Edge Protection

The Principal Contractor must ensure that all exposed edges and openings are guarded and demarcated at all times until permanent protection has been erected. The Principal Contractor’s risk assessment must include these items: protection of decking edges, finished floor slab or platform edges, stairways, floor penetrations, roof work and all other openings and areas where a person may fall. No exposed edges and other openings will be tolerated.

# 2. 14 	Demolition Work

Demolition work will be done under supervision of a competent person. No floor or part thereof will be overloaded with debris or material in such way to make it unsafe. Adequate shoring or extra support will be used to prevent any accidental collapse of the structure being demolished. Safe means of access shall be provided by the Contractor. All waste and debris will be removed from site as soon as possible. The demolition area shall be well barricaded with relevant warning sings displayed on the barricading to prevent any unauthorised person to enter the demolition area. Dust will be minimized to an acceptable standard. When working with Compressors and Jack Hammers, the Contractor will ensure that all couplings are safeguarded with safety chains to the couplings. All service lines will be detected before the work starts and all service lines will be secured by competent persons before work commences.

# 2. 15 	Form- & Support Work

Work will be done under supervision of a competent supervisor who has been appointed in writing.

Before work commences drawings will be issued to the Principal Contractor. Decks will be erected in a systematic way and will at no time endanger any persons working on the deck. Handrails will be placed around the edges of the temporary or permanent decks. Safe access will be provided and fall protection will be used as per the Contractor’s Risk assessment / Fall protection plan. No material will be thrown from any height.

# 2.16 	Steel Assembling & Placing

Area where assembly takes place must be demarcated. When working at heights employees must be issued with safety harnesses and other PPE required as per the risk assessment. The correct tools must be used for the work to be done. When handling steel, beware of the cutting edges of steel and be aware of other people. When lifting steel with a crane the load must be well balanced.

# 2.1.17 	Explosive actuated fastening devices and powered tools.

All operators will be trained by a competent company and will be appointed in writing. The operator will receive a training certificate which has to be forwarded to the Client/Agent. The “Gun” and the Cartridges will be stored in a lockable storage facility and will be stored separately.

# 2. 18 	OHS Act 85 of 1993

This document does not replace any regulations or any part of the OHS (Occupational Health and Safety Act) Act 85 of 1993, but does conform to the requirements of the OHS Act 85 of 1993 Construction Regulations. The Client shall provide a Health and Safety Specification to the Principal Contractor and the Principal Contractor will issue such information to the employed Contractors on the construction Project. As an Employer, the Contractor remains responsible to ensure compliance with the OHS Act 85 of 1993 and is regulations.

# 2. 19 	Non-Conformances

Any Contractor employee who is found not adhering to the Client H&S procedures, Contractor H&S Plan or OHS Act 85 of 1993 or who is observed doing unsafe acts or contributing to creating unsafe conditions will be issued with Site Instruction. Contractor employees will also be reprimanded as per the Company HR procedures, a first transgression constitutes a verbal warning, a second transgression constitutes a written warning and a third transgression constitutes a full disciplinary hearing as per the Company Hr Procedures. Any Life-threatening unsafe act or condition must be treated as Gross Neglect of Company Safe Rules and Procedures and a Disciplinary Hearing shall be conducted to determine the root cause of the incident and the appropriate action which must be taken to rectify the unsafe situation or prevent future incidents from occurring. Copies of the Non-Conformance Report and disciplinary procedures must be kept on record.

Copies of all Non-Conformance Reports must be kept in the Project H&S File for references.

# 3. 	Organisational Arrangements

3.1. 	Site Rules

The Principal Contractor’s organisational arrangements for health and safety on the project must include that of other contractors and sub-contractors involved. Site rules must be developed by the Principal Contractor to ensure that the restrictions, outlined in this Health and Safety Specification, are met.

In particular, arrangements and site rules must be developed to ensure that construction works do no put at risk the health and safety of any person.

The Principal Contractor must demonstrate a management structure for ensuring health and safety cooperation and coordination between all parties to the contract. This will include the development of a communications strategy between the appointed Principal Contractor, Contractors, Client, Health and Safety Agent, Design Team and consulting Project Manager. The Principal Contractor must ensure that an effective chain of communication exists, clearly showing that all levels of employees engaged on the contract participate in the communication process for health and safety concerns. Regular meetings will be established between the parties where health and safety performance will be discussed. Minutes must be kept and distributed for action following the conclusion of each meeting. Emergency and incident procedures must be developed and clearly co-ordinated between parties involved.

A security strategy must be developed by the Principal Contractor who must then communicate and coordinate the strategy to all parties to the contract.

3.2. 	Continuing Liaison

Procedures for liaison to continue between all parties throughout the project should include the particular points listed below. All unforeseen eventualities which may occur during construction and which affect previously recognized health and safety issues or resources should be reported to the Clients Health and Safety Agent and consulting Project Manager. The Principle Contactor’s appointed Construction Manager, Health and Safety Representative and/or Construction Safety Officer will consult with the workforce on health, safety and environmental matters through committee meetings, site meetings, contractor meetings, toolbox talks or verbally if so required. The Client or Designer will inform the Principle Contractor and Health and Safety Agent of all new designs, which may affect health and safety.

Information which will be relevant for inclusion in the health and safety file, should be collated, and should include information from Contractors. Arrangements should be made by the Principal Contractor with other contractors to ensure any information required for the health and safety file, which is generated by the contractors’ work, is stored and passed to the Principle Contractor prior to completion of the project.

The basic information, which will be relevant for inclusion in the health and safety file, should be passed to the Client. This should include but is not limited to the following:

- General details of the materials used in the construction process

- Details of the plan and equipment supplied and fitted

- Service details – gas, water, electricity, communications (telephone, cable, TV, etc)

- Specific maintenance details or requirements (plant, equipment, fixtures and fittings – where applicable)

- Suppliers’ brochures for health and safety information (use, maintenance and repairs)

- All Agreements, Safety Committee minutes and nominated competent individuals, etc.

- All training records – i.e. special training needs, induction and visitor inductions.

- Construction Health and Safety Plan

- All inspections and audits conducted

- Medical fitness certificates for all workers issued by an Occupational Health Practitioner

3.3. 	Responsibilities

# 3.3.1. 	The Client

The Client will ensure adequate information is available to all parties, to ensure they can perform their duties under the requirements of this document and relevant statutory legislation. The Client will appoint a competent Design Team, Project Manager, and after tender submittance, a competent Principal Contractor. The Client may also appoint a Health and Safety Agent who will carry the responsibilities of the said client. The Client may amend, vary or terminate these appointments as appropriate.

    - Design Team

The Design Team will be represented by consultant contact person, who will also be appointed Project Manager on this project. The Design Team is responsible for ensuring that the design is, as far as is reasonably possible, risk-free to persons constructing, maintaining or removing the structure. They are also responsible to make available all relevant risk information about the design and loading of structures, including suspended platforms, anticipated hazards or dangers and all method and sequencing of processes (with special conditions), to the Principle Contractor. The designer must also conduct a final inspection and issue a certificate.

# 3.3.3. 	Client’s H&S Agent

The Client may appoint a Health and Safety Agent for the Project who will, on behalf of the Client, be responsible for implementing the Client’s requirements for health and safety on the project. The Health and Safety Agent is also responsible for co-coordinating the Design Team, with reference to the design risk assessment process.

# 3.3.4. 	Principal Contractor

The Principle Contractor will develop and deliver the construction phase Health and Safety Plan and will further develop the plan prior to any construction work being undertaken and during the construction phase itself. The detailed Health and Safety Plan will set out clearly the Principal Contractor’s management systems for managing health and safety on the contract in accordance with the Client’s health and safety requirements set out in this document, the designer’s risk information and any relevant health and safety legislation.

The Health and Safety Plan will be kept up to date by the Principal Contractor to include other contractors’ and sub-contractors’ risk control management information. The Principal Contractor will co-operate with the Client, Health and Safety Agent or Project Manager in all aspects of complying with the duties laid upon them by the OHS Act, its Regulations and specifically the Construction Regulations (7 February 2014).

Generally, the Health and Safety Policy and construction Health and Safety Plan will be to specify site rules such as the wearing of personal protective equipment and no alcohol or drugs, etc on site.

3.3.5.	Contractors and Sub-Contractors

Each contractor and sub-contractor will be required to co-operate with the Principal Contractor and provide information on risk assessments, method statements, etc. for inclusion in the Health and Safety Plan prepared by the Principal Contractor. In addition, each contractor and sub-contractor will comply with the site rules and any reasonable instructions formulated by the Principal Contractor, in accordance with current relevant health and safety legislation. Contractors and sub-contractors will provide adequate information to the Principal Contractor, who in turn will collate this information for inclusion in the health and safety file documentation.

ANNEXURE 1.           Baseline Risk Assessment.

Project:  ROAD / WATER

| Ref. | ACTIVITY | HAZARD | RISK | MEASURES REQUIRED |
| --- | --- | --- | --- | --- |
|  | Site establishment | Heavy lifting | Injuries and strains | Procedures Equipment Training PPE |
|  |  | Traffic and moving vehicles | Injuries crushing, strains, death. | Traffic Management Training |
|  |  | Dust | Inhalation | Procedures PPE |
|  |  | Snakes and spiders | Poisonous bites can cause death | Procedures Emergency plan |
| 2. | Offloading equipment and materials | Heavy lifting | Injuries strains | Procedures Equipment Training PPE |
|  |  | Collapsing loads | Injuries crushing, strains, death. | Procedures Training PPE |
|  |  | Traffic and moving vehicles | Injuries crushing, strains, death. | Traffic Management Training |
| 3. | Excavations | Traffic and moving vehicles | Injuries crushing, strains, death. | Traffic Management Training |
|  |  | Collapsing side walls | Injuries crushing, strains, death. | Procedures Training PPE |
|  |  | Dust | Inhalation | Procedures PPE |
|  |  | Noise | Hearing impairment | Procedures PPE |
|  |  | Open edges | Falling into or from causing injuries and death. | Procedures Equipment Training PPE |
|  |  | Moving Plant | Injuries crushing, strains, death. | Traffic Management Procedures Training |

| Ref. | ACTIVITY | HAZARD | RISK | MEASURES REQUIRED |
| --- | --- | --- | --- | --- |
| 4. | Back Filling and Layer work | Traffic and moving vehicles | Injuries crushing, strains, death. | Traffic Management Training |
|  |  | Dust | Inhalation | Procedures PPE |
|  |  | Noise | Hearing impairment | Procedures PPE |
|  |  | Moving Plant | Injuries crushing, strains, death. | Traffic Management Procedures Training |
|  |  | Pedestrians and children | Injuries crushing, strains, death. | Traffic Management Procedures Training |
| 5. | Paving packing | Ergonomic constrains | Injuries and pain | Procedures and training |
|  |  | Sun and Heatstroke | Dehydration and death | Procedures PPE Providing Drinking Water |
|  |  | Traffic and moving vehicles | Injuries crushing, strains, death. | Traffic Management Training |
| 6. | Compacting | Traffic and moving vehicles | Injuries crushing, strains, death. | Traffic Management Training |
|  |  | Dust | Inhalation | Procedures PPE |
|  |  | Noise | Hearing impairment | Procedures PPE |
|  |  | Moving Plant | Injuries crushing, strains, death. | Traffic Management Procedures Training |
|  |  | Traffic and moving vehicles | Injuries crushing, strains, death. | Traffic Management Training |
| 7. | Kerb laying | Heavy lifting | Injuries and strains | Procedures Equipment Training PPE |
|  |  | Ergonomic constrains | Injuries and pain | Procedures and training |
|  |  | Sun and Heatstroke | Dehydration and death | Procedures PPE Providing Drinking Water |
|  |  | Traffic and moving vehicles | Injuries crushing, strains, death. | Traffic Management Training |
|  |  | Dust | Inhalation | Procedures PPE |
|  |  | Noise | Hearing impairment | Procedures PPE |
|  |  | Moving Plant | Injuries crushing, strains, death. | Traffic Management Procedures Training |

| Ref. | ACTIVITY | HAZARD | RISK | MEASURES REQUIRED |
| --- | --- | --- | --- | --- |
| 8. | Presence of visitors and members the public | Moving plant and equipment | Injuries crushing, strains, death | Procedures Traffic Management Training |
|  |  | Falling equipment | Injuries and death. | Procedures Equipment Training PPE |
|  |  | Dust | Inhalation | Procedures PPE |
|  |  | Noise | Hearing impairment | Procedures PPE |
|  |  | Collapsing structures and support | Injuries crushing, strains, death. | Procedures Equipment Training PPE |
| 9. | Brickwork | Heavy lifting | Injuries and strains | Procedures Training PPE |
|  |  | Ergonomic and posture | Strains and injuries | Procedures Training PPE |
|  |  | Collapsing structures | Injuries crushing, strains, death. | Procedures Equipment Training PPE |
| 10. | Plumbing and Storm water installation | Cutting grinding | Cuts, bruises and injuries | Procedures Equipment Training PPE |
|  |  | Dust | Inhalation | Procedures PPE |
|  |  | Noise | Hearing impairment | Procedures PPE |
| 11. | Moving Vehicles and plant | Traffic accidents | Injuries crushing, strains, death. | Traffic Management Procedures Training |

# ANNEXURE 2

# ACKNOWLEDGEMENT OF RECEIPT

This document must be completed by the bidding Principal Contractor and all Contractors pricing work on this Project.

Acknowledgement of receipt:

# I, ___________________________________representing________________________________________

Principal Contractor /Contractor / Employer have satisfied myself with the content of the Health and Safety Specification and shall ensure that the Principal Contractor / Contractor and its personnel comply with all obligations / requirements in respect thereof.

# Signature_______________________				Date___________________________

Principal Contractor / Sub Contractor

# Signature_______________________

# Date___________________________

Client/Agent_____________________

Signature ______________________

# Date___________________________

ANNEXURE 3

PRINCIPAL CONTRACTOR CONSTRUCTION MANAGER FORM

I, ____________________________________, of (company name) _______________________________,

do hereby appoint ____________________________________________ being a full-time employee on the

__________________________________________ project, with the duty of CONSTRUCTION MANAGER.

You are appointed in terms of the, OHS Act 85 of 1993 – CR 8(1), your area of responsibility is as follows;

______________________________________________________________________________________

Your duties will include but no be limited to:

- Ensuring that all company safety, health and environmental procedures along with any specific client requirements are implemented and adhered to.

- Ensuring that all applicable legislative requirements are implemented and complied with.

- Ensuring that only authorised persons gain access to the construction premises and associated areas.

- Ensuring that all persons are made aware of the hazards associated with their work and that all reasonable measures are implemented to reduce these risks.

- Ensuring that all construction activities are carried out under the control and supervision of competent supervisors.

- Ensuring that all plant and machinery is in a safe working condition and that only trained and authorised persons utilize such items.

- Ensuring that the necessary personal protective equipment made available and used by the appropriate persons.

- Ensuring that all contractors adhere to the health and safety requirements of the contract.

- Ensuring that all injuries and incidents are reported and investigated in the appropriate manner and that suitable measures are implemented to prevent re-occurrences.

- Ensuring that all reasonable steps are taken to ensure the health and safety of all persons employed on the contract and of those who are affected by the construction operations.

- You are to take all reasonable steps to ensure the health and safety of all persons associated with this designation.

- This appointment also entrusts you to assist and advise all employees in ensuring adherence to company and statutory health, safety and environmental requirements. Please familiarise yourself with these requirements and report all deviations and areas of non-compliance, which you cannot rectify to me directly.

SIGNATURE ______________________________________________________

DESIGNATION_____________________________________________________

DATE_____________________________________________________________

ACCEPTANCE OF DESIGNATION______________________________________

ANNEXURE 4

AGREEMENT WITH MANDATORY

In terms of Section 37 (1) and (2)

WRITTEN AGREEMENT ENTERED INTO AND BETWEEN

____________________________________________________

(Herein after referred to as the “CLIENT”)

AND

____________________________________________________

(Herein after referred to as the Contractor)

Each page as well as each change made to be initialled.

DEFINITION OF MANDATORY:

Includes an agent, a Contractor or Sub-Contractor for work, but without derogating from his status in his own right as an Employer or User.

SECTION 37 (1)

Whenever an employee does or omits to do any act which it would be an offence in terms of this Act for the employer or such employee or a user to do or omit to do, then, unless it is provided that: -

(a)	in doing or omitting to do that act the employee was acting without the connivance of permission of the employer or any such user;

(b)	it was not under any condition or in any circumstances within the scope of the authority of the employee to do or omit to do an act, whether lawful or unlawful, of the character of the act or omissions charged, and

(c)	all reasonable steps were taken by the Employer or any such user to prevent any act or omission of the kind in question.

The employer or any such user himself shall be presumed to have done or omitted to do that Act, and shall be liable to be convicted and sentenced in respect thereof; and the fact that he issued instructions forbidding any act or omissions of the kind in question shall not, in itself, be accepted as sufficient proof that he took all reasonable steps to prevent the act or omission.

SECTION 37 (2)

The provision of subsection (1) shall mutates mutandis apply in the case of a mandatory of employer or user, except if the parties have agreed in writing to the arrangements and procedures between them to ensure compliance by the mandatory with the provisions of this Act.

ACCEPTANCE BY MANDATORY

In terms of Section 37 (2) of the OHS Act 85 of 1993,

I _____________________________________________________________________________________

Representing (Contractor Company Name)  ___________________________________________________

responsible for carrying out (describe activity) _________________________________________________

at the (contract/site name)_________________________________________________________________

undertake to ensure that the requirements and provisions of the OHS Act and Construction Regulations are complied with.

__________________________		________________________

Section 16 (2) for Sub-Contractor	            Date

__________________________                       	 ________________________

Clients Agent		            Date

Annexure 5

APPOINTMENT

CONSTRUCTION REGULATION 5 (1) (k)

In terms of the above-mentioned regulation:

The Contractor shall submit the following for approval before commencement of any construction work and shall commence with activities only after approval:

- Letter of Good Standing.CR. 7(1)(c)(iv)

- Health and Safety file with Health and Safety plan.CR 7.(1)

- Required appointment letters of relevant responsible persons with proof of 	competency.CR 8

- Risk assessment of anticipated activities to be performed on this project. CR 9

I,_________________________________________________________ representing

________________________________________________________________________ (Client), appoint:

(Contractors company name)

to carry out the work of

(describe activity)

By this appointment:

- Your company must ensure that all relevant documentation as required by _______________________________________(The Client) Projects Fall protection plan is included.

CONSTRUCTION PROJECT: _____________________________________________________________

Appointment period:

From_____________________________Until_____________________________

ACCEPTANCE

I,_________________________ representing__________________________ (Contractors company name)

accept this appointment. I am familiar with Occupational Health and safety Act and Construction Regulations as well as the associated duties and responsibilities of this appointment.

SIGNATURE:________________    		DATE: _________________

Subcontractor representative

SIGNATURE:____________________________

Section 16 (2)

OHS 5	Covid-19

OHS 5.1 	Introduction

This specification is developed with the objective to Manage Health and Safety on the construction site with the emphasis on Health and preventing the spread and infection of and with the Corona virus.

This Specification is additional to the site-specific H&S Specification and do not reduce or change the contractor’s responsibility regarding Health and Safety management on site.

Due to the rapid changing situation this Specification shall be updated and amended as more information and other more conclusive measures are identified and verified.

This specification is subject to all relevant legislative notices regarding the COVID 19 Pandemic and the regulations issued by the South African Government.

OHS 5.2 	Objective

This specification is aimed at maintaining the health and wellbeing of all employed/working on the construction site and related activities as well as all people who might be affected by the construction process where the contractor have any influence or authority.

OHS 5.3 	Purpose of this specification:

This specification is a direct response to the current challenges in the work place in regard to the COVID 19 Pandemic and measures to be implemented in order to resume and continue work in an as safe manner as possible and to prevent the spread of infections associated with COVID 19.

OHS 5.4	 Covid-19 Risk Assessments:

COVID 19 Risk Assessments have been developed and are attached for reference see Addendum 1C19.

The Risk Assessments are based on current knowledge and available information.

General best practices in line with Government and WHO (World Health Organisation) guidelines propagated as control and mitigation.

OHS 5.5 		Management Plan and Protocols for Managing Construction operations during COVID                                                             19 Pandemic:

The Client shall provide a plan with protocols and measures to be implemented. This plan shall cover all aspects that needs to be addressed with instructions, checklists and procedures/protocols to be followed and managed in order to be compliant with current Government notices and regulations issued.

The Contractor shall inform the client of any shortcoming or other issues rendering the plan inefficient or non-compliant.

OHS 5.6 	Implementation of Specification and record keeping:

The Principal contractor shall implement this plan and keep records of all:

- Communications and awareness

- Training done

- Inspections

- Protocols implemented and managed

OHS 5.7 	Management and Responsibility

The Principal Contractors Construction Manager CR.8 (1) shall manage this plan with the assistance of his Safety Officer and a dedicated “COVID 19 Coordinator”

OHS 5.8 	Management in relation to construction activities

In addition to providing PPE as per Risk assessments for H&S Management the contractor shall provide sanitation and wash facilities with soap and water.

Supervisors shall manage work in with social distancing in mind. When work need to be done that require close proximity between workers, the number of workers shall be limited at that activity and appropriate PPE shall be issued to prevent the spreading and possible contamination of infection.

The contractor shall provide additional overalls in order for workers to wash their overalls on a daily basis.

Contractor to implement a cleaning routine for all surfaces that can be contaminated.

All work areas, offices to be cleaned daily and all waste to be removed. Registers to be kept of all cleaning and disinfecting on site.

OHS 5.9 	Compliance Monitoring

The Clients H&S Agent shall monitor and audit all measures and implemented protocols as required by Government Notices and the relevant Regulations.

Failure to abide by these standards and the guidelines set by Government shall result in the shutdown of the site or parts of it. Non-conformance can also lead to prosecution.

The Client have a duty under the Disaster Management Act to report any contraventions to the relevant Authorities.

## Risk Assessment for Coronavirus (COVID-19):

| Site: |  | Contractor Sec 16(2)/Project Manager |  |
| --- | --- | --- | --- |
| Project: |  | Done by: |  |
| Contractor: |  | Date: |  |
| Team: |  |  |  |

| SITUATIONS: |  |
| --- | --- |
|  | Someone entering the workplace already infected with CV19 |
|  | Someone becomes ill within the workplace |
|  | Contaminated workplace |
|  | Proximity, workplace gatherings (social distancing) |
|  | General Ignorance |
|  | Self-isolation |
|  | Transport and Travel (Travelling across district borders) |
|  | Symptomatic or exposed employee(s) |
|  | Presenteeism |
|  | First Aid Training / CPR Manikin |
|  | Lack of accurate information / a failure to disseminate information |
|  | Accommodation |
|  | Welfare facilities |
|  | Plant and Equipment |
|  | Consequence Management |

| Nr | HAZARD |  |  | INITIAL RISK |  |  | CONTROLS | RESIDUAL RISK |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Hazard Description | Risk | Health/Safety Influenced | Hazard Severity | Likeli -hood | Risk Rating | List Controls Required | Hazard Severity | Likeli -hood | Risk Rating |
| 1. | Someone entering the workplace with CV19 | Passing the virus on to other employees, causing illness and possible death | Health Safety | 5 | 3 | 15 | - Symptomatic individuals will not be allowed entry. - Hygiene requirements (handwashing etc.) and symptoms of CV19 included with Induction. - CV19 Information posters placed in accessible locations in the workplace | 3 | 1 | 3 |
| 2. | Someone becomes ill within the workplace | Workers contracting CV19 by any means, causing illness and possible death | Health Safety | 5 | 3 | 15 | - Worker removed to a designated area at least 2 metres away from other people. - The individual will be sent home and advised to follow Governmental guidance. - Workplace decontaminated following accepted standards. - Relevant PPE to be issued | 5 | 1 | 5 |

| Nr | HAZARD |  |  | INITIAL RISK |  |  | CONTROLS | RESIDUAL RISK |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Hazard Description | Risk | Health/ Safety Influenced | Hazard Severity | Likeli -hood | Risk Rating | List Controls Required | Hazard Severity | Likeli -hood | Risk Rating |
| 3. | Contaminated workplace | Workers catching CV19 due to contaminated surfaces, causing illness and possible death | Health Safety | 5 | 2 | 10 | - Formal cleaning regime introduced (Employees cleaning equipment and facilities more often). - Hand sanitisers to be been placed in readily accessible locations. - Extra hygiene requirements enforced. - Multi-use handtowels not allowed for drying hands. - Relevant PPE to be issued | 5 | 1 | 5 |
| 4. | Physical Proximity during workplace gatherings | Workers catching CV19 due to working closely with infected colleagues, causing illness and possible death | Health Safety | 5 | 3 | 15 | - Social Distancing policy implemented. All work areas and activities been evaluated for the possibility of implementing social distancing (no handshaking, deferring large meetings etc.) - Provision of suitable and sufficient PPE; - Demarcation and spacing of queueing areas; | 5 | 1 | 5 |
| 5. | General Ignorance | Workers unaware of risks from CV19 and become infected, causing illness and possible death | Health Safety | 5 | 3 | 15 | - A formal training program implemented to cover risks, symptoms and control measures. Attendance to all sessions mandatory with attendance registers kept on file as proof. | 5 | 1 | 5 |
| 6. | Self-isolation of workers | Workers unaware of the need to (or how to) self-isolate, causing further spread of disease and possible death | Health Safety | 5 | 3 | 15 | - A formal training program implemented educate workers on control measures, including self-isolation. Attendance to all sessions mandatory with attendance registers kept on file as proof. | 4 | 1 | 4 |
| Nr | HAZARD | INITIAL RISK | CONTROLS | RESIDUAL RISK | Nr | HAZARD | - INITIAL RISK | CONTROLS | RESIDUAL RISK | Nr |
| 7. | Transport and Travel (Travelling across District borders borders) | Travelling across district borders and afterwards returning "Maximum allowed capacity exceeded; No facilities for sanitising vehicles and passengers; No additional protective measures available, e.g. face masks; | Health Safety | 5 | 2 | 10 | - Adhere to general travel ban by SA Government. - Implement alternatives to travel - postpone trips or hold meetings via video conferencing. - Selection and provision of transport services compliant with gazetted requirements; - Policy and procedures and rules for travel, where possible to limit the use of public transport, or to arange selective methods of transport, - ongoing toolbox talks and supply of cloth masks to be worn when travelling or moving on and off site. - Vehicles maintained at 70% capacity or less; - Vehicles sanitised between trips; hand sanitiser provided for passengers. | 5 | 1 | 5 |
| 8. | Symptomatic or exposed employee(s) | Workers are symptomatic of CV19 or has been in close contact with someone with CV19, causing further spread of disease and possible death | Health Safety | 5 | 3 | 15 | - If worker is unfit for work, they will be booked off sick as per normal policy. - Symptomatic employees will be sent home. - Colleagues who came in contact with symptomatic workers will be informed of symptoms and advised to contact a doctor for guidance. - Working from home will be considered. - Relevant PPE to be issued | 5 | 1 | 5 |
| 9. | Presenteeism | A worker catches CV19 because a colleague continues working despite being unwell, causing further spread of disease and possible death | Health Safety | 5 | 3 | 15 | - Workers coming in contact with symptomatic ones will be informed of symptoms and advised to contact a doctor for guidance. - Workplace will be decontaminated following Governmental guidance: - Relevant PPE to be issued | 5 | 1 | 5 |

| Nr | HAZARD |  |  | INITIAL RISK |  |  | CONTROLS | RESIDUAL RISK |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Hazard Description | Risk | Health/Safety Influenced | Hazard Severity | Likeli -hood | Risk Rating | List Controls Required | Hazard Severity | Likeli -hood | Risk Rating |
| 10. | First Aid Training / CPR Manikin | Workers exposed to CV19 due to providing First Aid in the workplace or during CPR Training on Mannequin, causing further spread of disease and possible death | Health Safety | 5 | 2 | 10 | - Proper training of First Aid staff - Use of correct equipment while giving First Aid - Maintaining proper mannequin hygiene - Relevant PPE to be issued | 5 | 1 | 5 |
| 11. | Lack of accurate information / a failure to disseminate information | Employees unaware of risks from CV19 get infected due to lack of awareness of control measures, causing further spread of disease and possible death | Health Safety | 5 | 3 | 15 | - A designated person will be appointed to monitor CV19 by signing up for immediate news updates and monitoring relevant Websites and News outlets. - A risk communication plan will be implemented, ensuring timely updating/ sharing of information with all internal & external stakeholders | 5 | 1 | 5 |
| 12. | Accommodation | Social density - inability to maintain social distancing, Cross contamination from the lack of social distancing, shared utilities and belongings, shared ablutions , cross infection among inhabitants and cleaning, catering staff |  |  |  |  | - Policy and method statement for accommodation and to be reviewed - Sleeping and dining quarters to allow for minimum 1.5m space between persons; - Dedicated bedding, towels, utensils, soaps etc.; - Individual facilities for safe keeping; - Individual, segregated facilities for storage of laundry; - Procedures and rules of occupancy and cleaning; - Induction and primary health promotion to be done regularly. - Isolation area to be available should anyone display symptoms, and safe removal for testing. - Food to be served wrapped and available individually. |  |  |  |
| 13. | Welfare facilities | Social density - inability to maintain social distancing in, Cross contamination from the lack of social distancing, shared utilities and belongings, shared ablutions , cross infection among inhabitants and cleaning staff |  |  |  |  | - Updating of policy, method statements - limiting of personnel on site to minimum number required to maintain control and management. - Implement and maintain cleaning and disinfecting progamme. - Site rules for social distancing to 1.5m. - Use technology to avoid close proximity between individuals where possible |  |  |  |
| 14. | Plant and Equipment | No facilities for sanitising vehicle/plant and operators /drivers; No additional protective measures available, e.g. face masks; |  |  |  |  | - Only operator/driver allowed in cab - ongoing toolbox talks and supply of cloth masks to be worn when travelling or moving on and off site. - Vehicles maintained at 70% capacity or less; - Plant/Vehicles sanitised between trips; hand sanitiser provided for passengers. |  |  |  |
| 15. | Consequence Management |  |  |  |  |  | - Revision of policy, method statements and HIRA. - Supervisor/CCO must ensure that workers are updated daily with all the relevant COVID 19 information through DSTIS/Toolbox talks, notices etc.. - Supervisor/CCO must ensure that site is updated daily with all the relevant COVID 19 information. - Workers should be updated with new information daily. - Management must ensure that company disciplinary procedures are in place. - All employees should have knowledge of the company disciplinary procedures. - Work stoppage/site closure where non-compliance exists. |  |  |  |

C. Acknowledgement and Approval

### ANNEXURE D

CONFORMITY WITH EPWP GUIDELINES

### FEZILE DAB DISTRICT MUNICIPALITY

DRILLING AND EQUIPPING OF SIX NEW BOREHOLES AND REFURBISHMENT OF TWO EXISTING BOREHOLES IN MAFAHLANENG /TWEELING

BID NO: FDDM/BID NO: 012/2023-24

EPWP	CONFORMITY WITH RDP GUIDELINES

EPWP 1	PROJECT MANAGEMENT

Due to the complexity of the project an established contractor with applicable experience will be contracted for the construction of the works.  The contractor will however be required to comply with EPWP objectives and will have to submit proposals in this regard at tender stage. These proposals will become binding on the contractor in terms of the contract once accepted and approved by the Municipality.  The proposals should include provision for the employment of local subcontractors on both a conventional subcontract basis and a management contractor basis to create the maximum scope for employment opportunities. In the latter instance the main contractor will be responsible for logistics (e.g. materials and transport) and quality control and the subcontractor will be responsible for the manpower component.

EPWP 2	COMMUNITY PARTICIPATION AND EMPOWERMENT

Community participation in the implementation process will focus on the maximum exploitation of opportunities for employment, training and capacity building presented by the project. The established community structures will form the main communication link between the community and the Municipality and councillors will act as the interface between the Municipality and the community.

The implementation framework for the project, which will be established at Municipality level, will be work shopped with community representatives to ensure interaction with and acceptance by the community at large.  Contentious issues will be referred back to the Municipality for consideration and amendment of the implementation framework if required.

EPWP 3	EDUCATION, TRAINING AND CAPACITY BUILDING

Education, training and capacity building will focus on project related courses or activities and preference will be given to accredited training programmes.  Typical project related accredited training programmes are presented by the South African Federation of Civil Engineering Contractors (SAFCEC) and other similar (approved) accredited training will be considered.

Tenderers will be required to submit details of their proposed education, training and capacity building programmes in terms of the Project Specification and these details should include particulars of the proposed training institution. The actual programme for education, training and capacity building will be established in co-operation with the successful tenderer to comply with his proposals for employment and these programmes will become binding on the contractor in terms of the contract once accepted and approved by the Municipality.

Candidates for the training programmes will be selected mainly from unemployed members of the community in close co-operation and consultation with the Municipality and the relevant sub-committee.

EPWP 4	LABOUR INTENSITY

The aspects of the project representing activities which is either traditionally labour intensive or which could be executed using labour based methods and for which local labour can be employed must be identified.

Tenderers will be required to submit proposals on training, the optimum use of labour intensive construction methods and the use of SMME’s with their tenders.  Their proposals will become binding on the main contractor in terms of the contract once accepted and approved by the Municipality.

EPWP 5	EMPLOYMENT POLICY

Details of the employment policy will be established by the Municipality or the relevant sub-committee. The employment policy will form part of the Project Specification and the main contractor will be compelled in terms of the contract to comply with the employment policy.

The employment policy will focus on;

i)	maximizing local job creation,

ii)	targeting the most needy (single headed households, unemployed and youth), and

iii)	ensuring opportunities for women and disabled.

EPWP 6	WAGES AND LABOUR STANDARDS

Wages and labour standards for the project will comply with the Expanded Public Works Programme Framework Agreement and existing statutory requirements applicable to task based labour. All wage and labour standards’ variables will be determined by the Municipality or the relevant sub-committee and will be included in the Project Specification. The main contractor will be compelled in terms of the contract to comply with the applicable wages and labour standards.

MSCM Regulations: “in the service of the state” means to be –

- a member of –

  - any municipal council;

  - any provincial legislature; or

  - the national Assembly or the national Council of provinces;

- a member of the board of directors of any municipal entity;

- an official of any municipality or municipal entity;

- an employee of any national or provincial department, national or provincial public entity or constitutional institution within the meaning of the Public Finance Management Act, 1999 (Act No.1 of 1999);

- a member of the accounting authority of any national or provincial public entity; or

- an employee of Parliament or a provincial legislature.