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NEC3 Supply Contract (SC3)
	Between


	ESKOM HOLDINGS SOC Ltd 

(Reg No. 2002/015527/30)

	and


	(Reg No. ___________ )

	for


	SUPPLY & DELIVERY OF DIESEL GENERATORS FUEL SUPPLY, THE BULK DIESEL FUEL SUPPLY SYSTEM AND THE USED OIL SYSTEM SPARES FOR 60 MONTHS AS AN WHEN REQUIRED
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PART C1:
AGREEMENTS & CONTRACT DATA

	Contents:


	
	No of pages

	C1.1
	Form of Offer and Acceptance 
	

	C1.2a
	Contract Data provided by the Purchaser
	

	C1.2b
	Contract Data provided by the Supplier
	


C1.1 Form of Offer & Acceptance

Offer

The Purchaser, identified in the Acceptance signature block, has solicited offers to enter into a contract for the procurement of:

Supply and Delivery of Diesel Generators Fuel Supply, The Bulk Diesel Fuel Supply System and The Used Oil System Spares
The tenderer, identified in the Offer signature block, has

	either
	examined the documents listed in the Tender Data and addenda thereto as listed in the Returnable Schedules, and by submitting this Offer has accepted the Conditions of Tender.

	or
	examined the draft contract as listed in the Acceptance section and agreed to provide this Offer.


By the representative of the tenderer, deemed to be duly authorised, signing this part of this Form of Offer and Acceptance the tenderer offers to perform all of the obligations and liabilities of the Supplier under the contract including compliance with all its terms and conditions according to their true intent and meaning for an amount to be determined in accordance with the conditions of contract identified in the Contract Data. 

	
	The offered total of the Prices exclusive of VAT is 
	R 

	
	Value Added Tax @ 15% is
	R 

	
	The offered total of the amount due inclusive of VAT is

	R 

	
	(in words) 



This Offer may be accepted by the Purchaser by signing the Acceptance part of this Form of Offer and Acceptance and returning one copy of this document including the Schedule of Deviations (if any) to the tenderer before the end of the period of validity stated in the Tender Data, or other period as agreed, whereupon the tenderer becomes the party named as the Supplier in the conditions of contract identified in the Contract Data.

	Signature(s)


	
	
	

	Name(s)


	
	
	

	Capacity


	
	
	

	For the tenderer:

	

	Name & signature of witness
	(Insert name and address of organisation)
	
	Date
	

	
	


Acceptance

By signing this part of this Form of Offer and Acceptance, the Purchaser identified below accepts the tenderer’s Offer.  In consideration thereof, the Purchaser shall pay the Supplier the amount due in accordance with the conditions of contract identified in the Contract Data.  Acceptance of the tenderer’s Offer shall form an agreement between the Purchaser and the tenderer upon the terms and conditions contained in this agreement and in the contract that is the subject of this agreement.

The terms of the contract, are contained in: 

Part C1

Agreements and Contract Data, (which includes this Form of Offer and Acceptance)

Part C2

Pricing Data 
Part C3

Scope of Work:  Goods Information including Supply Requirements

and drawings and documents (or parts thereof), which may be incorporated by reference into the above listed Parts.

Deviations from and amendments to the documents listed in the Tender Data and any addenda thereto listed in the Returnable Schedules as well as any changes to the terms of the Offer agreed by the tenderer and the Purchaser during this process of offer and acceptance, are contained in the Schedule of Deviations attached to and forming part of this Form of Offer and Acceptance.  No amendments to or deviations from said documents are valid unless contained in this Schedule.

The tenderer shall within two weeks of receiving a completed copy of this agreement, including the Schedule of Deviations (if any), contact the Purchaser’s agent (whose details are given in the Contract Data) to arrange the delivery of any securities, bonds, guarantees, proof of insurance and any other documentation to be provided in terms of the conditions of contract identified in the Contract Data at, or just after, the date this agreement comes into effect.  Failure to fulfil any of these obligations in accordance with those terms shall constitute a repudiation of this agreement.

Notwithstanding anything contained herein, this agreement comes into effect on the date when the tenderer receives one fully completed and signed original copy of this document, including the Schedule of Deviations (if any).  

	Signature(s)


	
	
	

	Name(s)
	
	
	

	Capacity


	General Manager 

Medupi Generation Division
	
	

	for the Purchaser


	Eskom Holdings SOC Limited

Medupi Power Station

Private Bag x9003

LEPHALALE

Limpopo

0555

	Name & signature of witness
	(Insert name and address of organisation)
	
	Date
	


Note: If a tenderer wishes to submit alternative tenders, use another copy of this Form of Offer and Acceptance.

Schedule of Deviations to be completed by the Purchaser prior to contract award

Note:

1.  This part of the Offer & Acceptance would not be required if the contract has been developed by negotiation between the Parties and is not the result of a process of competitive tendering.
2. The extent of deviations from the tender documents issued by the Purchaser prior to the tender closing date is limited to those permitted in terms of the Conditions of Tender.

3. A tenderer’s covering letter must not be included in the final contract document.  Should any matter in such letter, which constitutes a deviation as aforesaid be the subject of agreement reached during the process of Offer and Acceptance, the outcome of such agreement shall be recorded here and the final draft of the contract documents shall be revised to incorporate the effect of it.

	No.
	Subject
	Details

	1
	[●]
	[●]

	2
	[●]
	[●]

	3
	[●]
	[●]

	4
	[●]
	[●]

	5
	[●]
	[●]

	6
	[●]
	[●]

	7
	[●]
	[●]

	
	
	


By the duly authorised representatives signing this Schedule of Deviations below, the Purchaser and the tenderer agree to and accept this Schedule of Deviations as the only deviations from and amendments to the documents listed in the Tender Data and any addenda thereto listed in the Tender Schedules, as well as any confirmation, clarification or changes to the terms of the Offer agreed by the tenderer and the Purchaser during this process of Offer and Acceptance.  

It is expressly agreed that no other matter whether in writing, oral communication or implied during the period between the issue of the tender documents and the receipt by the tenderer of a completed signed copy of this Form shall have any meaning or effect in the contract between the parties arising from this Agreement. 

	
	For the tenderer:


	
	For the Purchaser



	Signature


	
	
	

	Name
	
	
	

	Capacity


	
	
	General Manager: Medupi

Generation Division

	On behalf of
	(Insert name and address of organisation)


	
	Eskom Holdings SOC Limited

Medupi Power Station

Private Bag x9003

LEPHALALE

Limpopo

0555

	Name & signature of witness
	
	
	Manager: Procurement



	Date
	
	
	


C1.2 SC3 Contract Data

Part one - Data provided by the Purchaser
Completion of this data in full, according to the Options chosen, is essential to create a complete contract.

	Clause
	Statement
	Data

	1
	General
	

	
	The conditions of contract are the core clauses and the clauses for Options 
	

	
	
	X1        Price adjustment for inflation

	
	
	X2

Changes in the law

	
	
	X3:

Multiple currencies

	
	
	X7:

Delay damages

	
	
	X17:
Low performance damages

	
	
	Z:

Additional conditions of contract

	
	of the NEC3 Supply Contract (April 2013) 

	(If the December 2009 edition is to be used delete April 2013 and replace by December 2013)

	10.1
	The Purchaser is (name):
	Eskom Holdings SOC Ltd (reg no: 2002/015527/30), a state owned company incorporated in terms of the company laws of the Republic of South Africa

	
	Address
	Registered office at Megawatt Park, Maxwell Drive, Sandton, Johannesburg

	
	Tel No.
	011 800 8111

	
	Fax No.
	N/A

	10.1
	The Supply Manager is (name): 
	

	
	Address
	Medupi Power Station

	
	Tel
	

	
	e-mail
	

	11.2(13)
	The goods are 
	DIESEL GENERATORS FUEL SUPPLY, THE BULK DIESEL FUEL SUPPLY SYSTEM AND THE USED OIL SYSTEM SPARES

	11.2(14)
	The following matters will be included in the Risk Register
	· Force Majeure

· Labour and Community Unrest which prevent the Supplier access to deliver
· Early warning will be used by both Parties for new risks

	11.2(15)
	The Goods Information is in 
	Part 3: Scope of Work and all documents and drawings to which it makes reference.

	11.2(15)
	The Supply Requirements as part of the Goods Information is in 
	Annexure A to this Contract Data

	12.2
	The law of the contract is the law of 
	the Republic of South Africa

	13.1
	The language of this contract is 
	English

	13.3
	The period for reply is
	Five working days

	2
	The Supplier’s main responsibilities
	As per NEC3 SC Core clause 2

	3
	Time
	

	30.1
	The starting date is.
	TBC

	30.1
	The delivery date of the goods and services is:
	goods and services                  
	delivery date

	
	
	1
2
	Diesel generators fuel supply spares
Bulk diesel fuel supply system spares
	As per the purchase order

As per the purchase order

	
	
	3
	Oil system spares
	As per the purchase order

	30.2
	The Supplier does not bring the goods to the Delivery Place more than one week before the Delivery Date.
	To be agreed by both Parties before delivery 

	31.1
	The Supplier is to submit a first programme for acceptance within 
	Five working days after receipt of purchase order

	32.2
	The Supplier submits revised programmes at intervals no longer than 
	three working days

	4
	Testing and defects
	

	42
	The defects date is 
	Fifty-two weeks after Delivery.

	43.2
	The defect correction period is 
	Four weeks

	42.2
	The defects access period is  
	five days

	5
	Payment
	

	50.1
	The assessment interval is 
	between the 25th day of each successive month or Continuous assessment upon safe delivery and having met all the required standard and signed off

	51.1
	The currency of this contract is the 
	South African Rand

	51.2
	The period within which payments are made is
	30 calendar days after reception of a valid tax invoice for contracts valued below R50 000 0000.00 (Fifty Million Rands) excluding VAT. 60 calendar days after reception of a valid tax invoice for contracts valued R50 000 0000.00 (Fifty Million Rands) excluding VAT and above

	51.4
	The interest rate is 


	the publicly quoted prime rate of interest (calculated on a 365 day year) charged from time to time by the Standard Bank of South Africa Limited (as certified, in the event of any dispute, by any manager of such bank, whose appointment it shall not be necessary to prove) for amounts due in Rands 

	
	Compensation events
	As per NEC3 SC Core clause 6

	7
	Title
	

	70.1     
	Title to the goods
	Once the goods are accepted by the Purchaser

	8
	Risks, liabilities, indemnities and insurance
	

	80.1
	These are additional Purchaser’s risks  
	1. Damage goods during offloading by the Purchaser

	
	
	2. Preservation at Purchaser’s property

3. Damaged/unavailability of Plant and Material for offloading 

	88.1
	The Supplier’s liability to the Purchaser for indirect or consequential loss, including loss of profit, revenue and goodwill is limited to
	R0.0 (zero Rand)

	88.2
	For any one event, the Supplier’s liability to the Purchaser for loss of or damage to the Purchaser’s property is limited to
	(1) for the Purchaser’s existing and surrounding property in the care, custody and control of the Supplier the amount of the deductible (first amount payable) relevant to the event 
and

(2) for all other existing Purchaser’s property the applicable deductible as at contract date 

	88.3
	The Supplier’s liability for Defects due to his design which are not notified before the last defects date is limited to:
	The total price of the design, manufacturing and delivery

	88.4
	The Supplier’s total liability to the Purchaser, for all matters arising under or in connection with this contract, other than the excluded matters, is limited to
	The purchase order amount

	88.5
	The end of liability date is 
	One years after Delivery of the goods and services.

	9
	Termination and dispute resolution
	

	94.1
	The Adjudicator is 
	the person selected from the ICE-SA Division (or its successor body) of the South African Institution of Civil Engineering Panel of Adjudicators by the Party intending to refer a dispute to him.  (see www.ice-sa.org.za). If the Parties do not agree on an Adjudicator the Adjudicator will be appointed by the Arbitration Foundation of Southern Africa (AFSA).

	
	Address
	1st Floor, Maisels Chamber, 4 Protea Place, Sandton

	
	Tel No.
	011 320 0600

	
	Fax No.
	011 320 0533

	
	e-mail
	info@arbitration.co.za

	94.2(3)
	The Adjudicator nominating body is: 
	the Chairman of ICE-SA, a Division of the South African Institution of Civil Engineering, or its successor body (See www.ice-sa.org.za)

	94.4(2)
	The tribunal is: 
	arbitration

	94.4(5)
	The arbitration procedure is 
	the latest edition of Rules for the Conduct of Arbitrations published by The Association of Arbitrators (Southern Africa) or its successor body.

	94.4(5)
	The place where arbitration is to be held is
	South Africa

	
	The person or organisation who will choose an arbitrator 

· if the Parties cannot agree a choice or
· if the arbitration procedure does not state who selects an arbitrator, is
	the Chairman for the time being or his nominee of the Association of Arbitrators (Southern Africa) or its successor body.

	10
	Data for Option clauses
	

	X1
	Price adjustment for inflation
	

	X1.1
	The base date for indices is 
	one month prior to the tender closing date. Prices are fixed for the first 12 months of the contract. CPA can only then be applied after the first 12 months.

	
	The proportions used to calculate the Price Adjustment Factor are:
	proportion
	linked to index for
	Index prepared by

	
	
	0.10
	CPI
	[SEIFSA Table D-4]

	
	
	0.60
	Mechanical Engineering
	[SEIFSA Table G-1]

	
	
	0.15
	Transport
	[SEIFSA Table L2B]

	
	
	0.15
	non-adjustable
	

	
	
	1.00


	
	

	X2
	Changes in the law
	

	X2.1
	A change in the law of 


	Republic of South Africa is a compensation event if it occurs after the Contract Date

	X3
	Multiple currencies
	

	X3.1


	The Purchaser will pay for these items in the currencies stated
	Items
	Other currency
	Total maximum payment in the currency

	
	
	[●]
	     
	     

	
	
	[●]
	     
	     

	
	
	[●]
	     
	     

	X3.1
	The exchange rates are those published in
	[●] on [●] (date)

	
	
	The items will be paid in the other currency 
- to a foreign Bank account nominated by the Supplier 

- to a valid SARB approved CFC account in South Africa

- in accordance with an alternative payment method agreed with the Purchaser before the Contract Date.

(select one of the three methods as agreed with the successful tenderer prior to contract award and delete the others and this note)

	X7
	Delay damages
	

	X7.1
	Delay damages for Delivery are
	Delivery of
	amount per day

	
	
	Diesel generators fuel supply, the bulk diesel fuel supply system and the used oil system spares
	2% of the total value of the purchase order goods per day to a maximum of 20%

	X17
	Low performance damages
	

	X17.1
	The amounts for low performance damages are:
	Amount
	performance level

	
	
	Replace the spares at Supplier’s cost within defect correction period
	Defective spares delivered 

	Z
	The additional conditions of contract are
	Z1 to Z15 always apply for Eskom

	
	

	Z1
	Cession delegation and assignment

	Z1.1
	The Supplier does not cede, delegate or assign any of its rights or obligations to any person without the written consent of the Purchaser.

	Z1.2
	Notwithstanding the above, the Purchaser may on written notice to the Supplier cede and delegate its rights and obligations under this contract to any of its subsidiaries or any of its present divisions or operations which may be converted into separate legal entities as a result of the restructuring of the Electricity Supply Industry. 

	
	

	Z2
	Joint ventures

	Z2.1
	If the Supplier constitutes a joint venture, consortium or other unincorporated grouping of two or more persons or organisations then these persons or organisations are deemed to be jointly and severally liable to the Purchaser for the performance of this contract.

	Z2.2
	Unless already notified to the Purchaser, the persons or organisations notify the Supply Manager within two weeks of the Contract Date of the key person who has the authority to bind the Supplier on their behalf.

	Z2.3
	The Supplier does not alter the composition of the joint venture, consortium or other unincorporated grouping of two or more persons without the consent of the Purchaser having been given to the Supplier in writing.

	
	

	Z3
	Change of Broad Based Black Economic Empowerment (B-BBEE) status

	Z3.1
	Where a change in the Supplier’s legal status, ownership or any other change to his business composition or business dealings results in a change to the Supplier’s B-BBEE status, the Supplier notifies the Purchaser within seven days of the change.

	Z3.2
	The Supplier is required to submit an updated verification certificate and necessary supporting documentation confirming the change in his B-BBEE status to the Supply Manager within thirty days of the notification or as otherwise instructed by the Supply Manager.

	Z3.3
	Where, as a result, the Supplier’s B-BBEE status has decreased since the Contract Date the Purchaser may either re-negotiate this contract or alternatively, terminate the Supplier’s obligation to Provide the Goods and Services.

	Z3.4
	Failure by the Supplier to notify the Purchaser of a change in its B-BBEE status may constitute a reason for termination. If the Purchaser terminates in terms of this clause, the procedures on termination are P1, P2 and P3 as stated in clause 92, and the amount due is A1 and A3 as stated in clause 93.

	
	

	Z4
	Confidentiality

	Z4.1
	The Supplier does not disclose or make any information arising from or in connection with this contract available to Others. This undertaking does not, however, apply to information which at the time of disclosure or thereafter, without default on the part of the Supplier, enters the public domain or to information which was already in the possession of the Supplier at the time of disclosure (evidenced by written records in existence at that time).  Should the Supplier disclose information to Others in terms of clause 23.1, the Supplier ensures that the provisions of this clause are complied with by the recipient.

	Z4.2
	If the Supplier is uncertain about whether any such information is confidential, it is to be regarded as such until notified otherwise by the Supply Manager.

	Z4.3
	In the event that the Supplier is, at any time, required by law to disclose any such information which is required to be kept confidential, the Supplier, to the extent permitted by law prior to disclosure, notifies the Purchaser so that an appropriate protection order and/or any other action can be taken if possible, prior to any disclosure.  In the event that such protective order is not, or cannot, be obtained, then the Supplier may disclose that portion of the information which it is required to be disclosed by law and uses reasonable efforts to obtain assurances that confidential treatment will be afforded to the information so disclosed.

	Z4.4
	The taking of images (whether photographs, video footage or otherwise) of the goods or any portion thereof, in the course of Providing the Goods and Services and after Delivery, requires the prior written consent of the Supply Manager.  All rights in and to all such images vests exclusively in the Purchaser.  

	Z4.5
	The Supplier ensures that all his subcontractors abide by the undertakings in this clause.

	
	

	Z5
	Waiver and estoppel: Add to core clause 12.3:

	Z5.1
	Any extension, concession, waiver or relaxation of any action stated in this contract by the Parties, the Supply Manager or the Adjudicator does not constitute a waiver of rights, and does not give rise to an estoppel unless the Parties agree otherwise and confirm such agreement in writing.

	
	

	Z6
	Health, safety and the environment:  Add to core clause 25.4

	Z6.1
	The Supplier undertakes to take all reasonable precautions to maintain the health and safety of persons in and about the provision of the goods and execution of the services. 

Without limitation the Supplier:

· warrants that the total of the Prices as at the Contract Date includes a sufficient amount for proper compliance with all applicable health & safety laws and regulations and the health and safety rules, guidelines and procedures provided for in this contract and generally for the proper maintenance of health & safety in and about the execution of supply and

· undertakes, in and about the execution of the supply, to comply with all applicable health & safety laws and regulations and rules, guidelines and procedures otherwise provided for under this contract and ensures that his Subcontractors, employees and others under the Supplier’s direction and control, likewise observe and comply with the foregoing.

	Z6.2
	The Supplier, in and about the execution of the supply, complies with all applicable environmental laws and regulations and rules, guidelines and procedures otherwise provided for under this contract and ensures that his Subcontractors, employees and others under the Supplier’s direction and control, likewise observe and comply with the foregoing.

	
	

	Z7
	Provision of a Tax Invoice and interest.  Add to core clause 51

	Z7.1
	Within one week of receiving a payment certificate from the Supply Manager in terms of core clause 51.1, the Supplier provides the Purchaser with a tax invoice in accordance with the Purchaser's procedures stated in the Goods Information, showing the amount due for payment equal to that stated in the payment certificate.

	Z7.2
	If the Supplier does not provide a tax invoice in the form and by the time required by this contract, the time by when the Purchaser is to make a payment is extended by a period equal in time to the delayed submission of the correct tax invoice.  Interest due by the Purchaser in terms of core clause 51.2 is then calculated from the delayed date by when payment is to be made.

	Z7.3
	The Supplier (if registered in South Africa in terms of the companies Act) is required to comply with the requirements of the Value Added Tax Act, no 89 of 1991 (as amended) and to include the Purchaser’s VAT number 4740101508 on each invoice he submits for payment.

	
	

	Z8
	Notifying compensation events

	Z8.1
	Delete from the last sentence in core clause 61.3 the words, “unless the event arises from the Supply Manager giving an instruction, changing an earlier decision or correcting an assumption”.

	
	

	Z9
	Purchaser’s limitation of liability

	Z9.1
	The Purchaser’s liability to the Supplier for the Supplier’s indirect or consequential loss is limited to R0.00 (zero Rand)

	Z9.2
	The Supplier’s entitlement under the indemnity in 83.1 is provided for in 60.1(12) and the Purchaser’s liability under the indemnity is limited.

	
	

	Z10
	Termination: Add to core clause 91.1, at the second main bullet point, fourth sub-bullet point, after the words "against it":  

	Z10.1
	   or had a business rescue order granted against it.

	
	

	Z11
	Addition to secondary Option X7 Delay damages (if applicable in this contract)

	Z11.1
	If the amount due for the Supplier’s payment of delay damages reaches the limits stated in this Contract Data for Option X7, the Purchaser may terminate the Supplier’s obligation to Provide the Goods and Services using the same procedures and payment on termination as those applied for reasons R1 to R15 or R18 stated in the Termination Table.

	
	

	Z12
	Ethics

	For the purposes of this Z-clause, the following definitions apply:

	Affected Party
	means, as the context requires, any party, irrespective of whether it is the Supplier or a third party, such party’s employees, agents, or Subcontractors or Subcontractor’s employees, or any one or more of all of these parties’ relatives or friends,

	Coercive Action
	means to harm or threaten to harm, directly or indirectly, an Affected Party or the property of an Affected Party, or to otherwise influence or attempt to influence an Affected Party to act unlawfully or illegally,

	Collusive Action
	means where two or more parties co-operate to achieve an unlawful or illegal purpose, including to influence an Affected Party to act unlawfully or illegally,

	Committing Party
	means, as the context requires, the Supplier, or any member thereof in the case of a joint venture, or its employees, agents, or Subcontractors or the Subcontractor’s employees,

	Corrupt Action
	means the offering, giving, taking, or soliciting, directly or indirectly, of a good or service to unlawfully or illegally influence the actions of an Affected Party,

	Fraudulent Action
	means any unlawfully or illegally intentional act or omission that misleads, or attempts to mislead, an Affected Party, in order to obtain a financial or other benefit or to avoid an obligation or incurring an obligation,

	Obstructive Action
	means a Committing Party unlawfully or illegally destroying, falsifying, altering or concealing information or making false statements to materially impede an investigation into allegations of Prohibited Action, and

	Prohibited Action
	means any one or more of a Coercive Action, Collusive Action Corrupt Action, Fraudulent Action or Obstructive Action.

	Z12.1
	A Committing Party may not take any Prohibited Action during the course of the procurement of this contract or in execution thereof.

	Z12.2
	The Purchaser may terminate the Supplier’s obligation to Provide the Services if a Committing Party has taken such Prohibited Action and the Supplier did not take timely and appropriate action to prevent or remedy the situation, without limiting any other rights or remedies the Purchaser has. It is not required that the Committing Party had to have been found guilty, in court or in any other similar process, of such Prohibited Action before the Purchaser can terminate the Supplier’s obligation to Provide the Services for this reason.

	Z12.3
	If the Purchaser terminates the Supplier’s obligation to Provide the Services for this reason, the amounts due on termination are those intended in core clauses 92.1 and 92.2.

	Z12.4
	A Committing Party co-operates fully with any investigation pursuant to alleged Prohibited Action. Where the Purchaser does not have a contractual bond with the Committing Party, the Supplier ensures that the Committing Party co-operates fully with an investigation.


Z13
Insurance
Z __13.1
Replace core clause 84 with the following:
	Insurance cover
	84
	

	
	84.1
	When requested by a Party, the other Party provides certificates from his insurer or broker stating that the insurances required by this contract are in force. 

	
	84.2
	The Supplier provides the insurances stated in the Insurance Table A for events which are at the Supplier’s risk from the starting date until the last defects date or a termination certificate has been issued.

	
	
	

	INSURANCE TABLE A

	Insurance against

Minimum amount of cover or minimum limit of indemnity

Loss of or damage to the goods, plant and materials

The replacement cost where not covered by the Purchaser’s insurance.

The Purchaser’s policy deductible as at Contract Date, where covered by the Purchaser’s insurance.
Liability for loss of or damage to property (except the goods, plant and materials and equipment) and liability for bodily injury to or death of a person (not an employee of the Supplier) caused by activity in connection with this contract

Loss of or damage to property

Purchaser’s property

The replacement cost where not covered by the Purchaser’s insurance.

The Purchaser’s policy deductible as at Contract Date, where covered by the Purchaser’s insurance.
Other property

The replacement cost
Death of or bodily injury

The amount required by the applicable law.

Liability for death of or bodily injury to employees of the Supplier arising out of and in the course of their employment in connection with this contract

The amount required by the applicable law 




Z _13.2

Replace core clause 87 with the following:
	Insurance by the Purchaser
	
	87
	

	
	
	87.1
	The Purchaser provides the insurances stated in the Insurance Table B

	
	
	
	INSURANCE TABLE B

Insurance against or name of policy
Minimum amount of cover or minimum limit of indemnity

Assets All Risk

Per the insurance policy document

Contract Works insurance

Per the insurance policy document

Environmental Liability

Per the insurance policy document
General and Public Liability

Per the insurance policy document
Transportation (Marine)

Per the insurance policy document
Motor Fleet and Mobile Plant

Per the insurance policy document
Terrorism

Per the insurance policy document
Cyber Liability

Per the insurance policy document

Nuclear Material Damage and Business Interruption
Per the insurance policy document
Nuclear Material Damage Terrorism
Per the insurance policy document


	Z14
	Nuclear Liability

	Z14.1
	The Purchaser is the operator of the Koeberg Nuclear Power Station (KNPS), a nuclear installation, as designated by the National Nuclear Regulator of the Republic of South Africa, and is the holder of a nuclear licence in respect of the KNPS.

	Z14.2
	The Purchaser is solely responsible for and indemnifies the Supplier or any other person against any and all liabilities which the Supplier or any person may incur arising out of or resulting from nuclear damage, as defined in Act 47 of 1999, save to the extent that any liabilities are incurred due to the unlawful intent of the Supplier or any other person or the presence of the Supplier or that person or any property of the Supplier or such person at or in the KNPS or on the KNPS site, without the permission of the Purchaser or of a person acting on behalf of the Purchaser.

	Z14.3
	Subject to clause Z14.4 below, the Purchaser waives all rights of recourse, arising from the aforesaid, save to the extent that any claims arise or liability is incurred due or attributable to the unlawful intent of the Supplier or any other person, or the presence of the Supplier or that person or any property of the Supplier or such person at or in the KNPS or on the KNPS site, without the permission of the Purchaser or of a person acting on behalf of the Purchaser.

	Z14.4
	The Purchaser does not waive its rights provided for in section 30 (7) of Act 47 of 1999, or any replacement section dealing with the same subject matter.

	Z14.5
	The protection afforded by the provisions hereof shall be in effect until the KNPS is decommissioned.

	
	

	Z15
	Asbestos

	For the purposes of this Z-clause, the following definitions apply:

	AAIA
	means approved asbestos inspection authority.

	ACM
	means asbestos containing materials.

	AL
	means action level, i.e. a level of 50% of the OEL, i.e. 0.1 regulated asbestos fibres per ml of air measured over a 4 hour period. The value at which proactive actions is required in order to control asbestos exposure to prevent exceeding the OEL.

	Ambient Air
	means breathable air in area of work with specific reference to breathing zone, which is defined to be a virtual area within a radius of approximately 30cm from the nose inlet.

	Compliance Monitoring
	means compliance sampling used to assess whether or not the personal exposure of workers to regulated asbestos fibres is in compliance with the Standard’s requirements for safe processing, handling, storing, disposal and phase-out of asbestos and asbestos containing material, equipment and articles.

	OEL
	means occupational exposure limit.

	Parallel Measurements
	means measurements performed in parallel, yet separately, to existing measurements to verify validity of results.

	Safe Levels
	means  airborne asbestos exposure levels conforming to the Standard’s requirements for safe processing, handling, storing, disposal and phase-out of asbestos and asbestos containing material, equipment and articles.

	Standard
	means the Purchaser’s Asbestos Standard 32-303: Requirements for Safe Processing, Handling, Storing, Disposal and Phase-out of Asbestos and Asbestos Containing Material, Equipment and Articles.

	SANAS
	means the South African National Accreditation System.

	TWA
	means the average exposure, within a given workplace, to airborne asbestos fibres, normalised to the baseline of a 4 hour continuous period, also applicable to short term exposures, i.e. 10-minute TWA.

	Z15.1
	The Purchaser ensures that the Ambient Air in the area where the Supplier will Provide the Services conforms to the acceptable prescribed South African standard for asbestos, as per the regulations published in GNR 155 of 10 February 2002, under the Occupational Health and Safety Act, 1993 (Act 85 of 1993) (“Asbestos Regulations”). The OEL for asbestos is 0.2 regulated asbestos fibres per millilitre of air as a 4-hour TWA, averaged over any continuous period of four hours, and the short term exposure limit of 0.6 regulated asbestos fibres per millilitre of air as a 10-minute TWA, averaged over any 10 minutes, measured in accordance with HSG248 and monitored according to HSG173 and OESSM.

	Z15.2
	Upon written request by the Supplier, the Purchaser certifies that these conditions prevail. All measurements and reporting are effected by an independent, competent, and certified occupational hygiene inspection body, i.e. a SANAS accredited and Department of Employment and Labour approved AAIA. The Supplier may perform Parallel Measurements and related control measures at the Supplier’s expense. For the purposes of compliance the results generated from Parallel Measurements are evaluated only against South African statutory limits as detailed in clause Z15.1. Control measures conform to the requirements stipulated in the AAIA-approved asbestos work plan.

	Z15.3
	The Purchaser manages asbestos and ACM according to the Standard.

	Z15.4
	In the event that any asbestos is identified while Providing the Services, a risk assessment is conducted and if so required, with reference to possible exposure to an airborne concentration of above the AL for asbestos, immediate control measures are implemented and relevant air monitoring conducted in order to declare the area safe.

	Z15.5
	The Supplier’s personnel are entitled to stop working and leave the contaminated area forthwith until such time that the area of concern is declared safe by either Compliance Monitoring or an AAIA approved control measure intervention, for example, per the emergency asbestos work plan, if applicable.

	Z15.6
	The Supplier continues to Provide the Services, without additional control measures presented, on presentation of Safe Levels. The contractually agreed dates to Provide the Services, including the Completion Date, are adjusted accordingly. The contractually agreed dates are extended by the notification periods required by regulations 3 and 21 of the Asbestos Regulations.

	Z15.7
	Any removal and disposal of asbestos, asbestos containing materials and waste, is done by a registered asbestos contractor, instructed by the Purchaser at the Purchaser’s expense, and conducted in line with South African legislation.



Annexure A:
Supply Requirements
The Supply Requirements for this contract are as follows:

[Revise and complete as required]
	1. The requirements for the supply are
	Supplier manufactures, tests, preserve and deliver the goods within 2 weeks after receipt of the purchase order

	2. The requirements for transport are 
	The goods will be transported on the road

	3. The delivery place is
	The delivery location is Medupi Power Station Stores

	4. Actions of the Parties during supply
	Action
	Party which does it

	
	Giving notice of Delivery
	Supplier

	
	Checking packing and marking before dispatch
	Supplier

	
	Contracting for transport
	Supplier

	
	Pay costs of transport
	Supplier

	
	Arrange access to delivery place
	Purchaser 

	
	Loading the goods
	Supplier

	
	Unloading the goods
	Purchaser

	For international procurement
	Undertake export requirements
	

	
	Undertake import requirements
	

	5. Information to be provided by the Supplier 
	Title of document

	
	Packing lists for cases and their contents

	
	Copy of invoice for the goods

	
	Delivery Note

	
	Test results and maintenance manuals

	For international procurement
	Licences, authorisations and other formalities associated with export of the goods 

	
	Air Waybill or Bill of Lading with associated landing, delivery and forwarding order 

	
	The Bill of Entry endorsed by the importation authority

	
	Customs work sheets, showing tax, duties and surcharges which the law of the country into which the goods are being imported requires the importer to pay

	
	Invoice from the importation clearing agent showing airline fees, landing charges, wharfage and dock dues as applicable

	
	Specify other import documents required by authorised officials. 


All other information NOT pertinent to the above is given in the balance of the Goods Information
C1.2 Contract Data

Part two - Data provided by the Supplier
Completion of the data in full, according to Options chosen, is essential to create a complete contract.

	Clause
	Statement
	Data

	10.1
	The Supplier is (Name):
	

	
	Address
	

	
	Tel No.
	

	
	Fax No.
	

	11.2(8)
	The Goods Information for the Supplier’s design is in:
	

	11.2(11)
	The tendered total of the Prices is
	R 

(in words)

	11.2(12)
	The price schedule is in:
	

	11.2(14)
	The following matters will be included in the Risk Register
	

	25.2
	The restrictions to access for the Supply Manager and Others to work being done for this contract are
	

	30.1
	The delivery date of the goods and services is:
	goods and services 
	delivery date

	
	
	1
	
	

	
	
	2
	
	

	
	
	3
	
	

	31.1
	The programme identified in the Contract Data is contained in:
	

	63.2
	The percentage for overheads and profit added to the Defined Cost is
	      %


Part 2: Pricing Data

NEC3 Supply Contract
	Document reference
	Title
	No of pages

	C2.1
	Pricing assumptions
	2

	C2.2
	The price schedule 
	


C2.1 Pricing assumptions

1. How goods and services are priced and assessed for payment

Clause 11 in NEC3 Supply Contract, (SC3) core clauses states:

	Identified and defined terms
	11

11.2
	(11) The Prices are the amounts stated in the price column of the Price Schedule.  Where a quantity is stated for an item in the Price Schedule, the Price is calculated by multiplying the quantity by the rate.



	
	
	(12) The Price Schedule is the price schedule unless later changed in accordance with this contract.



	Assessing the amount due
	50.2
	The amount due is

· the Price for each lump sum item in the Price Schedule which the Supplier has completed, 
· where a quantity is stated for an item in the Price Schedule, an amount calculated by multiplying the quantity which the Supplier has completed by the rate,

· plus other amounts to be paid to the Supplier,

· less amounts to be paid by or retained from the Supplier.
Any tax which the law requires the Purchaser to pay to the Supplier is included in the amount due.




This confirms that the Supply Contract is a priced contract where the Prices are derived from a list of items of goods and services which can be priced as lump sums or as expected quantities of goods and services multiplied by a rate, or a mix of both.

2. Function of the Price Schedule

Clause 53.1 states: “Information in the Price Schedule is not Goods Information”.  This confirms that instructions to do work or how it is to be done are not included in the Price Schedule but in the Goods Information.  This is further confirmed by Clause 20.1 which states, “The Supplier Provides the Goods and Services in accordance with the Goods Information”. Hence the Supplier does not Provide the Goods and Services in accordance with the Price Schedule.   The Price Schedule is only a pricing document.  

3. Preparing the price schedule
Items in the price schedule may have been inserted by the Purchaser and the tendering supplier should insert any additional items which he considers necessary.  Whichever party provides the items in the price schedule the total of the Prices is assumed to be fully inclusive of everything necessary to Provide the Goods and Services as described at the time of entering into this contract.

It will be assumed that the tendering supplier has 

· Read Pages 8, 11, 12 and Appendix 5 of the SC3 Guidance Notes before preparing the price schedule;
· Included in his Prices and rates for correction of Defects (core clause 43.1) as there is no compensation event for this unless the Defect is due to a Supplier’s risk;

· Spread the cost of doing work he chooses not to list as separate items in the price schedule across other Prices and rates in order to fulfil the obligation to Provide the Goods and Services for the tendered total of the Prices; 
· Understood that there is no adjustment to lump sum prices in the price schedule if the amount, or quantity, of work within that lump sum item later turns out to be different to that which the Supplier estimated at time of tender. The only basis for a change to the Prices is as a result of a compensation event per clause 60.1;
· Understood that the Supplier does not have to allow in his Prices and rates for matters that may arise as a result of a compensation event.
3.1. Format of the price schedule
Entries in the first four columns in the price schedule in section C2.2 are made either by the Purchaser or the tendering supplier. 

If the Supplier is to be paid an amount for the item which is not adjusted if the quantity of work in the item changes, the tendering supplier enters the amount in the Price column only, the Unit, Quantity and Rate columns being left blank.

If the Supplier is to be paid an amount for the item which is the rate for the item multiplied by the quantity completed, the tendering Supplier enters the rate which is then multiplied by the Quantity to produce the Price, which is also entered.

If the Supplier is to be paid an amount for an item proportional to the length of time for which the goods and services are provided, a unit of time is stated in the Unit column and the length of time (as a quantity of the stated units of time) is stated in the Quantity column.

C2.2 the price schedule
	Item nr
	Description
	Unit
	Quantity
	Rate
	Price

	
	
	
	
	
	

	
	
	
	
	
	


	The total of the Prices
	


Part 3: Scope of Work

	Document reference
	Title
	No of pages

	
	This cover page
	1

	C3.1
	Purchaser’s Goods Information
	

	C3.2
	Supplier’s Goods Information
(insert at award stage or delete if not applicable)
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	Total number of pages
	


C3.1: Purchaser’s Goods Information
Contents

23Part 3: Scope of Work


24C3.1: Purchaser’s Goods Information


251
Overview and purpose of the goods and services


252
Specification and description of the goods


252.1
Factory acceptance testing (FAT)


252.2
Other tests and inspections and commissioning in place of use


252.3
Operating manuals and maintenance schedules


253
Supply Requirements


254
Specification of the services to be provided


265
Constraints on how the Supplier Provides the Goods


265.1
Programming constraints


265.2
Work to be done by the Delivery Date


265.3
Constraints at the delivery place and place of use


265.4
Services & other things to be provided by the Purchaser or Supplier


275.5
Management meetings


275.6
Documentation control


275.7
Health and safety risk management


275.8
Environmental constraints and management


275.9
Quality


275.10
Invoicing and payment


275.11
Contract change management


285.12
Provision of bonds and guarantees


285.13
Records of Defined Cost, payments & assessments of compensation events to be kept by the Supplier


286
Procurement


286.1
Subcontracting


286.1.1
Preferred subcontractors


286.1.2
Limitations on subcontracting


286.1.3
Spares and consumables


286.1.4
SD&L requirements


286.1.5
Cataloguing requirements by the Supplier


287
List of drawings


287.1
Drawings issued by the Purchaser


29C3.2
Supplier’s Goods Information




1 Overview and purpose of the goods and services
The scope is for the supply of spares to Medupi Power Station for a period of 60 months on an ‘as-and-when-required’ basis.
2 Specification and description of the goods
2.1 Supply of spares
The Works include the following:
1. The description of the spares and the quantities that the Employer envisages for the duration of the contract is indicated in Table 1.  This value will be used with other estimates to determine the overall contract value. It should be noted that this is just an estimate, and it does not mean that the Employer will definitely consume the spares in the duration of the contract.  These quantities are therefore not fixed, and the Contractor will only supply spares when instructed by a purchase order, from the Employer, to do so.
2. Spares that are not included in the list but fits the profile of the rest of the spares will be supplied as part of the “Miscellaneous spares not specified” portion, as indicated in Table 2 below.
3. Spares that are not catalogued can only be ordered and delivered with an approved ‘Data Capture Form’ (DCF) for that specific spare or assembly.  The Contractor will therefore be required to submit the completed DCF to the Employer’s Maintenance Technician and System Engineer for approval before an order can be placed. The Employer will supply the Contractor with blank DCF’s for population at the commencement of the contract.
4. The spares and components will be supplied to the “goods received” section of the Medupi main store where it will be received by the material management section.  The spares will be delivered with all of the required data books and certificates, where required. 

5. 
Medupi Stores Working Times: Monday – Thursdays:
07h00 – 16h00

                          
Fridays:


07H00 – 12h00

6. A draft QCP shall be submitted withhold and witness points specified, for review by the Employer prior to manufacturing if applicable.

7. If applicable, The Employer shall be given sufficient notice by the Contractor of any witness and hold points identified for adherence in the QCP. These points may be waived by the Employer from time to time depending on technical staff availability. Otherwise, it may be requested that photographic or other evidence be submitted electronically, for review and approval, before continuing with the manufacturing / assembly.

8. Hardcopies as well as electronic copies of Data Books shall be supplied to the Employer with or before the delivery of any new spare where applicable. This Data Book will be used during on site Quality Control checks to do final Quality acceptance of spares delivered. Spares delivered without its required documentation, if applicable, will be rejected. 

9. The Data Book shall contain as a minimum, but shall not be limited to, Datasheets of the components with clear indications of part numbers.

10. Only once the spares have passed the Quality Control checks and are booked into the system can payment be affected.
11. It is the Contractor’s responsibility to ensure that correct spares are delivered.  If the incorrect spares are delivered, the spares will have to be replaced with the correct spares at the Contractor’s cost.  This includes transport and delivery.

12. The Delivery and Transport Costs must be included in the list of Prices quoted.  

13. The following packaging requirements should be adhered to:

a) The Goods are to be packaged in such a manner that it can be transported and stored for an extended period without resulting in damage to the goods. 

b) This includes damage due to moisture ingress, corrosion, vibration from the power station etc.

c) Where lifting gear is utilised to move the goods, the packaging should allow the lifting operation and ensure that the goods are not damaged in any way during the process. 

d) It will also not be necessary to open packaging for any lifting or transport operation.  

e) Where eye bolts are fitted to move the goods, these eye bolts should be fitted such a way that they can be easily removed and replaced with the Employers’ eye bolts, ensuring that the packaging stays intact.

f) Packaging and labelling of the gearboxes should ensure that the spare can be identified without opening the packaging. 

g) Delivery packaging to have the following detail on it as a minimum (removable adhesive sticker if possible):

· Order number,

· A short description of component

· The stock number. 

· Manufacturing date (refurbishment date if applicable)

· Space for adding the installation date.
· The documentation for preservation requirements should be delivered with the component. 

2.2 Warranty
1. All spares shall carry a 24-month warrantee from date of delivery.
2. All spares shall carry a further 12-month warrantee after installation, against all defects. 
3. Any specific requirements to enable the 12-month warrantee shall be brought forward by the Contractor for agreement during negotiations. If witnessing of installation is required, this will be at the Contractor’s own cost.

4. The warranty shall also cover, but not be limited to, minor defects identified.

5. The contractor will bear all cost for warrantee repairs.

2.3 Operating manuals and maintenance schedules
Where applicable; test certificates, material certificate, manuals, General Arrangement (GA) drawing/s, Approved Inspection Authority (AIA) stamp and signature provided as required. All documents must be obtained during or before delivery of goods.

Data capturing forms information must be supplied and must meet an acceptable level.
3 Supply Requirements

The Supply Requirements for this contract are in an Annexure A to the Contract Data provided by the Purchaser. 

4 Specification of the services to be provided

	Delivery of the following 


	Item no.
	KKS
	Short Description
	Additional info


	OEM / Original construction contractor
	OEM Part No / Data Sheet
	SAP Material number
	Unit
	Est Qty

	1
	01XJN10 AA602
	Non Return Valve, Reduced Port, SW Ends, CL800
	1"; Reduced Port, SW Ends, CL800;  ANSI B16.34 ISO15761

Length: 127mm

Carbon Steel class 800
	Bonney Forge
	
	
	each
	2

	2
	01XJN10 AA603
	Fire Shut Off Valve, Threaded NPT Ends
	1"; Female NPT, ANSI B16.34, Inspection & testing according to API 598.  API 607 4th

Edition Fire-Safe Test approved.

Model nr: FLPLT059165010FW

Serial nr: 55446B23770
	Bi-TORQ Valve Automation
	
	
	each
	4

	3
	01XJN10 AA601
	Overfill Protection Valve
	2"; UL2227

1228-2" OP VALVE ASSEMBLY

Drawing nr: 1228-03-20XX
	C&B (CLAY & BAILEY MFG. CO.)
	
	
	each
	2

	4
	01XJN10 AA604
	High Flow Emergency Vent              
	3"; UL – Listed

  Model 0367-03-30HF
	C&B (Clay & Bailey)
	
	
	each
	1

	5
	01XJN10 AA401
	Ball Valve
	B Series Ball Valve 1/2", Full Port, Flanged Ends, CL150; ANSI B16.34 API607 ISO15761

Length: 108 mm

Two-piece, split body, cast steel, side entry design
	Neway
	
	
	each
	2

	6
	01XJN10 AA501
	Ball Valve
	B Series Ball Valve 1"; Full Port, Flanged Ends, CL150;  ANSI B16.34 API607 ISO15761

Length: 127 mm

Two-piece, split body, cast steel, side entry design
	Neway
	
	
	each
	2

	7
	01XJN10 AA201
	Solenoid Valve
	1"
	DanFoss
	
	
	each
	3

	8
	01XJN10 AT001
	Water Separator 
	Model SWK 2000/40/U/M
	Separ Filter
	
	
	each
	3

	9
	01XJN10 AT001
	Water Separator Element
	Element no: 04030
	Separ Filter
	
	
	each
	6

	10
	01XJN10 CL301 – CL305
	Day Tank Float Level Switch
	
	Finetek
	
	
	each
	1

	11
	01XJN10 CL001
	Day Tank Level Transmitter
	
	Endress + Hauser
	Order code:FMP51-1XMT4/0

Ser no: H5001B0112C

Ext Ord code: FMP51-BAACCABAA4AFJ+ AALAZ1
	
	each
	2

	12
	0 0END10 AA301

0 0END10 AA302

0 0END10 AA303

0 0END35 AA301

0 0END35 AA302
	Ball Valve
	Dimension Specification

15NB to ANSI B16.34

Threaded – BSP Female Thread

Material Specification

ASTM A216 Gr. WCB

Additional Requirements

•
Full bore type valves required.
	CONDOR;
	KV-061


	
	each
	2

	13
	0 0ENA10 AA501
	Ball Valve
	Dimension Specification

25NB to ANSI B16.34

Flanged to ASME B16.5 R/F 150 lb

Material Specification

ASTM A216 Gr. WCB

Additional Requirements

· Full bore type valves required.

Fire safe ball valves required.
	CONDOR;
	KV-061


	
	each
	1

	14
	0 0ENA45 AA502
	Ball Valve
	Dimension Specification

25NB to ANSI B16.34

Flanged to ASME B16.5 R/F 150 lb

Material Specification

ASTM A216 Gr. WCB

Additional Requirements

· Full bore type valves required.

Fire safe ball valves required.
	CVT - ENERMECH

PLEIX QUIP


	
	
	each
	1

	15
	0 0ENA10 AA505
0 0ENA45 AA501
	Ball Valve
	Dimension Specification

50NB to ANSI B16.34

Flanged to ASME B16.5 R/F 150 lb

Material Specification

ASTM A216 Gr. WCB

ASTM A315-CF8M (Level gauge isolation valves)

Additional Requirements

· Full bore type valves required.

Fire safe ball valves required.
	CONDOR;
	KV-061


	
	each
	1

	16
	0 0END45 CL501 KA01

0 0END45 CL501 KA02
	Ball Valve
	Dimension Specification

50NB to ANSI B16.34

Flanged to ASME B16.5 R/F 150 lb

Material Specification

ASTM A216 Gr. WCB

ASTM A315-CF8M (Level gauge isolation valves)

Additional Requirements

· Full bore type valves required.

Fire safe ball valves required.
	NEWAY
	NEWAY B Series

(Neway Floating Ball Valve Catalogue)
	
	each
	1

	17
	0 0END10 AA501
0 0END10 AA510
0 0END10 AA515
0 0END45 AA501
	Ball Valve
	Dimension Specification

80NB to ANSI B16.34

Flanged to ASME B16.5 R/F 150 lb

Material Specification

ASTM A216 Gr. WCB

Additional Requirements

· Full bore type valves required.

Fire safe ball valves required.
	CONDOR;
	KV-061


	
	each
	2

	18
	0 0END40 AA504
	Ball Valve
	Dimension Specification

80NB to ANSI B16.34

Flanged to ASME B16.5 R/F 150 lb

Material Specification

ASTM A216 Gr. WCB

Additional Requirements

· Full bore type valves required.

Fire safe ball valves required.
	FZV


	
	
	each
	1

	19
	0 0END40 AA402
	Ball Valve
	Dimension Specification

20NB to ANSI B16.34

Flanged to ASME B16.5 R/F 150 lb

Material Specification

ASTM A216 Gr. WCB
	NEWAY
	
	
	each
	1

	20
	0 0END40 AA401
0 0END40 AA403
0 0END40 AA404
0 0END40 AA405
0 0END40 AA410
0 0END40 AA415
0 0END40 AA420
0 0END40 AA425
0 0END40 AA430
0 0END40 AA440
0 0END40 AA445
0 0END40 AA450
0 0END40 AA455
	Ball Valve
	Dimension Specification

25NB to ANSI B16.34

Flanged to ASME B16.5 R/F 150 lb

Material Specification

ASTM A216 Gr. WCB
	NEWAY
	
	
	each
	4

	21
	0 0END10 AA517
0 0END35 AA501
	Ball Valve
	Dimension Specification

50NB to ANSI B16.34

Flanged to ASME B16.5 R/F 150 lb

Material Specification

ASTM A216 Gr. WCB
	CARILO


	
	
	each
	1

	22
	0 0ENA10 AA503
0 0ENA45 AA503
	Ball Valve
	Dimension Specification

80NB to ANSI B16.34

Flanged to ASME B16.5 R/F 150 lb

Material Specification

ASTM A216 Gr. WCB
	CARILO


	
	
	each
	1

	23
	0 0END40 AA502
0 0END40 AA503
0 0END40 AA505
	Ball Valve
	Dimension Specification

80NB to ANSI B16.34

Flanged to ASME B16.5 R/F 150 lb

Material Specification

ASTM A216 Gr. WCB
	NEWAY


	
	
	each
	1

	24
	0 0END40 AA501
0 0END50 AA505
0 0END50 AA515
0 0END50 AA525
	Ball Valve
	Dimension Specification

80NB to ANSI B16.34

Flanged to ASME B16.5 R/F 150 lb

Material Specification

ASTM A216 Gr. WCB
	BONNEY FORGE


	
	
	each
	1

	25
	0 0END10 AA603
0 0END10 AA604
0 0END40 AA603
0 0END45 AA601

	Ball Valve
	Dimension Specification

80NB to ANSI B16.34

Flanged to ASME B16.5 R/F 150 lb

Material Specification

ASTM A216 Gr. WCB

Additional Requirements

· Full bore type valves required.

· Fire safe ball valves required.

Complete with fusible link actuator.
	CVT - ENERMECH


	PQ Series Actuated Ball Valves

Rotork Safety Actuators Datasheets


	
	each
	1

	26
	0 0ENA10 AA502
	Manual Glove Valve
	Dimension Specification

25NB to ANSI B16.34

Socket to ASME B16.11 - 150 lb

Material Specification

ASTM A216 Gr. WCB
	CVT - ENERMECH

CARILO


	
	
	each
	1

	27
	0 0ENA10 AA401
0 0ENA45 AA401
0 0END31 AA401
	Manual Glove Valve
	Dimension Specification

50NB to ANSI B16.34

Socket to ASME B16.11 - 150 lb

Material Specification

ASTM A216 Gr. WCB
	CVT - ENERMECH

CARILO


	
	
	each
	1

	28
	0 0END10 AA516
0 0END35 AA502
0 1END10 AA501
0 2END10 AA501
0 3END10 AA501
	Manual Butterfly valve
	Dimension Specification

80NB to ANSI B16.34

Wafer to ASME B16.5 R/F 150 lb

Material Specification

ASTM A216 Gr. WCB
	Slim Wafer Type Butterfly Valve
	
	
	each
	2

	29
	0 1END10 AA101
0 2END10 AA101
0 3END10 AA101
0 0END40 AA101
	ELECTRICALLY OPERATED BUTTERFLY VALVES – SLIM WAFER / AUMA
	Dimension Specification

80NB to ANSI B16.34

Wafer to ASME B16.5 R/F150 lb

Material Specification

ASTM A216 Gr. WCB
	SLIM

AUMA
	SLIM:

AUMA


	
	each
	2

	30
	0 0END10 AA605
	NON-RETURN VALVES – PLEIX QUIP TILTED DISC TYPE
	Dimension Specification

50NB to ANSI B16.34

Wafer to ASME B16.5 R/F 150 lb

Material Specification

ASTM A216 Gr. WCB

Additional Requirements

Spring return type discs
	PLEIX QUIP


	
	
	each
	1

	31
	0 0END10 AA602
0 0END20 AA601
	NON-RETURN VALVES – PLEIX QUIP TILTED DISC TYPE
	Dimension Specification

80NB to ANSI B16.34

Wafer to ASME B16.5 R/F 150 lb

Material Specification

ASTM A216 Gr. WCB

Additional Requirements 

Spring return type discs.
	PLEIX QUIP


	
	
	each
	1

	32
	0 0END40 AA601
	NON-RETURN VALVES – PLEIX QUIP TILTED DISC TYPE
	Dimension Specification

80NB to ANSI B16.34

Wafer to ASME B16.5 R/F 150 lb

Material Specification

ASTM A216 Gr. WCB

Additional Requirements 

Spring return type discs.
	AVK


	
	
	each
	1

	33
	0 0END10 AA505
	THREE-WAY PLUG VALVE – AZ VALVE (F-3-W)
	Dimension Specification

80NB to ANSI B16.34

Flanged to ASME B16.5 R/F150 lb

Material Specification

ASTM A216 Gr. WCB

Additional Requirements

· Bottom entry type 3-way valve.

· Full bore type valve.

Two hole, L- port configuration
	
	Storage, Operating & Maintenance Instructions for AZ Plug Valves

Type F3 Standard F-3-W Three Way Plug Valves
	
	each
	1

	34
	0 0END35 CF001
	Flow Meter
	Diesel Supply Flow Meter
	ENDRESS & HAUSER 
	
	
	each
	1

	35
	0 0ENG10 AP001

0 0ENG10 AP001 –M01
	DIESEL FUEL SUPPLY PUMP / MOTOR
	CMG Motor & VIKING Pump
	CMG Motor & VIKING Pump
	Viking Pump Service Manual

CMG Motor & VIKING Pump Data Sheet


	
	each
	1

	36
	0 0END40 AA201
	Solenoid valve
	Dimension Specification

2” threaded to ISO 7-1 Rp 

Material Specification

Stainless Steel 1.4581 Body and FKM Seal

Additional Requirements

220V Normally Closed – Servo Assisted Controlled
	BURKERT


	BURKERT 
 Type 5282 2/2


	
	each
	1

	37
	0 0ENA45 CL501

0 0ENA45 CL301/302


	MAGNETIC LEVEL GAUGES AND SWITCHES
	Dimension Specification

Indicator length (CTC) of 934mm

Process Connection: 50NB 150lb RF Flanges

Material Specification

Float and Chamber: Stainless Steel 316L 

Rail: Aluminium 

Additional Requirements:

2 x Switches :1690 ATEX 220V Bi-Stable Change -over contact


	MAG LEVEL:
	Switches 1690ATEX


[image: image1.emf]ti_ba_switches_en.p df


	
	each
	1

	38
	0 0END10 AB001
	3” Dry Break API Coupling
	
	MANN


	MANN DDCouplings


	
	each
	1

	39
	0 0END10 AB002
	3” Emergency Quick Break Coupling
	
	MANN


	MANN SBCouplings


	
	each
	1

	40
	0 0ENA10 AA601
0 0ENA45 AA601
	Emergency Pressure Relief Vent
	
	Energas


	ENERGAS Protectoseal 


	
	each
	1

	41
	0 0ENA10 AA602
	Emergency Vacuum Relief Vent
	
	Energas


	ENERGAS Protectoseal 


	
	each
	1

	42
	0 0END10 AA601
0 0END35 AA601
0 0END40 AA602
0 0END45 AA602

	
	Thermal Relief Valves

Dimension Specification

20NB x 25NB – 150Lbs

Threaded – BSP Male Thread

Material Specification

SA 351 CF-3M
	EFS / TOSACA
	
	
	each
	4

	43
	0 1END10 AA601
0 2END10 AA601
0 3END10 AA601
	
	Thermal Relief Valves

Dimension Specification

20NB x 25NB – 150Lbs

Threaded – BSP Female Thread

Material Specification

SA 351 CF-3M
	EFS / TOSACA
	
	
	each
	3

	44
	0 0QSA10 AA402
0 0QSA20 AA402
0 0QSA50 AA401
0 0QSB40 AA501
0 0QSB41 AA501
0 0QSB42 AA401
0 0QSB42 AA402
0 0QSB42 AA403
0 0QSB42 AA404
0 0QSB42 AA405


	MANUAL GATE VALVES
	25NB to ANSI B16.34 – 150 lb

Flanged to ANSI B16.5 RF

Material Specification

ASTM A216 Gr. WCB


	BONNEY FORGE (BFE)
	
	
	each
	3

	45
	0 0QSA10 AA401
0 0QSA20 AA401


	MANUAL GATE VALVES
	Dimension Specification

50NB to ANSI B16.34, - 150 lb

Flanged to ANSI B16.5 RF

Material Specification

ASTM A216 Gr. WCB


	BONNEY FORGE (BFE)
	
	
	each
	1

	46
	0 0QSB42 AA301

0 0QSB42 AA302

0 0QSB42 AA303

0 0QSB42 AA304

0 0QSA60 AA301

0 0QSA60 AA302

0 0QSA60 AA303


	MANUAL BALL VALVES – 
	15NB PN10

Kingdom KV-030

3 piece  ¼ turn  ball manual ball valves, lever operated

Steel casting

Internals – S’/Steel

1000 WOG

Economical type

Full port

Blow-out proof stem

Locking device

Threaded bores BSP SANS 1109/

ISO 7-1


ANSI 16.34

ASTM A351-CF8M

A216 Gr. WCB

316/PTFE


	KINGDOM / CONDOR 
	
	
	each
	3

	47
	0 0QSA30 AA501

0 0QSA60 AA501

0 0QSA61 AA502

0 0QSA70 AA501


	MANUAL BALL VALVES 
	50NB PN10

Kingdom KV-030

3 piece  ¼ turn  ball manual ball valves, lever operated

Steel casting

Internals – S’/Steel

1000 WOG

Economical type

Full port

Blow-out proof stem

Locking device

Threaded bores BSP SANS 1109/

ISO 7-1


ANSI 16.34

ASTM A351-CF8M

A216 Gr. WCB

316/PTFE


	KINGDOM / CONDOR
	
	
	each
	2

	48
	0 0QSA50 AA501
0 0QSA50 AA502
0 0QSB40 AA502
0 0QSB41 AA502
0 0QSB42 AA501
0 0QSB42 AA503


	MANUAL BALL VALVES
	80NB to ANSI B16.34, - 150 lb

Flanged to ANSI B16.5 RF

Material Specification

ASTM A216 Gr. WCB

Fire Safe – API 608

Anti-static devices fitted

BOP stem

ASME 16.10 - Face-to-face

Inspection & Testing to API 598


	KINGDOM / CONDOR
	
	
	each
	3

	49
	0 0QSB42 AA601
0 0QSB42 AA602
	Thermal Relief Valve
	Thermal Relief Valves

Dimension Specification

20NB x 25NB – PN10/150Lbs

Type 1 / size 1 / Head ‘C’ 

Threaded – BSP Female 

Material Specification

ASME B1.20.1

ASTM A216 Gr. WCB
	Neizgodka/Tosaca.
	
	
	each
	1

	50
	0 0QSA30 AA602
	ACTUATED BALL VALVES
	Actuated Shut-off Ball Valve, 

2-Piece valve with ‘Fusible Link’

Dimension Specification

80NB to ANSI B16.34 - 150 lb

Flanged to ANSI B16.5 RF

Material Specification

ASTM A216 Gr. WCB

ASME 16.10 - Face-to-face

API - 607

Glass filled Teflon seats

Teflon packing

BS Fire Safe – API 6755

Anti-static devices 

BOP stem

Inspection & Testing to API 598
	ROTORK (Type FS-Fire)

PQ Series
	
	
	each
	1

	51
	0 0QSB42 AA502
	MANUAL 3-WAY PLUG VALVE
	AZ F3 STD, Non-lubricated plug, T4 Port Plug

Body - ASTM A216 Gr. WCB

Cover & Plug CF8M/1.4408

I&T to API598

Inspection Cert’ –

DIN EN 102043.1

Dimension Specification

80NB to ANSI B16.34, - 150 lb

Flanged to ANSI B16.5 RF

Material Specification

ASTM A216 Gr. WCB
	VALVETECH / GC BAARS


	
	
	each
	1

	52
	0 0QSA30 AA601


	NRV
	Dimension Specification

80NB to ANSI B16.34 – 150 lb

Flanged to ANSI B16.5 RF

Bolted bonnet, metal disc, welded-in seat-ring, full bore

Material Specification

ASTM A216 Gr. WCB

Cast steel (7.150), full-bore, swing-type
	
	
	
	each
	1

	53
	0 0QSA42 AP001

0 0QSA42 AP001

MO1
	Gear Pump & Motor
	Pump (PDP) -Type Viking, LQ4124A –RV (gear pump)

Duty Point

7,5 litres/s at 200 kPa

Dimension Specification

2” NPT female Screwed Suction and Discharge Nozzles

Integral relief valve (set at 300kpa)

Test pressure 10 Bar 

Motor – PPA 132M-4, 7.5 kW

400 Volt / 4 Pole / IP66

Material Specification

Carbon Steel
	CMG Motor & VIKING Pump
	
	
	each
	1

	54
	0 0QSA30 AB001
	Camlock Quick Connect Coupling
	Hose connection for ‘receiving’ oil from Mobile Trolley tank

Male Fitting

Dimension Specification

50NB

Material Specification

Stainless Steel (304L)


	Hose Solutions
	
	
	each
	1

	55
	0 0QSA61 AB001
	Camlock Quick Connect Coupling


	Hose connection, Mobile Trolley outlet for ‘transferring’ dirty oil from Trolley tank 

Female Fitting

Dimension Specification

50NB

Material Specification

Stainless Steel (304L)


	Hose Solutions
	
	
	each
	1

	56
	0 0QSA60 AB001
	Camlock Quick Connect Coupling


	Hose connection, Mobile Trolley inlet for ‘transferring’ dirty oil to trolley tank

Female Fitting

Dimension Specification

50NB

Material Specification

Stainless Steel (304L)


	Hose Solutions
	
	
	each
	1

	57
	0 0QSA42 AB001
	Breakaway Coupling’
	MannTek 3” (80NB) Industrial Safety ‘Breakaway Coupling’ : 

N461D1101-01 IND 

Weight = 5.5kg

Dimension Specification

80NB – 150 lb (10Bar)

Flanged to ANSI B16.5 RF

Material Specification

Carbon Steel
	JACHRIS
	
	
	each
	1

	58
	0 0QSA42 AB002


	Tanker Adaptor Coupling
	Male NATO STANAG Road Tanker 3” (80NB) Adapter Coupling (male)  

T461D1101-1 

Dimension Specification

80NB – 150 lb

Flanged to ANSI B16.5 RF

Material Specification

Carbon Steel
	JACHRIS
	
	
	each
	1

	59
	0 0QSA10 CL501

0 0QSA20 CL501
	Oil storage tank sight glass
	SIGHT-GLASS - fluid level indicators for main oil storage tanks i.e. two flanged units with inter-grated gauge cocks at upper & lower ends of sight-glass.

Dimension Specification

50NB  PN10 

(2”) -150 lb

ASME/ANSI B16.5

ATSM A106 Gr. B 

Drawing No – 2.040 / 149A

Type; Flanged units (4 off) with ¼ turn cock valves with associated sight-glass compression (sealing) fittings

Sight-glass length - centre-to centre = 1350.00mm

Material Specification

ASTM A106 Gr.B

ASTM A105
	MACSTEEL FLUID CONTROL

(Manufacturer – IGEMA)


	
	
	each
	1

	60
	0 0QSB42 AT001
	BASKET STRAINER
	PUMPTRON ‘PRO-FLO’ strainer with bolted bonnet, ductile iron & top-entry. 

3.2mm ‘Basket’ perforation holes x 5.25mm staggered pitch by 0.9mm thickness basket S/S

½” NPT drain 

Flanged to ANSI B16.5

ANSI 150 RF 

SABS 936, Gr SG42

Material Specification

Ductile iron, Stainless Steel basket


	GORMAN-RUPP
	
	
	each
	1

	61
	0 0QSA60 AP001 –M01


	GEAR PUMP / MOTOR
	POLLARD PUMP & MOTOR

Type; MPLN 40 – ‘Mtec’- “U” Blade

Duty Point

1 litre/s at 300 kPa, 1,1 Kw motor, with ‘integral’ Pressure Relief Valve & Mechanical seal

Std operating pressure = 5 bar

Std operating temperature = 

-20 to 150°C

Maximum hard particle size 8mm.

Material Specification

Cast Iron


	
	
	
	each
	1

	62
	0 0QSA60 AA301
0 0QSA60 AA302
0 0QSA61 AA303
	MANUAL BALL VALVE
	Dimension Specification

15NB to ANSI B16.34 – 150 lb

Flanged to ANSI B16.5

Material Specification

ASTM A216 Gr. WCB

“3-Piece”, 15mm screwed/threaded-ends NPT, PTFE seats, blow-out Proof-Stem.
	HAITIMA
	
	
	each
	1

	63
	0 0QSA60 AA501
0 0QSA61 AA502
0 0QSA70 AA501
	MANUAL BALL VALVE
	Dimension Specification

50NB to ANSI B16.34 – 150 lb

Flanged to ANSI B16.5

Material Specification

ASTM A216 Gr. WCB

“2-Piece” 50mm Flanged End Ball Valve 2020”/Full-port, PTFE seats & BOP stem.

Test to API 598  
	HAITIMA
	
	
	each
	1

	64
	0 0QSA61 AA501
0 0QSA61 AA502
	MANUAL 3-WAY PLUG VALVES
	Dimension Specification

50NB Flanged to ANSI B16.5

Material Specification

ASTM A216 Gr. WCB

AZ, 3-Way Plug Valve 2058L”

L-PORT, Threaded-ends, regular bore & blow-out proof stem. Stem packing PTFE, seats 15% glass-fibre/fill PTFE  
	AZ
	
	
	each
	1

	65
	0 0QSA60 AT001
	Strainer
	Dimension Specification

50NB PN10

Flanged to ANSI B16.5 – 150 lb

Threaded BS21 

Material Specification

Cast Iron

Type #400 “Y’ Strainer
	Vacuum Fluid & Technology (VFT)
	
	
	each
	1

	66
	0 0QSA60 CP501

0 0QSA60 CP502

0 0QSA61 CP501
	PRESSURE GAUGES
	Dimension Specification

WIKA – Bourdon type (1000kpa)

Material Specification

Stainless Steel case with liquid filling

Model type – 213.53

Design – EN837-1

Connection - Parallel thread sealing – EN837-1-7.3
	WIKA
	
	
	each
	1


5 The Supplier Provides the Goods

5.1 Programming constraints 

The Supplier to provide the plan (as per clause 31.2) of the goods after receiving the task order. See process below:
5.2 Work to be done by the Delivery Date

No incorrect, damaged or faulty spares will be accepted. All spares will be inspected before and after offloading. Where testing is required, the test will be done during delivery. All required manuals and test certificates must be available during delivery. 

5.3 Constraints at the delivery place and place of use

The Supplier shall adhere to Eskom speed limit of 40 km/h while driving on site. The preferred delivery times are Monday to Thursday between 07:00-16:00 and Friday between 07:00-12:00. However, for urgent delivery, the Supplier will communicate with the Supply Manager to agree on the time and date of delivery. 

The Supplier shall adhere to Eskom Life Saving rules

5.4 Services & other things to be provided by the Purchaser or Supplier
The Purchaser will provide the overhead cranes and forklift during offloading of the goods. The Purchaser will also provide the operator for both machines. 

5.5 Management meetings

Meetings of a specialist nature may be convened as specified elsewhere in this Goods Information or if not so specified by persons and at times and locations to suit the Parties, the nature and the progress of the manufacture of the goods.  Records of these meetings shall be submitted to the Supply Manager by the person convening the meeting within five days of the meeting.  

All meetings shall be recorded using minutes or a register prepared and circulated by the person who convened the meeting.   Such minutes or register shall not be used for the purpose of confirming actions or instructions under the contract as these shall be done separately by the person identified in the conditions of contract to carry out such actions or instructions.  

5.6 Documentation control

Contractual communication can be done though emails. For urgent request, both Parties can use telephone as form of communication, however it should be confirmed by email. 

5.7 Health and safety risk management

The Supplier shall comply with the health and safety requirements as per OHSAct 85 of 1993 
Medupi Power Station responsibility and commitment is to ensure a safe working environment

is in line with its Safety, Health, Environmental, and Quality (SHEQ) Policy and applicable

legislative obligations. This OHS specification is Medupi power station minimum requirements

which are required to be met for the duration of the contract period by appointed contractor

and, where required, the delivery organisation. Appointed Contractor is expected to develop

an OHS plan that meets these requirements as well as all the relevant applicable legislation

that they conform to. Medupi Power Station in no way assumes the contractor’s legal

responsibilities and liabilities. Appointed Contractor is and remains accountable for the quality

and execution of their health and safety programme for their employees and appointed

contractor employees. This OHS specification reflects minimum requirements and should not

be construed as all-encompassing.

Section 37(2) (Legal) Agreement

A section 37(2) agreement must be signed between Eskom and the main contractor at the

time of submitting the safety file. The main contractor must ensure that a section 37(2)

agreement is compiled between the main contractor and all their appointed contractors for the

contract. The original copy of the section 37(2) agreement must be retained by the contractor,

and a copy must be retained by the Contract Manager. A copy of all the agreements must

form part of the respective contractor’s OHS file.

The Appointed contractor shall before commencement of the project ensure that all their

employees are familiar with the relevant Eskom Medupi Power Station OHS documentation

that is applicable to Supply and Delivery of Personal Protective Equipment contract.

Eskom Life-saving Rules

1. Eskom places a high value on health and safety and urges every organization that undertakes work for Eskom to do the same.

2. Eskom has developed five life-saving guidelines that will apply to all Eskom Medupi Power Station employees, agents, consultants, and contractors. Any Eskom employee or employee of a Main Contractor or appointed contractor who fails to follow these rules would be deemed a serious violation. These rules are in place to protect any employee, labour broker, or contractor working from significant injury or death.

3. If any contractual work (including delivery of any product) is to be undertaken on Eskom Medupi Power Station premises, the rules shall be obeyed by any contractor and their employees.

4. Eskom Medupi Power station will take a zero-tolerance approach to these rules.

Noncompliance to Life-saving rules is regarded serious misconduct and will result in serious disciplinary action, which may include dismissal
5.8 Environmental constraints and management

The Supplier shall comply and conform to the following:

1. Environmental Requirements for contractors/suppliers working at Eskom Medupi Power Station

2. Eskom Medupi Power Station Operation Environmental Management Plan

3. Environmental legal and other requirements.
4. Eskom’s environmental standards, policies, and procedures where applicable.
5. Pledge to inform all staff of their role in managing environmental impacts on site.
6. Be aware that incidents must be reported within 24 hours of occurrence.
7. Pledge to always implement best practice on site during the contract.
8. Pledge that all non-conformances issued to us will be addressed promptly.
9. Commit to comply to the waste management hierarchy and Medupi waste management practices
5.9 Quality

The Supplier shall submit the following documents within 30 days or as per stated timeline after the contract date, prior to the commencement of work, for acceptance by Eskom:

· The supplier shall complete a QCP before contract award. This shall be reviewed and signed off by Eskom within 30 days or as per stated timeline after contract award.

· The supplier shall complete a quality control plan and ITP(s) for review and acceptance by Eskom prior to the commencement of any work, inclusive of subcontracted work, within 30 days or as per stated timeline after contract award.

· The sub-supplier QCP/ ITP shall be submitted for review and comment by the supplier and by Eskom within 30 days or as per stated timeline after the award of the tender. All supplier and Eskom comments shall be resolved prior to commencing work.

· The equipment lists and an indication of pressurised components and systems.
During the contract execution phase, suppliers shall be monitored by Eskom for performance on quality-related aspects.

The outcomes of such monitoring will enable Eskom to take any appropriate actions pertaining to the supplier.

The monitoring shall be carried out periodically by Eskom or at predetermined intervals during the execution of a contract using agreed key performance indicators. The monitored key performance areas include the following:

· CQP and QCP /ITP

· Delivery

· Design

· Cost

· Management system

Subsequent key performance indicators associated with these areas will include the following:

· Nonconformity monitoring

· Audit and assessment evaluation scoring

· Management system compliance and accreditation

· Achievement of delivery targets as per contractual agreements

· Process improvements

Correction and corrective action response and closure
5.10 Invoicing and payment
Within one week of receiving a payment certificate from the Supply Manager in terms of core clause 51.1, the Supplier provides the Purchaser with a tax invoice showing the amount due for payment equal to that stated in the Supply Manager’s certificate.  
The Supplier shall address the tax invoice to Purchaser and include on each invoice the following information:

· Name and address of the Supplier and the Supply Manager; 

· The contract number and title;

· Supplier’s VAT registration number;

· The Purchaser’s VAT registration number which is 4740101508.
· Description of goods and services provided for each item invoiced based on the Price Schedule;

· Total amount invoiced excluding VAT, the VAT and the invoiced amount including VAT;

· Goods Receipt(GR) and Purchase Order(PO) number

Note: The Supplier shall not submit tax invoice without GR and PO number
Procedure for invoice submission and payment

· All Electronic invoices must be sent in PDF format only. 

· An Invoice that was printed and then scanned to PDF by the Vendor is not acceptable as this is not an original tax invoice by SARS definition but a copy.

· The following wording needs to appear on the invoice: “Your invoice is encrypted in order to comply with SARS requirements that invoices, and statements sent electronically are tamperproof.” 

· All queries and follow up on invoice payments should made by contacting the FSS Contact Centre:   Tel: 011 800 5060 or email:fss@eskom.co.za

5.11 Contract change management 
The Purchaser will provide a standard form for contract communications. Forms for compensation event, instructions, risk register, early warning, notifications

5.12 Provision of bonds and guarantees

The form in which a bond or guarantee required by the conditions of contract (if any) is to be provided by the Supplier is given in Part 1 Agreements and Contract Data, document C1.3, Sureties.  

The Purchaser may withhold payment of amounts due to the Supplier until the bond or guarantee required in terms of this contract has been received and accepted by the person notified to the Supplier by the Supply Manager to receive and accept such bond or guarantee.  Such withholding of payment due to the Supplier does not affect the Purchaser’s right to termination stated in this contract. 

5.13 Records of Defined Cost, payments & assessments of compensation events to be kept by the Supplier
The Supplier will prepare the assessment of compensation event and the Purchaser must review before accepting. Both parties keep records of the assessment for a period of 12 months after the contract has expired. The compensation event prices should be as Price List of the contract.

6 Procurement
6.1 Subcontracting
6.1.1 Preferred subcontractors

The Supplier has full responsibility of Providing the Goods whether subcontracting or not

6.1.2 Limitations on subcontracting

The Supplier encourage to subcontract 30% minimum of the contract value to the local suppliers around Medupi Power Station or Lephalale area.

6.1.3 Spares and consumables
The Purchaser may instruct the Supplier to deliver part of the spares as the need arise due to plant condition

6.1.4 SD&L requirements
Skills development is designed to benefit the currently unemployed graduates or those fresh from

school: further education and training on campuses and universities.

The composition of these candidates must be representative of the population demographics of

South Africa. Note that these targets for skills development candidates categorically exclude Eskom

employees but only registered learners
6.1.5 Cataloguing requirements by the Supplier
When spares are procured, the spare specifications are captured on Data Capturing Forms (DCF’s) and then to SAP materials management. The Supplier will be required to complete the DCF where Eskom does not have information

7 List of drawings/documents
7.1 Drawings/documents issued by the Purchaser
This is the list of drawings/documents issued by the Purchaser at or before the Contract Date and which apply to this contract.  

	Drawing/ Document number
	Revision
	Title

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	


C3.2
Supplier’s Goods Information

	This section of the Goods Information will always be contract specific depending on the nature of the goods and services.

It is most likely to be required for supply contracts where the tendering supplier will have proposed specifications and schedules for the goods and services, which once accepted by the Purchaser prior to award of contract now become obligations of the Supplier per core clause 20.1.




This section could also be compiled as a separate file.



� This total is required by the Purchaser for budgeting purposes only.  Actual amounts due will be assessed in terms of the conditions of contract.


� Available from Engineering Contract Strategies Tel 011 803 3008 Fax 086 539 1902, www.ecs.co.za.
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Technical data switches 


1. General Table


Switch 1690 1690ATEX LMS-A LMS-A-EExd MS09K MS10 EExd 
Case synthetic synthetic Al Si 12 Al Si 12 synthetic Aluminium 
Contact 
Function 


bistable 
change-over 


contact 


bistable 
change-over 


contact 


bistable 
change-over 


contact** 


bistable 
change-over 


contact 


break- or make-
contact, 


change-over 
contact 


break- or make-
contact, change-


over contact 


Dimensions 20x15x80 20x15x80 65x65x40 ∅138x80 110x75x50 120x120x110 
230 VAC 230 VAC 12-250 VAC 220 VAC 250 VAC 250 VAC 


0,8 A 0,4 A 1,5 A 1,5 A 10 A 10 A 
Breaking on 
rupturing 
capacity 60 VA 30 VA 80 VA 80 VA --- --- 
Protective 
System 


IP65 IP65 IP65 
DIN40050 


IP65 DIN40050 IP65 DIN40050 IP65 DIN40050 


Option IP67 
DIN40050 


IP67 
DIN40050 


--- --- --- ---


Switch-
hysteresis 


15 mm 15 mm 8-12 mm 8-12 mm --- --- 


Medium-
temperature 


max. 130°C max. 130°C max. 200°C* max. 200°C* max. 100°C max. 200°C 


EEx-
protection 


--- EEx d II CT6 --- EEx d II CT6 --- EEx d II CT6 


Connection --- --- PG9 4 connection 
(¾” NPT) 


PG11 ¾” NPT


Electric connection with 3-channel plug and earth. 
For all switches valid the international standard EN 60529. 
* Type LMS-AH with heat-protection-execution through a max. temperature of 400°C.
** available with gold contact.


2. NI Ex NU-Switch


Inherent safety EEx-switch, on request with define error 
message. 


Supply voltage: 8 V DC 
Max. temperature: 60°C 


Contact-
transmitter 


Cable connection at 
the case: 


PG11 


Supply voltage: 220 V +15 % (45-60 Hz) 
Power consumption: Ca. 1,5 V 
Open circuit voltage: 8 V DC 
Admit charge: 4 A/250 V/ 250 VA 


Section 
switch 
appliance 


Admit temperature: -20...+60°C


3. Switch diagrams


Type Diagram 
1690 


bistable change-
over contact 


LMS-A 


bistable change-
over contact 


LMS-AH 


bistable change-
over contact 



Wayne.VanDerMerwe

Rectangle
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Technical data switches 


Switch LMS-A Switch LMS-AH 


Switch 1690 / 1690ATEX Switch MS09 K 


Switch MS10 EExd Switch LMS-A-EExd 
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Technical data switches 


Switch NI Ex NJ 


Switch NI-Ex-NJ 
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Contact NJ-EX 


The contact NJ-EX is an inductive contact NJ 1.5-6.5 N, kontex System,  
Protective system EEx ia IIC T6. 


Function 


Actuation is provided by the magnet installed in the 
float. The follow magnet system of the contact 
maker moves the switching disk, which serves for 
releasing the contact between two small 
inductances of the slotted initiator and thereby 
varies the attenuation of the resonant circuit. 


Technical data 


Electrical connection : 8 V DC 
Temp./ambient temp. : 60°C 
Cable connections : M20x1,5 


Switch relay 


KFA6-SR2-Ex1.W : for 1 inductive contact EEx ia IIC 
KFA6-SR2-Ex2.W : for 2 inductive contacts EEx ia IIC 










