P.02537/ Zoe/Hydro/Elec-Spec: ELECTRICAL SYSTEM SPECIFICATION Rev 01

DESIGN, MANUFACTURE, SUPPLY, DELIVERY, INSTALLATION, TEST, COMMISSION, OPERATE AND MAINTENANCE OF ELECTRICAL EQUIPMENT FOR A HYDRO POWER GENERATION PLANT AT ZOEKFONTEIN CONTROL WORKS

Record of Revisions

Rev Date					Details of Revision

01        	   				Design document for tender purposes

Contents

1.	ELECTRICAL SCOPE OF WORK	5

2.	ELECTRICAL DESIGN	6

3.	CONSTRUCTION SUPERVISION	22

4.	MEDIUM VOLTAGE SWITCHGEAR	25

5.	PROTECTION RELAY SPECIFICATIONS	62

6.	ADDITIONAL MEDIUM VOLTAGE SWITCHGEAR TIER AT ZUIKERBOSCH ENGINE ROOM 4A/4B	72

7.	MEDIUM VOLTAGE SWITCH ROOM REQUIREMENTS	73

8.	NEUTRAL EARTHING COMPENSATORS	75

9.	TURBINE GENERATOR, EXCITATION AND SYCHRONISATION SYSTEMS	78

10.	400V DISTRIBUTION SWITCHBOARDS	79

11.	400 V DISTRIBUTION SWITCHBOARD ROOM REQUIREMENTS	98

12.	DISTRIBUTION TRANSFORMERS	99

13.	TRANSFORMER BAY REQUIREMENTS	104

14.	110 V DC BATTERY CHARGERS AND STATIONARY BATTERIES	105

15.	BATTERY ROOM REQUIREMENTS	109

16.	TURBINE AND GENERATOR AUXILIARIES PANEL	112

17.	COOLING WATER PUMP LOCAL CONTROL PANELS	113

18.	VALVE AND MOTOR ISOLATING PANELS	116

19.	SUMP PUMP CONTROL PANELS	117

20.	FLOOD ALARM PANEL, SIREN AND LEVEL SWITCHES	119

21.	TURBINE BUILDING AND SUBSTATIONS CABLE INSTALLATION REQUIREMENTS	121

22.	RETICULATION TO ZUIKERBOSCH PUMPING STATION	125

23.	ZUIKERBOSCH SITE RETICULATION	129

24.	MIMIC DISPLAY PANELS, METERING AND POWER QUALITY	129

25.	UNINTERRUPTIBLE POWER SUPPLIES (UPS) AND BATTERY SYSTEMS	135

26.	EMERGENCY STANDBY DIESEL GENERATOR	137

27.	SMALL POWER AND LIGHTING INSTALLATIONS	147

28.	LIGHTNING PROTECTION AND EARTHING	151

29.	AREA LIGHTING	152

30.	OPERATING AND MAINTENANCE MANUALS	153

31.	TOOLS AND SPARES	155

32.	QUALITY ASSURANCE REQUIREMENTS	157

33.	ELECTRICAL BOQ FOR CONSIDERATION BY THE CONTRACT (NOT EXHAUSTIVE)	157

34.	APPLICABLE DRAWINGS	158

35.	APPLICABLE STANDARDS	159

# ELECTRICAL SCOPE OF WORK

  - General requirements

The Contractor scope shall be for the provision of all the labour, materials and services and also be responsible for the design, supply, delivery, offloading, installation, testing commissioning, operating and maintenance of all electrical equipment as per the tender document, typical Single Line Diagrams, schematic diagrams, P&IDs, relevant standards and Rand Water specifications.

  - Electrical Scope of Work

The proposed scope of work entails the following as minimum:

    - Turbine Generator

    - Excitation and Synchronisation Systems for Generator

    - Medium Voltage Switchgear at Zoekfontein Control Works

    - 110 VDC Batteries and Battery Chargers

    - Low Voltage Distribution Boards

    - Auxiliaries Distribution Board for the turbine generator set

    - Cooling Water Control Panel if required

    - Valve Distribution Boards where required

    - Valve and Motor Isolation Panels

    - Mimic Panels at Zoekfontein and Zuikerbosch (Forebay)

    - Flood Alarm Panel if required.

    - Sump Pump Control panels

    - Energy Metering

    - Step up Power Transformer(s)

    - Reticulation from Zoekfontein to Zuikerbosch pumping station via underground cable and/or overhead line

    - Step down Transformer (s) at Zuikerbosch pumping station (Forebay) with synchronisation equipment to connect to existing Zuikerbosch electrical infrastructure

    - Medium Voltage Switchgear at Zuikerbosch (Forebay). Note: Existing Medium Voltage equipment at Zuikerbosch is 11kV.

    - Tie-in to Zuikerbosch 11kV electrical network at Engine Room 4A/4B with 11kV cable

    - Cable trenching and cable ducts as required

    - Neutral Earthing Compensator Resistive Transformer (NECRT)(s) at the step up and step down substations

    - Uninterruptable Power Supplies (UPS)

    - Standby Generators at Zoekfontein and Zuikerbosch (Forebay)

    - Interface of electrical infrastructure to all buildings with regard room requirements, sizes, volumes, cable ducts, cable access etc

    - Earthing and lightning protection at Zoekfontein and Zuikerbosch

    - Fire detection, monitoring and protection where required

    - Small power and lighting installations for all new buildings/structures, valve chambers etc

    - Area lighting where new buildings/structures are being built.

    - Submit Electrical returnable schedule as indicated in the applicable Rand Water Standards, e.g. MV & LV switchgear, etc.

    - Spares

    - As built documentation.

    - Operating and Maintenance manuals

# ELECTRICAL DESIGN

The Contractor shall execute the electrical design requirements as follows:

  - Preparation and compiling a design philosophy and calculations work package for main items as set out in the contractor’s Bill of Quantities, Detail Engineering Package Deliverables Document which are in line with Rand Water design criteria, Rand Water typical design drawings, Rand Water specifications, legal requirements and national and international specifications (SANS/IEC/IEEE). The contractor shall allow for integration with responsible Rand Water Design Office personnel and applicable vendors of equipment and submit a draft detail design to be presented to Rand Water before the final philosophy and design document is submitted for verification and record keeping before manufacturing by appointed vendors of the equipment can commence.

  - Preparation of compiling all required detail design drawings and schedules, suitable to be issued for the construction of equipment and installations as set out in the contractor’s Bill of Quantities, Detail Engineering Package Deliverables Document, in line with Rand Water design criteria, Rand Water typical design drawings, Rand Water specifications, legal requirements and national and international specifications (SANS/IEC/IEEE). The contractor shall allow for integration with responsible Rand Water Design Office personnel and applicable vendors of equipment and submit a draft detail design to be presented to Rand Water before the final philosophy and design document is submitted for verification and record keeping before manufacturing by appointed vendors of the equipment can commence.

  - Prepare a detailed drawing and schedule register indicating the drawing No, drawing title description and revision No starting with Revision A and progressing alphabetically for subsequent submissions.

  - Select vendors and manufacturers to finalise detail designs for construction. Update typical design documents and generate new design documents were required to incorporate vendor specific details in these documents. Vendor selected equipment shall comply with Rand Water design criteria, Rand Water generic design drawings, Rand Water specifications, legal requirements and national and international specifications (SANS/IEC/IEEE).

  - Design drawings shall be in the Rand Water approved drawing templates for the drawing size. Design drawings shall incorporate the following on the template of the drawing as a minimum:

    - Rand Water drawing number which shall be different to any tender drawing number. New drawing numbers are to be obtained from the Rand Water drawing office or Technical Information Centre.

    - Station Name and Plant: Zoekfontein Control Works Hydro Power plant

    - Rand Water Contract Number

    - Project SAP No and Network Number

    - Contractors Logo

    - Contractors Name and Address, Company Registration Number

    - Contractors Contract Number

    - Contractors Drawing Number

    - Name and ECSA Registration number of the Company’s design engineer who will approve the drawings. The full name and ECSA number of the engineer shall be clearly legible on each drawing. As Rand Water only accepts drawings.

  - Submit design documents in pdf and AUTOCAD drawing format to Rand Water for verification together with the drawing and schedule register, and a transmittal note for signature by the Rand Water project manager, clearly indicating the documents submitted. The Rand Water Lead Design Engineer shall also receive the electronic versions of the above documents at the same time as submission to the Project Manager. Any submissions without an official transmittal note and an update drawing and schedule register and the correct updated Revision number will not be accepted.

  - Receive comments or acceptance of design documents from Rand Water.

  - Update design documents as required by Rand Water.

  - Drawings or schedules accepted by Rand Water will be returned to the Rand Water Project Manager together with the Rand Water Design Review Comments Document.

  - Re submit documents updated complete with new Revision No e g B as required. Documents that are not rigorously checked and with repeat errors will be referred back in totality to the Contractor for proper checking. This will not be accepted as a delay in the project as far as design approval is concerned or for extensions of time.

  - Accepted drawings and schedules will be taken to Revision 0 status, printed in hard copy, stamped “For Construction”, signed by the Contractors ECSA registered design engineer and signed as accepted by the Rand Water Lead Engineer.

  - Revisions during construction will be taken to the next revision e g Revision 0A together with revision comments and follow the same process as in Clause 2.11 above.

  - A detailed CV of the Contractors’ ECSA registered design engineer together with his/her registration certificate shall be submitted at the time of tendering

  - Detail Electrical Engineering Design Package Deliverables.

The Contractor shall provide the following design deliverables, which include reports, calculations, drawings and schedules:

|  | #### Medium Voltage Switchgear |
| --- | --- |
|  | Final MV Switchgear design basis, requirements and equipment specification as per SANS IEC 62271 |
|  | Power system desktop study on proprietary software to determine the switchboard short circuit and service ratings. A final report with calculation results and the actual model in the primary software shall be submitted. The ETAP software package is preferred. |
|  | Recommended protection settings for overcurrent, earth fault, over and under voltage and negative sequence current for each distribution and generator feeder |
|  | Final MV Switchgear interface with PLC and SCADA system drawings |
|  | Final MV Switchgear interface with the Rand Water on-line billing metering and power quality systems, drawings |
|  | Final MV Switchgear Single Line Diagrams |
|  | Final MV Switchgear Parts List and Full Construction Schedule e g paint colours, specification, wiring, lamp colours etc |
|  | Final MV Switchgear General Arrangements showing all compartment, foot prints, etc. |
|  | Final MV Switchgear Schematic and Wiring Diagrams of each circuit including detailed PLC/SCADA Interface |
|  | Final MV Switchgear Individual Tier LV Door Layout |
|  | Final MV Switchgear Individual Tier LV Chassis Layout |
|  | Final MV Switchgear Individual Rear Layout showing full details of cable and current transformer chambers, gland plate, core balance current transformers, cable clamping and terminal strip arrangements |
|  | Final MV Switchgear Cross Sectional Layout showing full details of cable and current transformer, bus bar, instrument and circuit breaker chambers, including MV connections to Voltage Transformers |
|  | Final MV Switchgear Detailed Internal Arc Detection System Layout showing full details of detectors in cable and current transformer, bus bar, voltage transformer and circuit breaker chambers |
|  | Final MV Switchgear Tier dimensioned footprint showing power and control cable entry points |
|  | Final MV Switchgear Tier mounting and installation detail requirements |
|  | Final MV Switchgear detailed Connection Diagram to each protection relay with relay terminal numbers and wire numbers connected to the terminals |
|  | Final MV Switchgear Protection Relay Configuration and Settings Files including ladder logic programs for each relay in hard copy and electronic copy format |
|  | Final MV Switchgear Wiring Diagrams of each circuit breaker truck |
|  | MV Switchgear Schematic and Wiring Diagrams of bus wiring for 110 V AC. Each pane must have own dedicated DC feeder/ supply |
|  | Final Terminal strip layouts complete with wire numbers and terminal numbers for all terminal strips |
|  | MV Switchgear Diagrams showing the final relay front panel annunciation in hard copy and electronic copy format |
|  | MV Switchgear WKS numbering details |
|  | MV Switchgear labels per circuit |
|  | Stationary Battery Charger and Battery Systems |
|  | Battery capacity sizing complete with design calculations and assumptions |
|  | Battery charger sizing and specification complete with design calculations and assumptions |
|  | Battery data sheet with technical data and performance data (constant current discharge from 1 minute to 24 hour duration) |
|  | Battery installation drawing (enclosed battery cabinets, interconnection between battery/cells etc) |
|  | Battery Charger General Arrangement drawing |
|  | Battery Charger Schematic Diagrams |
|  | Battery Charger Configuration Data |
|  | Battery Room Requirements (Maintainability, Ventilation, Operating Temperature, OHS Act requirements) |
|  | Low Voltage Switchboard |
|  | Low Voltage Load Flow analysis (Kilowatts, Kilovars, Voltage levels, Current flows) |
|  | Low Voltage Load List complete with diversities applied and spare capacity allowed |
|  | Low Voltage Short Circuit Analysis (Fault levels: Three phase symmetrical, Asymmetrical, Asymmetrical peak, Single phase to earth) |
|  | Final LV system operating basis/philosophy. (Example: dual supply, paralleling, diversity etc) |
|  | Final LV system future expansion requirements and allowance thereof |
|  | Final LV MCC/Switchgear design basis, requirements and equipment specification as per SANS IEC 61439 and 60947 |
|  | Final LV MCC/Switchgear interface with PLC and SCADA system |
|  | Final LV MCC/Switchgear Single Line Diagrams |
|  | Final LV MCC/Switchgear External General Arrangement |
|  | Final LV MCC/Switchgear Individual Tier Door Layout |
|  | Final LV MCC/Switchgear Individual Tier Chassis Layout |
|  | Final LV MCC/Switchgear Individual Rear Layout showing full details of busbar droppers, trunking and terminal strip arrangements(where applicable) |
|  | Final LV MCC/Switchgear Individual Incomer Circuit side view complete with dimensions of the Air Circuit Breaker and all busbar dimensions, together with the gland plate position and height of gland plate to the main busbar connection, where applicable. |
|  | Final LV MCC/Switchgear Busbar Layout/Specification with full details of main busbars including dimensions and all busbar droppers. Provision for maintenance of busbars to be taken into account |
|  | Final LV MCC/Switchgear Schematic and Wiring Diagrams of each circuit including detailed PLC/SCADA Interface |
|  | Standby Generator Changeover and Control Schematic diagrams |
|  | Final LV MCC/Switchgear Label Design and Nameplate in compliance with SANS 1973. RW has additional requirements for this nameplate: E.g. date of manufacture, RW contract number, Contractor contract number, Contractor contact details, etc. |
|  | Low Voltage Distribution Boards |
|  | LV Load Flow analysis (Current flows) |
|  | LV Short Circuit Analysis (Fault levels: Three phase symmetrical, Single phase to earth) |
|  | Final LV system operating basis/philosophy. (Example: paralleling, diversity etc) |
|  | Final LV system future expansion requirements and allowance thereof |
|  | Final LV Distribution Board design basis, requirements and equipment specification as per SANS IEC 60439 and 60947 |
|  | Final LV Distribution Board General Arrangement, Exterior and Interior |
|  | Final LV Distribution Board Single Line Diagram |
|  | Final LV Distribution Board Schematic and Wiring Diagrams of each circuit |
|  | Transformers |
|  | Power transformer requirements specification (control and indication, construction requirements) |
|  | Power transformer operating voltages |
|  | Power transformer schematic and wiring diagrams |
|  | Power transformer nameplate details and layout |
|  | Power transformer layout and general arrangement |
|  | Transformer accessories details and layout |
|  | Transformer main cable termination box arrangement for LV and MV |
|  | Cabling requirements (Cable sizing) |
|  | Mimic Panels |
|  | Mimic panel requirements specification (control and indication, construction requirements) |
|  | Mimic panel operating voltage and uninterruptible power supply requirements |
|  | Mimic panel schematic and wiring diagrams |
|  | Mimic panel layout and artwork detailing |
|  | Mimic panel layout and general arrangement (floor standing) |
|  | Fire Detection System |
|  | Fire Detection, monitoring &/or protection philosophy |
|  | Adherence to Local Fire Regulations and OHS Act |
|  | Control Panel Design with zone design |
|  | Fire Detection Equipment Layout Drawings (Plan, Sections, Elevations) |
|  | Fire Detection Conduiting Layout, Cable Access Requirements (Plan, Sections, Elevations) |
|  | Interface to SCADA systems |
|  | Fire Detection Equipment Network Drawings |
|  | Fire protection equipment (refer to Mechanical Design) |
|  | Diesel Standby Generator |
|  | Load Flow analysis (Kilowatts, Current flows, Diversity) |
|  | Motor starting requirements of essential power supplies (sump pumps, valves) and diversity between standing and starting loads |
|  | Future load requirements and allowance thereof |
|  | Generator and Diesel Engine Ratings |
|  | Optimising Generator Load Rating to prevent operation outside optimal load |
|  | Generator Control Philosophy and Controller Configuration |
|  | Generator Outline and General Arrangement Drawings |
|  | Generator Bunding requirements and design, including level sensors, valves, PLC interface etc |
|  | Generator Changeover and Control Schematic diagrams |
|  | Generator Controller Configuration and Settings |
|  | Earthing and Lightning Protection |
|  | Plant earthing and lightning protection philosophy and tie-in with existing system where applicable |
|  | Soil resistivity surveys |
|  | Design using proprietary software in accordance with SANS, IEC and IEEE criteria |
|  | Development of earth mat designs including electrodes, conductors etc in accordance with the software output above and detail documentation of the designs |
|  | Compliance with step and touch potentials limitations in terms of SANS, IEC and IEEE standards where there is human presence |
|  | Detail drawings of earth mat design connection points of components of the system and test points |
|  | Lightning protection requirements, risk assessments and design in accordance with SANS and IEC standards |
|  | Detail earthing and lightning protection layout (Plan, Elevations), conductor sizing, routing and layout, down conductors, etc. Tie in to building re-inforcing bars will not be accepted |
|  | Building Small Power and Lighting System |
|  | Requirements (Socket Outlets, Water Heaters, HVAC isolators, Surface/Built in installation) |
|  | Lighting philosophy: Final design including lux calculation (Daylight switching, selection of fitting type per application) |
|  | Emergency lighting (Operational and OHS Act requirements) |
|  | Conduiting requirements (Built-in/Surface mount) |
|  | Standby power requirements (UPS and /or generator backup) |
|  | Exterior Building Lighting |
|  | Interface to data, communication, access control and fire detection systems, where applicable |
|  | Fault Level Requirements |
|  | Conductor Design and Specification |
|  | Small Power and Lighting Layout (Plan and Elevation, Interior and Exterior) |
|  | Small Power and Lighting Conduiting Layout (Plan and Elevation), Cable Access Requirements |
|  | Distribution Board Design (Rating, Fault Level, Circuits, Balancing of Loads, Sections (Raw/Standby/UPS section) |
|  | Interface to HVAC systems where required |
|  | Cable reticulation and plant cabling |
|  | Normal and essential service supply points from within the existing reticulation in the plant |
|  | Service detection along anticipated cable routes |
|  | MV and LV cable reticulation design |
|  | Cable installation philosophy (ducts, trenches, sleeves, protection from other services, cable transit system, road crossings) |
|  | Interface to other services (buildings, pipes, roads, valve chambers, sewerage lines, telecommunications and data) |
|  | Cable support system philosophy and specification (Cable Basement, where applicable and plant cable support systems, including valve chambers, where required) |
|  | Cable racking system design calculations (mechanical loading) |
|  | Detailed layout of all cables at all sections of the cable support system |
|  | Requirements for ancillary equipment (Pushbutton stations, junction boxes, welding plugs, isolator panels) |
|  | Cable Design Schedules for MV and LV Power Cables (Voltage, Size, de-rating for non-standard installation conditions, Volt Drop, Fault Withstand etc) |
|  | Cable Schedules (Detailed Design with full cable termination details of each core of the cable for both power and control cables) |
|  | Cable Route Drawings for all cables |
|  | Cable Support System Drawings (Cable Basement, where applicable, Valve Chambers, Switchgear Rooms) |
|  | Reticulation Cable Access into buildings, structures (Ducts, cable racking, slots, sleeves including casting into concrete structures at right position and height during chamber construction, cable transit systems etc) |
|  | Schedule and full details of all cable transit systems in and out of the building and valve chambers |
|  | Schedule of any core drilling requirements through reinforced concrete slabs and interface with the structural engineer in this regard |
|  | Cabling sealing systems, where cables enter and exit buildings |
|  | Electrical interface with Civil, Architectural, Mechanical, Process, Pipelines and Automation Requirements (where required and applicable) |
|  | Switchgear Room Philosophy (number of rooms, separation of equipment, sizing, clearances to all walls, doors, etc.) |
|  | Switchgear Room Heights and Ceiling requirements (Internal Arc, IEC 62271, arc ducting) |
|  | Switchgear Room Lighting philosophy (natural and artificial lighting, emergency lighting) |
|  | Switchgear Room HVAC philosophy (natural ventilation, A/C, emergency ventilation) |
|  | Switchgear Room Access Control (Doors, emergency exits, type of door mechanisms) |
|  | Switchgear Room Cable Ducts and Access (Cable duct requirements, Slots, sleeves, cable transit systems, water ingress control) |
|  | Switchgear Room Materials Handling Requirements (Crawl Beam) |
|  | Switchgear Room Architectural/Structural Drawings (Plan, Elevation and Sections) |
|  | Diesel Standby Generator Bay Requirements (Size, Noise Control, Exhaust Ducting, Bunding, Fuel Storage, environmental and safety requirements) |
|  | Diesel Standby Generator Bay Equipment Handling (Crawl Beam) |
|  | Diesel Standby Generator Bay Cable Ducts (Slots, sleeves, water ingress control, cable transit systems) |
|  | Diesel Standby Generator Bay Lighting (natural and artificial lighting, emergency lighting) |
|  | Diesel Standby Generator Bay Ventilation requirements (Forced/Natural ventilation) |
|  | Diesel Standby Generator Bay/Room Layout Drawings (Plan, Elevations, Sections) |
|  | Transformer Room Requirements (Sizing, Bunding, Plinth details, cable ducts, explosion separation) |
|  | Transformer Bay Cable Access (cable transit systems, final finish of transformer bay, chipped stone etc) |
|  | Transformer Bay Equipment Handling (Crawl beam etc) |
|  | Transformer Bay Lighting (natural and artificial lighting, emergency lighting) |
|  | Transformer Bay Ventilation requirements (ONAN) |
|  | Transformer Bay Layout Drawings (Plan, Elevations, Sections) |
|  | UPS and Battery Rooms Sizing |
|  | UPS and Battery Room Lighting philosophy (natural and artificial lighting, emergency lighting) |
|  | UPS and Battery Room HVAC philosophy (natural ventilation, A/C, emergency ventilation, safety requirements w.r.t. explosive gases) |
|  | UPS and Battery Room Cable Ducts and Access (Slots, sleeves, Water ingress control, cable transit systems) |
|  | UPS and Battery Room Layout Drawings (Plan, Elevations, Sections) |
|  | Mimic positioning in Control Room |
|  | Control Room Cable Ducts and Access (Slots, sleeves, Water ingress control, cable transit systems) for mimic cables |
|  | Control Room Lighting philosophy (natural and artificial lighting, emergency lighting) |
|  | Control Room HVAC philosophy (natural ventilation, A/C, emergency ventilation) |
|  | Control Room Cable Ducts and Access (Slots, sleeves, Water ingress control, cable transit systems) for mimic cables |
|  | Control Room Layout Drawings (Plan, Elevations, Sections) |

# CONSTRUCTION SUPERVISION

After verification of all designs the Contractors’ design engineer shall be responsible for supervision of the entire electrical installation during construction as follows:

  - The Contractors’ design engineer shall fulfil the duties of the electrical design engineer under Section 6 of the Construction Regulations and shall conduct design compliance inspections at all relevant milestone points in the project. At the completion of the project the design engineer shall declare the installation safe and issue a completion certificate.

  - Obtaining a proposed quality control plan from every manufacturer of equipment and in consultation with the Rand Water Lead Engineer enter witness and hold points for each construction milestone of the manufactured equipment.

  - Inform the Rand Water Lead Engineer of each construction milestone inspection required as per the quality control plan. Attend each construction milestone inspection and generate documentary evidence of the inspection in the form of a completed and signed attendance of all present at the inspection, sign off of the milestone if accepted or generate a punch list of items to be corrected, with actions required by each party and agreed completion dates, signed by the design engineer and the manufacturers’ representative. Records shall be kept of each such visit for submission in a monthly report to the Rand Water Lead Engineer. The contractor must complete his own FAT and rectify all faults, before RW is invited to attend the FAT. The contractor must produce evidence of this FAT.

  - Once the manufactured equipment is ready for a Factory Acceptance Test the Contractors’ design engineer shall carry out the Acceptance Test with the minimum of the following tests (Rand Water to witness all Factory Acceptance Test carried out):

    - Specifying witness and hold points on the QCP documents from each manufacturer during manufacture.

    - Management of the QCP documents and witnessing at hold points, including sign off.

    - Generation of defects lists and management of clearance of defects.

    - Construction quality checks for compliance with the requirements of the specifications.

    - Point to point wiring checks of all wiring and agreement with the schematic diagrams.

    - Injection tests on current transformers where required.

    - Pressure and Insulation Resistance Tests.

    - Functional tests including closing, tripping and indication from all possible operational modes

    - Labelling

    - Protection settings, Configuration where required and adjustments.

    - Functionality of metering equipment.

    - Relevant photographic evidence.

  - A signed attendance register for each day of a test shall be kept.

  - A master set of approved construction documents shall be kept by the Contractors’ design engineer and the manufacturer on which tested and completed circuits shall be marked up. Any modifications that may be required shall also be recorded on the documents, together with the date(s). A master set of approved construction documents shall ALSO be kept by the Contractor on site, at all times

  - Once construction, impacting any electrical part of the installation, commences on site, the following must be adhered to:

    - Attend site once a week or when a significant construction milestone such as lift in concrete pouring, finalisation of concrete ducts, cable racking, casting in of cable transit system boxes etc is reached. A record of progress or events witnessed shall be kept in a site diary, together with dated photographic evidence. Where site instructions are issued these shall be communicated to the Rand Water Project Manager and Lead Engineer. Compliance to the Contractors’ approved design shall be checked and any deviations recorded as a site instruction. Every calendar month the Contractors’ design engineer shall submit a concise report containing all items above to the Lead Engineer and Rand Water Project Manager.

    - Attend all scheduled project and technical meetings on site.

    - Once the electrical installation commences on site, the following must be adhered to:

    - Attend site twice or more frequently a week or when a significant construction milestone such as delivery of a distribution board etc is reached. The Contractors’ design engineer shall check that the installation on site such as cable racking, cable installation, installation of other equipment such as control panels etc proceeds in accordance with the approved design. A record of progress or events witnessed shall be kept in a site diary, together with dated photographic evidence. Where site instructions are issued these shall be communicated to the Rand Water Project Manager and Lead Engineer. Compliance to the Contractors’ approved design shall be checked and any deviations recorded as a site instruction. Every calendar month until final handover of the completed installation the Contractors’ design engineer shall submit a concise report containing all items above to the Lead Engineer and Rand Water Project Manager.

  - Once the completed installation or a logical part thereof e g a turbine set is completed the Contractors’ design engineer shall determine the necessary testing requirements and carry out the commissioning and Site Acceptance Test on the completed installation with the minimum of the following:

    - Construction quality checks for compliance with the requirements of the specifications.

    - Checking the cable installation is as per the approved design.

    - Cable trench inspections.

    - Inspection of cable transit points e g into valve chambers where required.

    - Cable supports are as per specification or best practice.

    - Point to point wiring checks of all wiring between connected equipment and agreement with the schematic diagrams and cable schedules.

    - Pressure and Insulation tests.

    - Functional tests including closing, tripping and indication (including alarms) from all possible operational modes.

    - Labelling including but not limited to cable numbers, equipment labelling and equipment rooms cable numbers

    - Configuration and protection settings and adjustments.

    - Functionality of metering.

    - Relevant photographic evidence.

    - A signed attendance register for each day of the Test shall be kept.

  - A master set of approved construction documents shall be kept by the Contractors’ design engineer and the manufacturer on which tested and completed circuits shall be marked up. Any modifications that may be required shall also be recorded on the documents, together with the date(s). Close out of the implemented modifications shall also be recorded on the documents complete with dates.

  - A commissioning report of the completed installation addressing all the results of testing and checking shall be submitted to the Rand Water Project Manager and Lead Engineer.

# MEDIUM VOLTAGE SWITCHGEAR

  - A dedicated room for medium voltage switchboards shall be provided. Separate rooms shall be provided for MV switchboards rated at different voltage levels. Specific room requirements for the room.

  - All switchboards shall be equipped with withdrawable circuit breakers for each circuit. Insertion and withdrawal of circuit breaker trucks shall be horizontal and preferably mid mount.

  - All switchboards shall be front and rear access.

  - The typical circuit arrangements for the Zoekfontein ##kV Medium Voltage switchboard is as follows:

| Circuit No- Left To Right | Description |
| --- | --- |
| 1 | Bus Bar VT Panel 1 |
| 2 | Turbine Generator Incomer BG2 |
| 3 | ## / ##kV Step Up Transformer No 1 |
| 4 | Bus-Section 1 |
| 5 | Bus Bar VT Panel 2 |
| 6 | Turbine Generator Incomer BG3 |
| 7 | ## / ##kV Step Up Transformer No 2 |

  - The typical circuit arrangements for the Zoekfontein ##kV switchboard is as follows:

| Circuit No- Left To Right | Description |
| --- | --- |
| 1 | Bus Bar VT Panel 1 |
| 2 | Incomer 1 |
| 3 | Zuikerbosch Feeder No 1 |
| 4 | Bus-Section 1 |
| 5 | Bus Bar VT Panel 2 |
| 6 | Incomer 2 |
| 7 | Zuikerbosch Feeder No 2 (Future) |

  - The typical circuit arrangements for the Zuikerbosch/Forebay ##kV receiving switchboard is as follows:

| Circuit No- Left To Right | Description |
| --- | --- |
| 1 | Bus Bar VT Panel 1 |
| 2 | Zoekfontein Incomer 1 |
| 3 | Zuikerbosch Transformer Feeder No 1 |
| 4 | Bus-Section 1 |
| 5 | Bus Bar VT Panel 2 |
| 6 | Zuikerbosch Transformer Feeder No 2 |
| 7 | Zoekfontein Incomer 2 (Future) |

  - The typical circuit arrangements for the Zuikerbosch 11kV reticulation switchboard is as follows:

| Circuit No- Left To Right | Description |
| --- | --- |
| 1 | Bus Bar VT Panel 1 |
| 2 | Incomer 1 |
| 3 | Zuikerbosch Engine Room 4A/4B Feeder (No 1) |
| 4 | Bus-Section 1 |
| 5 | Bus Bar VT Panel 2 |
| 6 | Incomer 2 |
| 7 | Zuikerbosch Engine Room 4A/4B Feeder (No 2) |

  - 11kV SWITCHGEAR REQUIREMENTS

NOTE:  TBA in the following tables refers to information that will be finalised during detail design

| Circuit Type | 1 |  |  | 2 | 3 | 4 |
| --- | --- | --- | --- | --- | --- | --- |
| Circuit Description | Transformer Feeder | Outgoing Feeder | Incomer | Generator Incomer | Bus-Section | Bus Riser and Busbar VT |
| No of Circuits | TBA | 2 | 2 | TBA | 1 | 1 |
| IEC 62271 Type Test Certification Required |  |  |  |  |  |  |
| General | Yes | Yes | Yes | Yes | Yes | Yes |
| Dielectric Tests | Yes | Yes | Yes | Yes | Yes | Yes |
| Radio Interference Tests | Yes | Yes | Yes | Yes | Yes | Yes |
| Resistance of Main Circuit | Yes | Yes | Yes | Yes | Yes | Yes |
| Temperature Rise | Yes | Yes | Yes | Yes | Yes | Yes |
| Short Time Withstand and Peak Withstand Current Tests | Yes | Yes | Yes | Yes | Yes | Yes |
| Internal Arc Withstand | Yes | Yes | Yes | Yes | Yes | Yes |
| Verification of Degree of Protection | Yes | Yes | Yes | Yes | Yes | Yes |
| Tightness Tests | Yes | Yes | Yes | Yes | Yes | Yes |
| Electromagnetic Compatibility (EMC) | Yes | Yes | Yes | Yes | Yes | Yes |
| Site Altitude (maMSL) | 1595 | 1595 | 1595 | 1595 | 1595 | 1595 |
| Ambient Temperature Range | -5 to 40˚C | -5 to 40˚C | -5 to 40˚C | -5 to 40˚C | -5 to 40˚C | -5 to 40˚C |
| Rated Normal Rating (A) | 1250 or 630 | 1250 or 630 | 1250 or 630 | 1250 or 630 | 1250 or 630 | 1250 or 630 |
| Busbar Fault Rating (kA) | TBA | TBA | TBA | TBA | TBA | TBA |
| Rated Short Time Withstand Current (Ik) (kA) | TBA | TBA | TBA | TBA | TBA | TBA |
| Rated Peak Withstand Current (Ip) (kA) | TBA | TBA | TBA | TBA | TBA | TBA |
| DC Offset Current at Fault Clearance (%) | 30.00 | 30.00 | 30.00 | 30.00 | 30.00 | 30.00 |
| Rated duration of fault (tk) (secs) | 3.00 | 3.00 | 3.00 | 3.00 | 3.00 | 3.00 |
| Busbar Voltage Rating (kV) (Ur) | TBA | TBA | TBA | TBA | TBA | TBA |
| Rated Frequency (fr) (Hz) | 50.00 | 50.00 | 50.00 | 50.00 | 50.00 | 50.00 |
| Busbar Operating Voltage (kV) | TBA | TBA | TBA | TBA | TBA | TBA |
| Rated Short Duration Power Frequency Voltage Withstand (Ud) (kV) | 28.00 | 28.00 | 28.00 | 28.00 | 28.00 | 28.00 |
| Rated Lightning Impulse Withstand Voltage (Up) (kV) | 95.00 | 95.00 | 95.00 | 95.00 | 95.00 | 95.00 |
| Rated Supply Voltage of Opening and Closing Circuits and Auxilliary Devices (Ua) (Vdc) | 110.00 | 110.00 | 110.00 | 110.00 | 110.00 | 110.00 |
| Internal Arc Classification | IAC Classified | IAC Classified | IAC Classified | IAC Classified | IAC Classified | IAC Classified |
| Internal Arc Withstand (kA) | TBA | TBA | TBA | TBA | TBA | TBA |
| Internal Arc Withstand Time (secs) | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 |
| Arc Vent Ducting | TBC | TBC | TBC | TBC | TBC | TBC |
| Accessibility | AFLR | AFLR | AFLR | AFLR | AFLR | AFLR |
| Level of Service Continuity | LSC2A | LSC2A | LSC2A | LSC2A | LSC2A | LSC2A |
| Partition Class | PM | PM | PM | PM | PM | PM |
| Circuit Rating (A) | 1250 or 630 | 1250 or 630 | 1250 or 630 | 1250 or 630 | 1250 or 630 | 1250 or 630 |
| Circuit Breaker |  |  |  |  |  |  |
| Nominal Rating (A) | 630 | 630 | 630 | 630 | 630 | - |
| Rated Short Time Withstand Current (Ik) (kA) | TBA | TBA | TBA | TBA | TBA | - |
| Rated Peak Withstand Current (Ip) (kA) | TBA | TBA | TBA | TBA | TBA | - |
| DC Offset Current at Breaker Opening (%) | 30.00 | 30.00 | 30.00 | 30.00 | 30.00 | - |
| Rated duration of fault (tk) (secs) | 3.00 | 3.00 | 3.00 | 3.00 | 3.00 | - |
| Interrupting Medium | Vacuum | Vacuum | Vacuum | Vacuum | Vacuum |  |
| Breaker Tripping | Shunt Trip | Shunt Trip | Shunt Trip | Shunt Trip | Shunt Trip | - |
| Breaker Undervoltage Release | Yes | Yes | Yes | Yes | Yes | - |
| Undervoltage Release Voltage | 110 V DC | 110 V DC | 110 V DC | 110 V DC | 110 V DC |  |
| Breaker Closing | Solenoid | Solenoid | Solenoid | Solenoid | Solenoid | - |
| Circuit Breaker Operations (average/annum) | 20 | 100 | 100 | 100 | 20 | - |
| Circuit Breaker Actuation | Spring Charge | Spring Charge | Spring Charge | Spring Charge | Spring Charge | - |
| Spring Charge Motor | 110 V DC | 110 V DC | 110 V DC | 110 V DC | 110 V DC |  |
| Circuit Breaker Remote Operation Plug & Pendant | Yes, Close & Open | No | No | No | Yes, Close & Open | - |
| Circuit Breaker Remote Pendant Indication | Yes, Close & Open Indication | - | - | - | Yes, Close & Open Indication | - |
| Castell Interlocking | No | No | No | Yes for generator | No | - |
| Degree of Protection | IP4X | IP4X | IP4X | IP4X | IP4X | IP4X |
| Degree of Protection Internal | IP20 | IP20 | IP20 | IP20 | IP20 | IP20 |
| Panel Colour | B26 Orange To SANS 1091 | B26 Orange To SANS 1091 | E46 Light Admiralty Grey To SANS 1091 | E46 Light Admiralty Grey To SANS 1091 | E46 Light Admiralty Grey To SANS 1091 | B26 Orange To SANS 1091 |
| Circuit Earth Switch Required | Yes | No | No | No | No | No |
| Earth Switch Rated Short Time Withstand Current (Ik) | TBA | - | - | - | - | - |
| Earth Switch Rated Peak Withstand Current (Ip) | TBA | - | - | - | - | - |
| Protection C T | TBA/1; 10VA; 5P20 | TBA/1; 10VA; 5P20 | TBA/1; 10VA; 5P20 | TBA/1; 10VA; 5P20 | - | - |
| Differential Protection C T | TBA | TBA | TBA | TBA | - | - |
| Metering C T | TBA/1, Class 0,5, 5VA | TBA/1, Class 0,5, 5VA | TBA/1, Class 0,5, 5VA | TBA/1, Class 0,5, 5VA | - | - |
| Core Balance C T | 100/1, 2 VA, 5P20 | 100/1, 2 VA, 5P20 | 100/1, 2 VA, 5P20 | 100/1, 2 VA, 5P20 | - | - |
| Transformer or Generator Neutral C T | TBA | TBA | TBA | TBA | - | - |
| Transformer NER C T | - | - | - | - | - | - |
| Voltage Transformer | - | - | - | - | - | 11000/110; Class 0,5, 100VA |
| Voltage Transformer Primary/Secondary | - | - | - | - | - | Yyn |
| Voltage Transformer Connection | - | - | - | - | - | Busbar |
| Voltage Transformer Type | - | - | - | - | - | Withdrawable |
| Trip Circuit Supervision | Yes | Yes | Yes | Yes | Yes | - |
| Breaker Fail Protection | Yes | No | No | No | No | - |
| Protection Relays | Transformer Protection | Feeder Protection | Feeder Protection | Generator Protection | - | - |
| Relay Specification | See elsewhere in document | See elsewhere in document | See elsewhere in document | See elsewhere in document | - | - |
| Relay Inputs |  |  |  |  |  |  |
| Closing Supply On | Yes | Yes | Yes | Yes | - |  |
| VCB Racked In (Service Position) | Yes | Yes | Yes | Yes | - |  |
| VCB Spring Charged | Yes | Yes | Yes | Yes | - |  |
| O/C and E/F Relay Healthy | Yes | Yes | Yes | Yes | - |  |
| Upstream Breaker Closed | Yes | - | - | - | - |  |
| VCB No Volt Relay Healthy | Yes | Yes | Yes | Yes | - |  |
| Service Selected | Yes | Yes | Yes | Yes | - |  |
| VCB Open | Yes | Yes | Yes | Yes | - |  |
| VCB Closed | Yes | Yes | Yes | Yes | - |  |
| Arc Flash and Circuit Breaker Fail 1 | Yes | Yes | Yes | Yes | - |  |
| Arc Flash and Circuit Breaker Fail 2 | Yes | Yes | Yes | Yes | - |  |
| Switchgear Circuit Breaker Open Command | Yes | Yes | Yes | Yes | - |  |
| Mimic Open Command | Yes | Yes | Yes | Yes | - |  |
| Mimic Close Command | Yes | Yes | Yes | Yes | - |  |
| Tripping Supply On | Yes | Yes | Yes | Yes | - |  |
| Earth Switch Open | Yes | - | - | - | - |  |
| External Transformer Trips Healthy | Yes | - | - | - | - |  |
| Protection Relay Healthy | Yes | Yes | Yes | Yes | - | - |
| Relay Outputs |  |  |  |  |  |  |
| Relay Healthy | Yes | Yes | Yes | Yes | - |  |
| VCB Racked In (Service Position) | Yes | Yes | Yes | Yes | - |  |
| VCB Spring Charged | Yes | Yes | Yes | Yes | - |  |
| Protection Relay Annunciation | Yes | Yes | Yes | Yes | - |  |
| IDMT O/C Trip | Yes | Yes | Yes | TBA | - |  |
| Inst O/C Trip | Yes | Yes | Yes | TBA | - |  |
| E/F Trip | Yes | Yes | Yes | TBA | - |  |
| Undervoltage Trip | Yes | Yes | Yes | TBA | - |  |
| Upstream Supply Breaker Opened | - | Yes | Yes | TBA | - |  |
| PLC Trip | Yes | Yes | Yes | TBA | - |  |
| Fire Trip | - | Yes | Yes | TBA | - |  |
| Breaker Fail Trip | Yes | Yes | Yes | Yes | - |  |
| Transformer External Trips | Yes | - | - | - | - |  |
| Motor Thermal Trip | - | - | - | - | - |  |
| Internal Arc Protection | Yes | Yes | Yes | Yes | Yes | Yes |
| Current and Light | Yes | Yes | Yes | Yes | Yes | Yes |
| Busbar Compartment | Yes | Yes | Yes | Yes | Yes | Yes |
| Cable Compartment | Yes | Yes | Yes | Yes | - | - |
| Circuit Breaker Compartment | Yes | Yes | Yes | Yes | Yes | - |
|  |  |  |  |  | - |  |
| Differential Protection | TBA | - | - | TBA | - | - |
| Metering |  |  |  |  |  |  |
| Metering Unit 1 | Multi-Functional | Multi-Functional | Multi-Functional | Connect to existing Elster Kent meter- CT/VT signals | - | - |
| Metering Unit 1 Communications | - | - | - | Modbus TCP/IP | - | - |
|  |  | - | - | - |  |  |
| Power Quality Meter | - | - | - | Yes as per Specification elsewhere in this document | - | - |
| Protection Test Block | MMLG 1 | MMLG 1 | MMLG 1 | MMLG 1 | - | - |
| Metering Test Block | MMLG 1 | MMLG 1 | MMLG 1 | MMLG 1 | - | - |
| Selector Switches | Remote/ Off/ Maint | Remote/ Off/ Maint | Remote/ Off/ Maint | Remote/ Off/ Maint | Remote/ Off/ Maint | - |
| Control Wiring | Minimum 1,5mm2 stranded copper | Minimum 1,5mm2 stranded copper | Minimum 1,5mm2 stranded copper | Minimum 1,5mm2 stranded copper | Minimum 1,5mm2 stranded copper | Minimum 1,5mm2 stranded copper |
| Control Wiring Colour | RW standard | RW standard | RW standard | RW standard | RW standard | RW standard |
| Control wire identification system | Clip on, individual colour coded | Clip on, individual colour coded | Clip on, individual colour coded | Clip on, individual colour coded | Clip on, individual colour coded | Clip on, individual colour coded |
| Circuit Breaker Local Control |  |  |  |  |  |  |
| Trip Button | Yes | Yes | Yes | Yes | Yes | - |
| Hardwired Interlocks | Yes | Yes | Yes | Yes | Yes |  |
| Closing Supply On | Yes | Yes | Yes | Yes | Yes |  |
| VCB Racked In (Service Position) | Yes | Yes | Yes | Yes | Yes |  |
| VCB Spring Charged | Yes | Yes | Yes | Yes | Yes |  |
| O/C and E/F Relay Healthy | Yes | Yes | Yes | Yes | - |  |
| Upstream Breaker Closed | Yes | Yes | Yes | Yes | - |  |
| VCB No Volt Relay Healthy | Yes | Yes | Yes | Yes | Yes |  |
| Service Selected | Yes | Yes | Yes | Yes | Yes |  |
| VCB Open | Yes | Yes | Yes | Yes | Yes |  |
| Earth Switch Open | Yes | - | - | - | - |  |
| O/C & E/F & Transformer Trips Healthy | Yes | - | - | - | - |  |
| Power Factor Correction & Zorc Interlock | - | - | - | - | - |  |
| Interlocks Annunciator | Yes | Yes | Yes | Yes | Yes |  |
| Closing Supply On | Yes | Yes | Yes | Yes | Yes |  |
| VCB Racked In (Service Position) | Yes | Yes | Yes | Yes | Yes |  |
| VCB Spring Charged | Yes | Yes | Yes | Yes | Yes |  |
| O/C and E/F Relay Healthy | Yes | Yes | Yes | Yes | - |  |
| Upstream Breaker Closed | Yes | - | - | - | - |  |
| VCB No Volt Relay Healthy | Yes | Yes | Yes | Yes | Yes |  |
| Service Selected | Yes | Yes | Yes | Yes | Yes |  |
| VCB Open | Yes | Yes | Yes | Yes | Yes |  |
| Earth Switch Open | Yes | - | - | - | - |  |
| O/C & E/F & Transformer Trips Healthy | Yes | - | - | - | - |  |
| NVR Healthy | Yes | Yes | Yes | Yes | Yes |  |
| PLC Hardwired Inputs to outgoing terminals | - | Yes | Yes | Yes | Yes |  |
| Closing Supply On | - | Yes | Yes | Yes | Yes |  |
| VCB Racked In (Service Position) | - | Yes | Yes | Yes | Yes |  |
| VCB Spring Charged | - | Yes | Yes | Yes | Yes |  |
| Generator Protection Relay Healthy | - | Yes | Yes | Yes | - |  |
| VCB No Volt Relay Healthy | - | Yes | Yes | Yes | Yes |  |
| Service Selected | - | Yes | Yes | Yes | Yes |  |
| VCB Open | - | Yes | Yes | Yes | Yes |  |
| Earth Switch Open | - | - | - | - | - |  |
| Power Factor Correction & Zorc Interlock | - | - | - | - | - |  |
| PLC Hardwired Outputs to outgoing terminals |  |  |  |  |  |  |
| Breaker Close Contact | Yes | Yes | Yes | Yes | Yes |  |
| Breaker Open Contact | Yes | Yes | Yes | Yes | Yes |  |
| Remote Reset Contact | - | - | - | - | - |  |
| Local Indication |  |  |  |  |  |  |
| Circuit Breaker On | Yes | Yes | Yes | Yes | Yes | - |
| Circuit Breaker Off | Yes | Yes | Yes | Yes | Yes | - |
| Circuit Breaker Tripped | Yes | Yes | Yes | Yes | - | - |
| Circuit Instrument Panel Interior Illumination |  |  |  |  |  |  |
| Strip LED illumination | Yes | Yes | Yes | Yes | Yes | Yes |
| Circuit Anti-Condensation Heater |  |  |  |  |  |  |
| Cable Chamber | Yes | Yes | Yes | Yes | - | - |
| Busbar Chamber | No | No | No | No | No | - |
| Circuit Breaker Chamber | Yes | Yes | Yes | Yes | Yes | - |
| Heater Supply Voltage (Vac) | 230 | 230 | 230 | 230 | 230 | - |
| Cable Type | 6,35/11 kV XLPESWAPVC | 6,35/11 kV XLPEPVC | 6,35/11 kV XLPEPVC | 6,35/11 kV XLPEPVC | - | - |
| Cable Size (mm2) | TBA mm2 3 core | TBA mm2 3 core | TBA mm2 3 core | TBA mm2 3 core | - | - |
| No of Cables | 1 | 1 | 1 | 1 | - | - |
| Transformer Rating (kVA) | TBA | TBA | TBA | TBA | - | - |
| Transformer FLC (A) | TBA | TBA | TBA | TBA | - | - |
| Transformer Ratio | 11/22/0.4kV | 11kV | 11kV | 11kV | - | - |
| Transformer Impedance (%) | - | - | - | - | - | - |
| Transformer Vector Group | dY | - | - | - | - | - |
| Transformer Earth Fault Current Transformer | 100/1 | - | - | - | - | - |
| LV Grounding | NER- Limited to 350 A | TBA | TBA | TBA | - | - |

  - OTHER ##kV MEDIUM VOLATGE SWITCHBOARD REQUIREMENTS

| Circuit Type | 1 | 2 | 3 | 4 | 5 |
| --- | --- | --- | --- | --- | --- |
| Circuit Description | Cable Feeder | Transformer Feeder | Incomer | Bus-Section | Bus Riser and Busbar VT |
| No of Circuits | TBA | TBA | TBA | TBA | TBA |
| IEC 62271 Type Test Certification Required |  |  |  |  |  |
| General | Yes | Yes | Yes | Yes | Yes |
| Dielectric Tests | Yes | Yes | Yes | Yes | Yes |
| Radio Interference Tests | Yes | Yes | Yes | Yes | Yes |
| Resistance of Main Circuit | Yes | Yes | Yes | Yes | Yes |
| Temperature Rise | Yes | Yes | Yes | Yes | Yes |
| Short Time Withstand and Peak Withstand Current Tests | Yes | Yes | Yes | Yes | Yes |
| Internal Arc Withstand | Yes | Yes | Yes | Yes | Yes |
| Verification of Degree of Protection | Yes | Yes | Yes | Yes | Yes |
| Tightness Tests | Yes | Yes | Yes | Yes | Yes |
| Electromagnetic Compatibility (EMC) | Yes | Yes | Yes | Yes | Yes |
| Site Altitude (maMSL) | 1595 | 1595 | 1595 | 1595 | 1595 |
| Ambient Temperature Range | -5 to 40˚C | -5 to 40˚C | -5 to 40˚C | -5 to 40˚C | -5 to 40˚C |
| Rated Normal Rating (A) | 1250 or 630 | 1250 or 630 | 1250 or 630 | 1250 or 630 | 1250 or 630 |
| Busbar Fault Rating (kA) | TBA | TBA | TBA | TBA | TBA |
| Rated Short Time Withstand Current (Ik) (kA) | TBA | TBA | TBA | TBA | TBA |
| Rated Peak Withstand Current (Ip) (kA) | TBA | TBA | TBA | TBA | TBA |
| DC Offset Current at Fault Clearance (%) | 30.00 | 30.00 | 30.00 | 30.00 | 30.00 |
| Rated duration of fault (tk) (secs) | 3.00 | 3.00 | 3.00 | 3.00 | 3.00 |
| Busbar Voltage Rating (kV) (Ur) | 24 | 24 | 24 | 24 | 24 |
| Rated Frequency (fr) (Hz) | 50.00 | 50.00 | 50.00 | 50.00 | 50.00 |
| Busbar Operating Voltage (kV) | TBA | TBA | TBA | TBA | TBA |
| Rated Short Duration Power Frequency Voltage Withstand (Ud) (kV) | 50.00 | 50.00 | 50.00 | 50.00 | 50.00 |
| Rated Lightning Impulse Withstand Voltage (Up) (kV) | 150.00 | 150.00 | 150.00 | 150.00 | 150.00 |
| Rated Supply Voltage of Opening and Closing Circuits and Auxilliary Devices (Ua) (Vdc) | 110.00 | 110.00 | 110.00 | 110.00 | 110.00 |
| Internal Arc Classification | IAC Classified | IAC Classified | IAC Classified | IAC Classified | IAC Classified |
| Internal Arc Withstand (kA) | TBA | TBA | TBA | TBA | TBA |
| Internal Arc Withstand Time (secs) | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 |
| Arc Vent Ducting | TBC | TBC | TBC | TBC | TBC |
| Accessibility | AFLR | AFLR | AFLR | AFLR | AFLR |
| Level of Service Continuity | LSC2A | LSC2A | LSC2A | LSC2A | LSC2A |
| Partition Class | PM | PM | PM | PM | PM |
| Circuit Rating (A) | 630 | 630 | 630 | 630 | - |
| Circuit Breaker |  |  |  |  |  |
| Nominal Rating (A) | 630 | 630 | 630 | 630 | - |
| Rated Short Time Withstand Current (Ik) (kA) | TBA | TBA | TBA | TBA | - |
| Rated Peak Withstand Current (Ip) (kA) | TBA | TBA | TBA | TBA | - |
| DC Offset Current at Breaker Opening (%) | 30.00 | 30.00 | 30.00 | 30.00 | - |
| Rated duration of fault (tk) (secs) | 3.00 | 3.00 | 3.00 | 3.00 | - |
| Interrupting Medium | Vacuum | Vacuum | Vacuum | Vacuum |  |
| Breaker Tripping | Shunt Trip | Shunt Trip | Shunt Trip | Shunt Trip | - |
| Breaker Undervoltage Release | Yes | Yes | Yes | Yes | - |
| Undervoltage Release Voltage | 110 V DC | 110 V DC | 110 V DC | 110 V DC |  |
| Breaker Closing | Solenoid | Solenoid | Solenoid | Solenoid | - |
| Circuit Breaker Operations (average/annum) | 20 | 20 | 100 | 20 | - |
| Circuit Breaker Actuation | Spring Charge | Spring Charge | Spring Charge | Spring Charge | - |
| Spring Charge Motor | 110 V DC | 110 V DC | 110 V DC | 110 V DC |  |
| Circuit Breaker Remote Operation Plug & Pendant | Yes, Close & Open | Yes, Close & Open | No | Yes, Close & Open | - |
| Circuit Breaker Remote Pendant Indication | Yes, Close & Open Indication | Yes, Close & Open Indication | - | Yes, Close & Open Indication | - |
| Castell Interlocking | No | No | No | No | - |
| Degree of Protection | IP4X | IP4X | IP4X | IP4X | IP4X |
| Degree of Protection Internal | IP20 | IP20 | IP20 | IP20 | IP20 |
| Panel Colour | B26 Orange To SANS 1091 | B26 Orange To SANS 1091 | E46 Light Admiralty Grey To SANS 1091 | E46 Light Admiralty Grey To SANS 1091 | B26 Orange To SANS 1091 |
| Circuit Earth Switch Required | Yes | Yes | No | No | No |
| Earth Switch Rated Short Time Withstand Current (Ik) | TBA | TBA | - | - | - |
| Earth Switch Rated Peak Withstand Current (Ip) | TBA | TBA | - | - | - |
| Protection C T | TBA/1; 10VA; 5P20 | TBA/1; 10VA; 5P20 | TBA/1; 10VA; 5P20 | - | - |
| Differential Protection C T | TBA | TBA | TBA | - | - |
| Metering C T | TBA/1, Class 0,5, 5VA | TBA/1, Class 0,5, 5VA | TBA/1, Class 0,5, 5VA | - | - |
| Core Balance C T | 100/1, 2 VA, 5P20 | 100/1, 2 VA, 5P20 | 100/1, 2 VA, 5P20 | - | - |
| Neutral C T (Sensitive Earth Fault) | TBA/1, 10 VA, 5P20 | 100/1, 10 VA, 5P20 | 100/1, 10 VA, 5P20 | - | - |
| Transformer NER C T | - | - | - | - | - |
| Voltage Transformer | - | - | - | - | xx/110; Class 0,5, 100VA |
| Voltage Transformer Primary/Secondary | - | - | - | - | Yyn |
| Voltage Transformer Connection | - | - | - | - | Busbar |
| Voltage Transformer Type | - | - | - | - | Withdrawable |
| Trip Circuit Supervision | Yes | Yes | Yes | Yes | - |
| Breaker Fail Protection | Yes | Yes | No | No | - |
| Protection Relays | Feeder Protection | Transformer Protection | Feeder Protection | - | - |
| Relay Specification | See elsewhere in document | See elsewhere in document | See elsewhere in document | - | - |
| Relay Inputs |  |  |  |  |  |
| Closing Supply On | Yes | Yes | Yes | - |  |
| VCB Racked In (Service Position) | Yes | Yes | Yes | - |  |
| VCB Spring Charged | Yes | Yes | Yes | - |  |
| O/C and E/F Relay Healthy | Yes | Yes | Yes | - |  |
| Upstream Breaker Closed | Yes | Yes | - | - |  |
| VCB No Volt Relay Healthy | Yes | Yes | Yes | - |  |
| Service Selected | Yes | Yes | Yes | - |  |
| VCB Open | Yes | Yes | Yes | - |  |
| VCB Closed | Yes | Yes | Yes | - |  |
| Arc Flash and Circuit Breaker Fail 1 | Yes | Yes | Yes | - |  |
| Arc Flash and Circuit Breaker Fail 2 | Yes | Yes | Yes | - |  |
| Switchgear Circuit Breaker Open Command | Yes | Yes | Yes | - |  |
| Mimic Open Command | Yes | Yes | Yes | - |  |
| Mimic Close Command | Yes | Yes | Yes | - |  |
| Tripping Supply On | Yes | Yes | Yes | - |  |
| Earth Switch Open | Yes | Yes | - | - |  |
| External Transformer Trips Healthy | Yes | Yes | - | - |  |
| Protection Relay Healthy | Yes | Yes | Yes | - | - |
| Relay Outputs |  |  |  |  |  |
| Relay Healthy | Yes | Yes | Yes | - |  |
| VCB Racked In (Service Position) | Yes | Yes | Yes | - |  |
| VCB Spring Charged | Yes | Yes | Yes | - |  |
| Protection Relay Annunciation | Yes | Yes | Yes | - |  |
| IDMT O/C Trip | Yes | Yes | Yes | - |  |
| Inst O/C Trip | Yes | Yes | Yes | - |  |
| E/F Trip | Yes | Yes | Yes | - |  |
| Undervoltage Trip | Yes | Yes | Yes | - |  |
| Upstream Supply Breaker Opened | - | - | Yes | - |  |
| PLC Trip | Yes | Yes | Yes | - |  |
| Fire Trip | - | - | Yes | - |  |
| Breaker Fail Trip | Yes | Yes | Yes | - |  |
| Transformer External Trips | Yes | Yes | - | - |  |
| Motor Thermal Trip | - | - | - | - |  |
| Internal Arc Protection | Yes | Yes | Yes | Yes | Yes |
| Current and Light | Yes | Yes | Yes | Yes | Yes |
| Busbar Compartment | Yes | Yes | Yes | Yes | Yes |
| Cable Compartment | Yes | Yes | Yes | - | - |
| Circuit Breaker Compartment | Yes | Yes | Yes | Yes | - |
|  |  |  |  | - |  |
| Differential Protection | TBA | TBA | - | No | - |
| Metering |  |  |  |  |  |
| Metering Unit 1 | Multi-Functional | Multi-Functional | Multi-Functional | - | - |
| Metering Unit 1 Communications | Modbus TCP/IP | Modbus TCP/IP | Modbus TCP/IP | - | - |
|  |  |  | - |  |  |
| Power Quality Meter | - | - | Yes | - | - |
| Protection Test Block | MMLG 1 | MMLG 1 | MMLG 1 | - | - |
| Metering Test Block | MMLG 1 | MMLG 1 | MMLG 1 | - | - |
| Selector Switches | Remote/ Off/ Maint | Remote/ Off/ Maint | Remote/ Off/ Maint | Remote/ Off/ Maint | - |
| Control Wiring | Minimum 1,5mm2 stranded copper | Minimum 1,5mm2 stranded copper | Minimum 1,5mm2 stranded copper | Minimum 1,5mm2 stranded copper | Minimum 1,5mm2 stranded copper |
| Control Wiring Colour | RW standard | RW standard | RW standard | RW standard | RW standard |
| Control wire identification system | Clip on, individual colour coded | Clip on, individual colour coded | Clip on, individual colour coded | Clip on, individual colour coded | Clip on, individual colour coded |
| Circuit Breaker Local Control |  |  |  |  |  |
| Trip Button | Yes | Yes | Yes | Yes | - |
| Hardwired Interlocks | Yes | Yes | Yes | Yes |  |
| Closing Supply On | Yes | Yes | Yes | Yes |  |
| VCB Racked In (Service Position) | Yes | Yes | Yes | Yes |  |
| VCB Spring Charged | Yes | Yes | Yes | Yes |  |
| O/C and E/F Relay Healthy | Yes | Yes | - | - |  |
| Upstream Breaker Closed | Yes | Yes | - | - |  |
| VCB No Volt Relay Healthy | Yes | Yes | Yes | Yes |  |
| Service Selected | Yes | Yes | Yes | Yes |  |
| VCB Open | Yes | Yes | Yes | Yes |  |
| Earth Switch Open | Yes | Yes | - | - |  |
| O/C & E/F & Transformer Trips Healthy | Yes | Yes | - | - |  |
| Power Factor Correction & Zorc Interlock | - | - | - | - |  |
| Interlocks Annunciator | Yes | Yes | Yes | Yes |  |
| Closing Supply On | Yes | Yes | Yes | Yes |  |
| VCB Racked In (Service Position) | Yes | Yes | Yes | Yes |  |
| VCB Spring Charged | Yes | Yes | Yes | Yes |  |
| O/C and E/F Relay Healthy | - | - | Yes | - |  |
| Upstream Breaker Closed | - | - | Yes | - |  |
| VCB No Volt Relay Healthy | Yes | Yes | Yes | Yes |  |
| Service Selected | Yes | Yes | Yes | Yes |  |
| VCB Open | Yes | Yes | Yes | Yes |  |
| Earth Switch Open | Yes | Yes | - | - |  |
| O/C & E/F & Transformer Trips Healthy | Yes | Yes | - | - |  |
| Power Factor Correction & Zorc and NVR Healthy | - | - | - | - |  |
| PLC Hardwired Inputs to outgoing terminals | - | - | - | Yes |  |
| Closing Supply On | - | - | Yes | Yes |  |
| VCB Racked In (Service Position) | - | - | Yes | Yes |  |
| VCB Spring Charged | - | - | Yes | Yes |  |
| Motor Protection Relay Healthy | - | - | - | - |  |
| VCB No Volt Relay Healthy | - | - | Yes | Yes |  |
| Service Selected | - | - | Yes | Yes |  |
| VCB Open | - | - | Yes | Yes |  |
| Earth Switch Open | - | - | - | - |  |
| Power Factor Correction & Zorc Interlock | - | - | - | - |  |
| PLC Hardwired Outputs to outgoing terminals |  |  |  |  |  |
| Breaker Close Contact | Yes | Yes | Yes | Yes |  |
| Breaker Open Contact | Yes | Yes | Yes | Yes |  |
| Remote Reset Contact | - | - | - | - |  |
| Local Indication |  |  |  |  |  |
| Circuit Breaker On | Yes | Yes | Yes | Yes | - |
| Circuit Breaker Off | Yes | Yes | Yes | Yes | - |
| Circuit Breaker Tripped | Yes | Yes | Yes | - | - |
| Circuit Instrument Panel Interior Illumination |  |  |  |  |  |
| Strip LED illumination | Yes | Yes | Yes | Yes | Yes |
| Circuit Anti-Condensation Heater |  |  |  |  |  |
| Cable Chamber | Yes | Yes | Yes | - | - |
| Busbar Chamber | No | No | No | No | - |
| Circuit Breaker Chamber | Yes | Yes | Yes | Yes | - |
| Heater Supply Voltage (Vac) | 230 | 230 | 230 | 230 | - |
| Cable Type | XX/XX kV XLPESWAPVC | XX/XX kV XLPESWAPVC | XX/XX kV XLPESWAPVC | - | - |
| Cable Size (mm2) | TBA mm2 3 core | TBA mm2 3 core | TBA mm2 3 core | - | - |
| No of Cables | TBA | TBA | TBA | - | - |
| Transformer Rating (kVA) | TBA | TBA | TBA | - | - |
| Transformer FLC (A) | TBA | TBA | TBA | - | - |
| Transformer Ratio | XX/XX/0.4kV | XX/XX/0.4kV | XXkV | - | - |
| Transformer Impedance (%) | - | - | - | - | - |
| Transformer Vector Group | dY | dY | YNd1 | - | - |
| Transformer Earth Fault Current Transformer | 100/1 | 100/1 | - | - | - |
| LV Grounding | NER- Limited to 350 A | NER- Limited to 350 A | TBA | - | - |

# PROTECTION RELAY SPECIFICATIONS

  - FEEDER PROTECTION RELAY SPECIFICATION

| Requirement | Transformer Feeder | Cable Feeder |
| --- | --- | --- |
| IEC-ANSI Functionality Minimum Requirements |  |  |
| Undervoltage | 27 |  |
| Negative Sequence Inst. Overcurrent | 46/50 |  |
| Negative Sequence Time Overcurrent | 46/51 |  |
| Negative Sequence Voltage | 47 |  |
| Breaker Failure | 50 BF |  |
| Phase Instantaneous Overcurrent | 50P |  |
| Neutral Instantaneous Overcurrent | 50N |  |
| Ground Instantaneous Overcurrent | 50G |  |
| Phase Time Overcurrent | 51P |  |
| Neutral Time Overcurrent | 51N |  |
| Ground Time Overcurrent | 51G |  |
| Overvoltage | 59 |  |
| Trip Curves ANSI |  |  |
| Extremely Inverse | Yes |  |
| Very Inverse | Yes |  |
| Normally Inverse | Yes |  |
| Moderately Inverse | Yes |  |
| Definite Time | Yes |  |
| Trip Curves IEC |  |  |
| Curve A (BS142) | Yes |  |
| Curve B (BS142) | Yes |  |
| Curve C (BS142) | Yes |  |
| Short Inverse | Yes |  |
| Protection Setting Groups | Four |  |
| Protection Function Setting Accuracy and Resolution |  |  |
| PHASE/NEUTRAL/GROUND/NEGATIVE SEQUENCE TIME OVERCURRENT PROTECTION |  |  |
| Pickup level: 0.05 to 20.00 in steps of 0.01 x CT | Yes |  |
| Dropout level: 97 to 98% of Pickup | Yes |  |
| Definite time: (0.1 s base curve) | Yes |  |
| Curve multiplier: 0.00 to 100.00 in steps of 0.01 | Yes |  |
| Reset type: Instantaneous/linear | Yes |  |
| PHASE/NEUTRAL/GROUND/NEGATIVE SEQUENCE INSTANTANEOUS OVERCURRENT PROTECTION |  |  |
| Pickup level: 0.05 to 20.00 in steps of 0.01 x CT | Yes |  |
| Dropout level: 97 to 98% of pickup | Yes |  |
| Time delay: 0.00 to 600.00 in steps of 0.01s | Yes |  |
| Timing accuracy: At 0 ms time delay (no intentional delay) | Yes |  |
| UNDERVOLTAGE |  |  |
| Minimum voltage:> programmable threshold from 0.00 to 1.25 x VT in steps of 0.01 | Yes |  |
| Pickup level: 0.00 to 1.25 in steps of 0.01 x VT | Yes |  |
| Dropout level: 102 to 103% of pickup | Yes |  |
| Curve: Definite time or inverse time | Yes |  |
| Time delay: 0.0 to 6000.0 in steps of 0.1 s | Yes |  |
| Phases: Any one/any two/all three (programmed) to operate for output | Yes |  |
| Level accuracy: Per voltage input | Yes |  |
| OVERVOLTAGE |  |  |
| Pickup level: 0.00 to 1.25 in steps of 0.01 x VT | Yes |  |
| Dropout level: 97 to 98% of pickup | Yes |  |
| Time delay: 0.0 to 6000.0 in steps of 0.1 s (definite time) | Yes |  |
| Phases: Any one/any two/all three (programmable) phases have to operate for output | Yes |  |
| Level accuracy: Per voltage input | Yes |  |
| Timing accuracy: ±100 ms | Yes |  |
| BREAKER FAILURE |  |  |
| Pickup level: 0.05 to 20.0 x CT in steps of 0.01 | Yes |  |
| Dropout level: 97 to 98% of pickup | Yes |  |
| Time delay: 0.03 to 1.00 s in steps of 10 | Yes |  |
| Timing accuracy: ±20 ms error | Yes |  |
| Level accuracy: per CT input | Yes |  |
| Protection Relay 1 Digital Inputs | See Switchgear Specification |  |
| Protection Relay 1 RTD Inputs |  |  |
| Input 1 | - |  |
| Input 2 | - |  |
| Input 3 | - |  |
| Protection Relay 1 Outputs | See Switchgear Specification |  |
| Protection Relay LED Annunciation | See Switchgear Specification |  |
| Relay Display | 40 character display of actual values, setpoints and user defined and default messages |  |
| Measurement Functions: |  |  |
| All three phase currents and neutral current | Yes |  |
| All three phase voltages and phase to neutral voltages | Yes |  |
| Apparent power (kVA) | Yes |  |
| Reactive power (kVAr) | Yes |  |
| Active power (kW) | Yes |  |
| Power factor | Yes |  |
| Frequency | Yes |  |
| Reactive energy (kVArh) | Yes |  |
| Active power (kWh) | Yes |  |
| Relay Self Test Features: | Yes |  |
| Self-diagnostics to be performed at after power-up, and continuously thereafter. Self test failures to be selective such as major failures which can disable protection features, and minor failures, which just alarm. |  |  |
| Monitoring |  |  |
| Breaker Conditions: | Yes |  |
| The device calculates the wear on the breaker contacts on each phase to establish a threshold. |  |  |
| When user determined breaker maintenance threshold is exceeded the relay can trigger an alarm. |  |  |
| VT failure: | Yes |  |
| Each phase of the VT to be monitored and an alarm and trigger of a programmable output is generated when a supply failure is detected. |  |  |
| Event recording: | Yes |  |
| Storage of a minimum of last 100 events, recording the time, date, cause, and system parameters. |  |  |
| Category of events may be recorded selectively, |  |  |
| Oscillography: | Yes | Yes |
| Configurable memory to be provided for recording of all AC input voltages and currents and the status of the status of logic inputs and output relays. Between 2 to 16 blocks with up to 16 to 128 power frequency cycles of data to be available. The amount of pre-event trigger data to be configurable. Trace to be triggered by selected features, logic inputs or output relays. | Yes | Yes |
| Data logging: | Yes |  |
| A configurable memory block to be provided to record 8 channels of any measured or calculated parameter. |  |  |
| Resolution configurable to store 60 seconds of data showing every power frequency cycle or 20 weeks with hourly data. |  |  |
| Relay Communication Ports |  |  |
| RS232 in front of relay | Yes |  |
| RS485/422 at back of the relay | Yes |  |
| TCP/IP Ethernet port at back of the relay | Yes |  |
| Communication Speed | Up to 19,2kbps |  |

  - GENERATOR PROTECTION RELAY SPECIFICATION

| Requirement | Specification |
| --- | --- |
| CT input | 1A or 5A selectable |
| VT input | 3 phase star connection 110 V |
| Protection Relay- IEC-ANSI Functionality |  |
| Stator earth fault 90 % | 64, 59N, 67N |
| Overcurrent time | 50, 51V |
| Unbalanced load | 46 |
| Stator overload | 49 |
| Overvoltage | 59 |
| Frequency f > | 81 |
| Frequency f < | 81 |
| Reverse power | 32 |
| Motor Overload Protection | A minimum of 5 standard overload curves to be provided. |
|  | Custom overload curves functionality. |
|  | Thermal capacity biasing for negative sequence currents to be provided. |
|  | RTD thermal capacity biaising, and the application of motor running and stopped cooling |
|  | time constants. |
|  | Thermal capacity calculation and start inhibit due to insufficient available thermal capacity. |
| Protection Settings Capability |  |
| 51 OVERLOAD/STALL/THERMAL MODEL |  |
| Curve Shape: | 1 to 15 standard, custom |
| Curve Biasing: | Unbalance, temperature, hot/cold ratio, cool time constants |
| Pickup Level: | 1.01 to 1.25 × FLA |
| Dropout Level: | 96 to 98% of pickup |
| Timing Accuracy: | ±100 ms or ±2% of total trip time |
| 50 SHORT CIRCUIT |  |
| Pickup Level: | 2.0 to 20.0 × CT in steps of 0.1 |
| Dropout Level: | 96 to 98% of pickup |
| Time Delay: | 0 to 255.00 s in steps of 0.01 s |
| Backup Delay: | 0.10 to 255.00 s in steps of 0.01 s |
| Timing Accuracy: | +50 ms for delays <50 ms |
|  | ±100 ms or ±0.5% of total trip time |
| 50G/51G 50N/51N GROUND FAULT |  |
| Pickup Level: | 0.25 to 25.00 A for 50:0.025 CT |
| Dropout Level: | 96 to 98% of pickup |
| Time Delay: | 0 to 255.00 s in steps of 0.01 s |
| Backup Delay: | 0.01 to 255.00 s in steps of 0.01 s |
| Timing Accuracy: | +50 ms for delays <50 ms |
|  | ±100 ms or ±0.5% of total trip time |
| 46 UNBALANCE |  |
| Pickup Level: | 4 to 30% in steps of 1 |
| Pickup Accuracy: | ±2% |
| Dropout Level: | 1 to 2% below pickup |
| Time Delay: | 1 to 255 s in steps of 1 |
| Start Delay: | 0 to 5000 s in steps of 1 |
| Timing Accuracy: | ±500 ms or ±0.5% of total time |
| 27 UNDERVOLTAGE |  |
| Pickup Level: | 0.50 to 0.99 × rated in steps of 0.01 |
| Dropout Level: | 102 to 104% of pickup |
| Time Delay: | 0.0 to 255.0 s in steps of 0.1 |
| Start Delay: | separate level for start conditions |
| Timing Accuracy: | +75 ms for delays <50 ms |
|  | ±100 ms or ±0.5% of total trip time |
| 59 OVERVOLTAGE |  |
| Pickup Level: | 1.01 to 1.25 × rated in steps of 0.01 |
| Dropout Level: | 96 to 98% of pickup |
| Time Delay: | 0.0 to 255.0 s in steps of 0.1 |
| Timing Accuracy: | ±100 ms or ±0.5% of total trip time |
| STARTER FAILURE |  |
| Pickup level: | motor run condition when tripped |
| Dropout level: | motor stopped condition |
| Time delay: | 10 to 1000 ms in steps of 10 |
| Timing accuracy: | ±100 ms |
| Protection Relay 1 Digital Inputs | See Switchgear Specification |
| Protection Relay 1 RTD Inputs |  |
| Input 1 | Motor Winding Red Phase |
| Input 2 | Motor Winding White Phase |
| Input 3 | Motor Winding Blue Phase |
| Protection Relay 1 Outputs | See Switchgear Specification |
| Metering |  |
| All three phase currents and neutral current | Yes |
| All three phase voltages and phase to neutral voltages | Yes |
| Apparent power (kVA) | Yes |
| Reactive power (kVAr) | Yes |
| Active power (kW) | Yes |
| Power factor | Yes |
| Frequency | Yes |
| Reactive energy (kVArh) | Yes |
| Active power (kWh) | Yes |
| STATUS INDICATORS GROUP 1 | LED indication of motor stopped, starting, running, overloaded or locked out |
| STATUS INDICATORS GROUP 2 | LED indication of activation of every output and relay self diagnostic failure |
| DISPLAY | 40 Character alpha-numeric LCD display for viewing actual values, alarm and trip messages and programming setpoints |
| Parameters to be available for display | Average and individual phase currents |
|  | RTD temperatures (hottest, individual, maximum) (R Option) |
|  | Current Unbalance |
|  | Ground leakage current |
|  | Thermal capacity remaining/estimated time to trip at present overload level |
| Parameters to be available for display | Motor load as a percent of full load |
|  | Phase-to-phase or phase-to-neutral voltage |
|  | Power |
|  | Reactive power |
|  | Power factor |
|  | Frequency |
| KEYPAD | Used to navigate the LCD display and the help function. |
|  | Multi level password protection |
| EVENT RECORD |  |
| Capacity: | last 512 events |
| Triggers: | Trip, inhibit, power fail, alarms, self test, waveform capture |
| WAVEFORM CAPTURE |  |
| Length: | 3 buffers containing 16 cycles of all current and voltage channels |
| Trigger position: | 1 to 100% pre-trip to post-trip |
| Trigger: | From trip, manually via communications or digital input |
| MOTOR START DATA LOGGER |  |
| Length: | 6 Buffers containing 30 seconds of motor start data. |
| Trigger: | Motor Start Status. |
| Trigger position: | 1-second pre-trigger duration. |
| Logging rate: | 1 sample/200ms. |
| Learn functionality | Yes |
| Statistical Data | Record of the following |
|  | Total running hours |
|  | Number of motor starts |
|  | Total number of motor trips |
|  | Breakdown of types of motor trips |
| Protection Relay Communications | RS232 in front of relay |
|  | RS485/422 at back of the relay |
|  | TCP/IP Ethernet port at back of the relay |

  - MULTI-FUNCTION METERING UNIT SPECIFICATION

Multi-Function Meter Specification

CT input: 1A or 5A Primary current up to 1 250 A

VT input: 3 phase star connection 110 V Primary Voltage 11 000 V (to suit MV board voltage)

Control power: 110 V DC

Instantaneous rms values:

Current per phase, neutral and ground

Voltage Total, per phase , phase to phase and phase to neutral

Frequency

Real, reactive, and apparent power total and per phase Signed, Four Quadrant

True Power Factor Total and per phase Signed, Four Quadrant

Displacement PF Total and per phase Signed, Four Quadrant

% Unbalanced I per phase and total,

% Unbalanced Voltage phase to neutral, phase to phase

Energy values:

Accumulated Active, Reactive and Apparent Energy Received/Delivered; Net and absolute

Demand values:

Current average Present, Last, Predicted, Peak, and Peak Date Time

Active power Present, Last, Predicted, Peak, and Peak Date Time

Reactive power Present, Last, Predicted, Peak, and Peak Date Time

Apparent power Present, Last, Predicted, Peak, and Peak Date Time

Peak demand with time stamping D/T for current and powers

Power quality measurements:

Total Harmonic Distortion, Current per phase and Total, Voltage Total, phase to phase and phase to neutral

Individual harmonics (odds) up to the 15th Current per phase and Total, Voltage Total, phase to phase and phase to neutral

True rms sampling rate: 64 samples per cycle

EMC compatibility: IEC 61000

Display: Minimum of four parameters at a time

Keypad: Navigate instantaneous and cumulative/minimum/maximum values

Alarm log with date and time stamping

Compliance: IEC 61557-12 Class 0,5

# ADDITIONAL MEDIUM VOLTAGE SWITCHGEAR TIER AT ZUIKERBOSCH ENGINE ROOM 4A/4B

  - An additional tier complete with a joggle chamber if required shall be designed, manufactured, installed and commissioned at either the Engine Room 4A or Engine Room 4B.

  - The requirements for the additional tier is as for an Incomer as mentioned previously.

  - Any synchronisation and Castell interlocking requirements between the Zuikerbosch/ Forebay feeder and this switchgear tier shall be included.

# MEDIUM VOLTAGE SWITCH ROOM REQUIREMENTS

  - Each medium voltage switchboard shall be housed in a dedicated switchgear room for that switchboard.

  - The switch rooms shall be compliant with the seismic requirements of the sites where they are installed.

  - The structural stability of the switch room (floor, walls and roof) shall be designed for a catastrophic failure of the switchgear as a result of any venting of gases due to a full prospective short circuit occurring on any circuit of the switchboard. Pressure relief measures shall be built into the room with no compromise on safety of personnel or an arc venting duct must be installed.

  - The clearances around each switchboard shall be as follows:

    - Rear- Not less than 1500 mm but not exceeding 1800 mm at every point of the switch room. There should be a minimum of 1000mm from top of panel to ceiling, if arc venting duct is not installed.

    - Front- Double the depth of the switchboard at every point along the length of the switchboard to allow for the withdrawal and handling of circuit breakers.

    - Sides- 2500 mm on each side of the switchboard.

  - Heating, Ventilation and Air Conditioning (Part. 2 of IEC 62271-1)

    - The ambient air temperature shall not exceed 35°C and its average value, measured over 24 hours, must not exceed 30°C.  The minimum ambient air temperature will be -5°C

    - The average relative humidity measured over 24 hours must not exceed 95%; average water vapour pressure measured over 24 hours must not exceed 2,2 kPa; average relative humidity over one month must not exceed 90% and average water vapour pressure measured over one month must not exceed 1,8 kPa.

  - The correct positioning of control, communications and power cable entries to the switchgear from either a cable basement or cable duct below shall be specifically determined. The switchgear placement taking into account the switchgear clearances required in clause 7.4 shall be complied with. NO top entry cable installation will be accepted.

  - Purpose formed cable ducts or an entry into a cable basement shall be provided below the switchgear to meet amongst other the following requirements:

    - The depth of the cable duct shall be such that cables below the switchgear shall be installed vertically against the cable duct wall.

    - The minimum bending radii requirement for all cables installed in the cable duct shall be met.

    - Suitable chamfering of 90° bends in the cable ducts shall be provided to cater for cable bending radii.

    - The separation requirements to any communication cables to prevent EMC interference shall be complied with.

    - Wherever possible the cable duct width shall be such that no additional supports for the switchgear straddling the duct shall be required. If additional support is required it shall be horizontal across the duct and not to the duct floor.

  - Where required the switchgear supplier and installer will install custom manufactured frames for the mounting of switchgear tiers. Where frames are to be cast into the floor this shall be co-ordinated with the casting of concrete and shall meet the switchgear suppliers’ requirements and specification. The required tolerances in levels by the switchgear supplier in all directions shall be met. A certificate with specific level measurements and tolerances shall be signed off by the switchgear supplier.

  - The switchgear rooms shall be equipped with a double door with sufficient dimensions (width and especially height) to enable the switchgear to be installed into the room. Particular attention shall be paid to the landing area outside the doors, preferably a concrete base to enable the switchgear tier sections to be placed comfortably and safely for further installation into the switchgear room.

  - Each switchgear room shall be provided with two doors preferably at opposite ends of the room for access by operating and maintenance personnel and providing an escape route out of the room. The doors shall be provided with panic bar ironmongery to facilitate the easy egress from the room.

  - The switchgear installer shall install one lockable steel enclosure correctly dimensioned for the secure and lockable storage of one spare circuit breaker truck which shall be supplied for each switchboard. In the same vicinity the switchgear installer will install a wall mounted cabinet of approximately 1600mm wide and 1600mm high for any switchgear operating tools. A storage space shall be allowed for any trolley to facilitate the withdrawal and insertion of switchgear trucks. Stepladder, with wheels, required if control cubicle is higher than 1.8m.

  - The roof or ceiling height of the switch room shall be minimum 3 000mm from finished floor level to meet the switchgear arc venting requirements, but shall be determined by the final fault rating of the switchgear and the switchgear suppliers arc venting design including possible arc vent ducting, plasma deflectors and absorbers.

  - The contractor shall interface with the switchgear supplier for the installation of possible arc vent ducting above the switchgear and to exit ducts. The roof and wall designs shall accommodate these requirements.

  - The effect of possible solar radiation and heating on the switchgear shall be taken into account. Preferably no windows directly in front of, behind, or on the sides of the panel. This introduces extra heat.

  - The contractor shall take measures to prevent the ingress of dust into the switchgear room.

  - No PLC panel, Battery Charger, Batteries and UPS’s shall be housed in the any medium voltage switch room.

# NEUTRAL EARTHING COMPENSATORS

  - The requirement for a NECRT on the generator bus or on the Distribution system shall be considered by the Contractor.

  - If NECRT’s are required they shall comply with the following requirements:

    - Type

      - The units shall be oil filled, naturally cooled, free breathing, zig-zag connected three phase 50 Hz NEC combined with current limitation resistor NER.

      - The windings shall be of high conductivity copper.

      - The core and winding assembly shall be correctly located on the tank bottom and adequately braced.

      - The current limiting resistor shall be suitably insulated to withstand full line voltage and securely located in the same oil filled tank as the NEC.

      - The resistor shall be of stainless steel (or similar) material.

      - Where the resistor is built from a large number of series connected grids, the welding method of connecting these grids is preferred.

      - Electrical stresses on resistor insulation shall be defined, i.e.: no construction metal pieces may be at "floating" potential.

      - To prevent entry of gas developed during normal NER operation into gas and oil operated relay, a suitable gas trap shall be provided above the NER only. This trap shall be vented to the conservator by-passing the relay. Reaction of the relay to the NEC winding faults may not be affected.

    - Main terminals

      - The NER to earth connection shall be brought out of the tank through an outdoor bushing complying with SANS 833.

      - The supply terminals shall be brought out through bushings into an air filled cable box having a removable gland plate suitable for XLPE cable heat shrink termination

    - Current transformers

      - The NEC/NER shall be fitted with two 300/1 ratio current transformers in the neutral connection on the earthed end.

      - Both CT's shall be Class X 15 VA. Their knee point voltage shall be 30 volts and they shall be compatible with the protection relays installed on the MV switchgear.\

      - The NEC/NER shall be fitted with:

        - Oil conservator with oil level indicator;

        - Gas and oil actuated relay;

        - Dehydrating breather;

        - Dial type top oil thermometer having alarm and trip contacts;

        - Check thermometer pocket;

        - Rating and diagram plate;

        - Drain valves;

        - Skid underbase;

        - Tank earth stud.

    - Painting

      - Painting to coastal area standards.

    - Auxiliary cable box

      - An auxiliary cable box with terminals and removable gland plate for PVC cable compression glands is to be fitted for all small wiring on the NEC/NER.

    - Ratings

      - It is required that the NEC/NER combination shall limit earth fault currents to the order of 300 to 355 amps taking into account manufacturing tolerances and system parameters.

      - The maximum continuous neutral current shall be taken as 15 amperes.

    - Overfluxing

      - The NEC/NER must be suitable of withstanding 1,15 times the relevant system nominal voltage on the main transformer terminals and the NEC/NER shall be designed to operate continuously at this level.

    - Short-Time Currents

      - The NEC and NER shall be capable of withstanding 355 amps in the neutral connection and 118 amps in each phase of the NEC for 10 seconds without exceeding the temperature rise limits below

    - Temperature rise limits

      - Top oil temperature rise resulting from the magnetisation losses plus the losses due to the maximum continuous neutral current shall be 55°C. Temperature rise of the metallic resistor resulting from the load described in 8.10above shall be 60°C.

      - Average NEC winding temperature rise resulting from the load described in Clause 8.10 above shall be 65°C.

# TURBINE GENERATOR, EXCITATION AND SYCHRONISATION SYSTEMS

  - The generator shall be a synchronous generator with a static or brushless excitation system.

  - The generator and bearings shall be designed to withstand the runaway speed of the turbine for the time required for the controlled closing of the main inlet valve.

  - The generator shall comply with the applicable sections of the SANS/IEC 60034 standard.

  - The generator stator insulation system shall be Class F with a Class B temperature rise.

  - The generator and excitation system shall be provided with sufficient monitoring and protection devices for the safe operation of the Generating Plant.

  - As a minimum this shall include:

    - Stator temperature monitoring

    - Bearing oil level monitoring

    - Bearing temperature monitoring

    - Cooling water circulation monitoring

    - Overcurrent protection (stator and rotor)

    - Earth fault protection (stator and rotor).

    - Under and over voltage protection

    - Under and over frequency protection

    - Reverse Power protection

    - Generator differential protection

  - Cooling system

    - Where possible, air cooling of the generator and bearings is preferred.

    - Where water cooling is necessary, the design must include means to ensure there is no possibility of contamination of the discharged cooling water. The tender shall provide information on the design methods employed.

  - Synchronisation Systems

    - Synchronisation systems shall be provided to synchronise the two generators at Zoekfontein and to synchronise the generation system to the Zuikerbosch system at the Zuikerbosch/ Forebay substation.

# 400V DISTRIBUTION SWITCHBOARDS

| 400V DISTRIBUTION BOARD DESIGN CRITERIA |  |  |
| --- | --- | --- |
| POWER SUPPLY TO LV DISTRIBUTION BOARD |  |  |
| Supply details: | 400 | V ac |
| Supply voltage variations | -15% and +10% |  |
| Supply Frequency Variations | ± 2.5 | % |
| Total Harmonic Content | < 3% up to 25th harmonic |  |
| Supply Transformers | TBA kVA |  |
| Ratio | xx/0.4 kV |  |
| Impedance | TBA% |  |
| Vector Group | Dyn11 |  |
| CURRENT RATINGS |  |  |
| Rated Operational Current In | TBA | A continuous |
| Complete Busbar System Derating Factor | 0.85 |  |
| Short Circuit Rating Icw | 50 | kA for 1 second |
| Operating configuration | The short circuit rating of the switchboard shall be suitable for paralleling of two incoming transformers even though this will not be the normal operating mode |  |
| Rated Peak Withstand Ipk | TBA | kA |
| Internal arc rating | TBA | kA |
| VOLTAGE RATINGS & INSULATION SYSTEM REQUIREMENTS |  |  |
| Rated voltage Ue | 400 | V |
| Insulation Ui | 1 000 | V |
| Impulse Withstand Level | 6 | kV peak |
| BUSBAR SYSTEM |  |  |
| Busbars: |  |  |
| Busbar Material | High Conductivity Copper |  |
| Busbar Nominal Rating | TBA | A |
| Rated Diversity Factor | 1 |  |
| Busbar Maximum Current Density | 1,55 | A/mm2 |
| Neutral Busbar Rating | >=500 | A |
| System of Earthing | TNCS |  |
| TEMPERATURE RISE SPECIFICATION |  |  |
| Assembly Temperature Rise Limit |  | °C above ……°C |
| Busbar Support Temperature Rise |  | °C above ……°C |
| Maximum Busbar Temperature Rise | 50 | °C above 40°C |
| OTHER |  |  |
| Place of Installation | Indoor Closed Room |  |
| Form | 2b & 3b |  |
| IP rating | 55 |  |
| Type of access: | Front and Rear |  |
| Type of entry: | Bottom Cable Entry |  |
| Type of mounting: | Solid floor |  |
| Enclosure materials: | Mild Steel |  |
| Door Thickness: | 1,6 | mm minimum |
| Chassis Plate Thickness: | 1,6 | mm minimum |
| Finish | Powder Coated Structured |  |
| Colour: | B26 to SANS 1091 | Normal Section |
|  | A11 to SANS 1091 | Emergency Section |
|  | F01 to SANS 1091 | UPS Distribution |
|  | G12 to SANS 1091 | 110 V DC Distribution |
| Certification required | Approved performance to SANS 1973-1 |  |
| Special environmental conditions: | None |  |
| Humidity | 80 | % |
| Maximum Ambient Temperature | 40 | °C |
| Minimum Ambient Temperature | -5 | °C |
| Altitude | 1590 m | AMSL |
| Rapid temperature variations | No |  |
| Pollution level: | Dust |  |
| Exposure to magnetic fields | Site Specific |  |
| Direct radiation from the sun/furnaces | No |  |
| Attacks by fungi /Small creatures | Yes |  |
| Fire / Explosive environment | No |  |
| EMC environmental requirements | No |  |
| Fixed DISTRIBUTION BOARDBs | Yes |  |
| SCPD / Motor starter coordination | Type II Coordination |  |
| EQUIPMENT SPECIFICATIONS: |  |  |
| INCOMER AND BUS-SECTION MOULDED CASE CIRCUIT BREAKERS or ACB: | TBA |  |
| RATINGS AND CONFIGURATION | TBA |  |
| Rated Operational Voltage (Ue) | 690 V |  |
| Rated Insulation Voltage (Ui) | 800 V |  |
| Rated Impulse Withstand Voltage (Ue) | V |  |
| Rated Uninterrupted Current (Iu) at 40˚C | TBA A |  |
| Rated Ultimate Short Circuit Breaking Capacity (Icu) | TBA kA |  |
| Rated Service Short Circuit Breaking Capacity (Ics) | 100% of Icu |  |
| Rated Short Time Withstand Current (Icw) (1 sec) | TBA kA |  |
| Poles | Four |  |
| Neutral Pole Current Carrying Capacity (%Icu) | 100 |  |
| Mounting configuration | Horizontal Drawout |  |
| SAFETY FEATURES |  |  |
| All poles shall operate simultaneously for circuit breaker opening, closing and tripping. | Yes |  |
| MCCBs shall be actuated by a toggle or handle that clearly indicates the three positions: ON, OFF and TRIPPED. | Yes |  |
| Suitability for isolation complying with SANS/IEC 60947-2 | Yes |  |
| The operating mechanism shall be such that the toggle or handle can only be in OFF position (O) if the power contacts are all actually separated, in OFF position, the toggle or handle shall indicate the isolation position. | Yes |  |
| Isolation shall be provided by a double break on the main circuit. | Yes |  |
| MCCB shall be able to receive a device for locking in the “isolated” position, with up to 3 padlocks. | Yes |  |
| MCCBs shall be designed to prevent access to live parts when the cover is removed. | Yes |  |
| MCCBs shall be equipped with a “push to trip” button in front to test operation and the opening of the poles. | Yes |  |
| MCCB rating, “push to trip” button, performances and contact position indication must be clearly visible and accessible from the front, through the front panel or the door of the switchboard. | Yes |  |
| ACCESSORIES |  |  |
| Motor mechanism | Yes 110 V DC |  |
| An “auto/manual” switch in front shall, when set to the “manual” position, lock out electrical control; when set to “auto”, lock out the manual control; remote indication of “manual” or “auto” mode shall be possible. It shall also be possible to control the access to the “auto” control. | Yes |  |
| Closing shall take place in less than 80 ms. | Yes |  |
| The operating mechanism shall be of the stored-energy type only | Yes |  |
| The addition of a motor mechanism or a rotary handle shall in no way affect circuit breaker characteristics | Yes |  |
| Electronic Trip Module | Yes 110 V DC |  |
| Residual Current Module | Yes 110 V DC |  |
| Shunt Trip | Yes 110 V DC |  |
| Undervoltage Release | Yes 110 V DC |  |
| Auxiliary Contacts | Two NO and NC each One “TRIPPED” Position Carriage Inserted Changeover Contact Carriage Withdrawn Changeover Contact |  |
| Mechanical Operations Counter | Yes |  |
| Lockout key provision | Yes |  |
| PROTECTION UNIT FUNCTIONALITY |  |  |
| Electronic Protection Unit Protection: | Yes |  |
| Power for protection shall be from current transformers and shall operate at currents as low as 5% of the nominal rating | Yes |  |
| Overload Protection (L) adjustable for current and time | Yes |  |
| Thermal memory for overload protection | Yes |  |
| IDMT Short Circuit Protection (S)adjustable for time and current | Yes |  |
| Instantaneous Short Circuit Protection (I) adjustable in several thresholds | Yes |  |
| Ground Fault Protection Module adjustable for time and current up to 1000mA | Yes |  |
| Programming of protection unit | Keypad or RS232 or USB interface |  |
| Measurement: |  |  |
| Power for protection shall be from current transformers and shall operate at currents as low as 5% of the nominal rating | Yes |  |
| Parameters to be measured: |  |  |
| All three phase currents and neutral current | Yes |  |
| All three phase voltages and phase to neutral voltages | Yes |  |
| Indication of all measured parameters | Yes |  |
| Visual Indication |  |  |
| Trip indication of L, S and I breaker trips | Yes |  |
| Trip indication of RCD device | Yes |  |
| Communication: |  |  |
| Facility to communicate on Ethernet IP and Profibus | Yes |  |
| MULTI FUNCTION METER SPECIFICATION |  |  |
| CT input: 1A or 5A Primary current up to 1 250 A | Yes |  |
| VT input: 3 phase star connection 400/231 V | Yes |  |
| Control power: 110 V DC or 231 AC UPS | Yes |  |
| Instantaneous rms values: |  |  |
| Current per phase, neutral and ground | Yes |  |
| Voltage Total, per phase , phase to phase and phase to neutral | Yes |  |
| Frequency | Yes |  |
| Real, reactive, and apparent power total and per phase Signed, Four Quadrant | Yes |  |
| True Power Factor Total and per phase Signed, Four Quadrant | Yes |  |
| Displacement PF Total and per phase Signed, Four Quadrant | Yes |  |
| % Unbalanced I per phase and total, | Yes |  |
| % Unbalanced Voltage phase to neutral, phase to phase | Yes |  |
| Energy values: |  |  |
| Accumulated Active, Reactive and Apparent Energy Received/Delivered; Net and absolute | Yes |  |
|  | Yes |  |
| Demand values: | Yes |  |
| Current average Present, Last, Predicted, Peak, and Peak Date Time | Yes |  |
| Active power Present, Last, Predicted, Peak, and Peak Date Time | Yes |  |
| Reactive power Present, Last, Predicted, Peak, and Peak Date Time | Yes |  |
| Apparent power Present, Last, Predicted, Peak, and Peak Date Time | Yes |  |
| Peak demand with time stamping D/T for current and powers | Yes |  |
| Power quality measurements |  |  |
| Total Harmonic Distortion, Current per phase and Total, Voltage Total, phase to phase and phase to neutral | Yes |  |
| Individual harmonics (odds) up to the 15th Current per phase and Total, Voltage Total, phase to phase and phase to neutral | Yes |  |
| True rms sampling rate: 64 samples per cycle | Yes |  |
| EMC compatibility: IEC 61000 | Yes |  |
| Display: Minimum of four parameters at a time | Yes |  |
| Keypad: Navigate instantaneous and cumulative/minimum/maximum values | Yes |  |
| Alarm log with date and time stamping | Yes |  |
| Compliance: IEC 61557-12 Class 0,5 | Yes |  |
| MoDBus TCP/IP Interface | Yes |  |

  - Distribution Boards Sections

    - The 400V Distribution Boards shall include the following:

      - Two incomers, one from each transformer tertiary winding. Incomers and bus-sections are specified as above.

      - Bus-section per board

      - Circuits dedicated per turbine shall be on the bus with the same transformer connected to the medium voltage circuit e g BG3 turbine to Transformer 2 low voltage.

      - A 110VDC distribution section, should be as per the typical single line diagram and shall be powder coated Dark Admiralty Grey G12, to SANS 1091:2012.

      - A 231VAC UPS distribution section for the Turbine UPS system, as per the single line diagram and load list and shall be powder coated Royal Blue, F01, to SANS 1091:2012.

      - A 400VAC essential services distribution section, as per the single line diagram and load list and shall be powder coated Signal Red A11, to SANS 1091:2012.

      - Suitably rated surge arrestors.

  - Circuits Per Power Supply Category

The following circuits shall be allowed for, as a minimum, in the Zoekfontein and Zuikerbosch/Forebay Low Voltage Distribution Boards, per category of power supply:

    - Normal Raw Power

| Description |  |
| --- | --- |
| Zoekfontein | Zuikerbosch/Forebay |
| Cathodic Protection Feeder 1 | ------- |
| Turbine 1 Auxiliaries Distribution Board | ------- |
| Turbine 2 Auxiliaries Distribution Board | ------- |
| Welding Plug 1 | ------- |
| Welding Plug 2 | ------- |
| Spare Feeder 1 | ------- |
| Spare Feeder 2 | ------- |
| Spare Feeder 3 | ------- |

    - Essential Services Power (Generator Backed Up)

| Description |  |
| --- | --- |
| Zoekfontein | Zuikerbosch/Forebay |
| Generator 1 Auxiliaries and Excitation System | Area Lighting Feeder 1 |
| Generator 2 Auxiliaries and Excitation System | Building Small Power and Lighting DB Feeder |
| Crane Feeder 1 | Central UPS Feeder |
| Crane Feeder 2 (Future) | Sump Pump Control Panel 1 |
| Area Lighting Feeder 1 | Spare Feeder 1 |
| Area Lighting Feeder 2 (Future) | Spare Feeder 2 |
| Turbine Hall Small Power and Lighting Upper Level DB Feeder | Spare Feeder 3 |
| Electrical Building Small Power and Lighting DB Feeder | 110 V DC Battery Charger Feeder |
| 110 V DC Battery Charger Feeder | ------- |
| Turbines UPS Feeder | ------- |
| Control Room UPS Feeder | ------- |
| Sump Pump Control Panel 1 | ------- |
| Sump Pump Control Panel 2 | ------- |
| Spare Feeder 1 | ------- |
| Spare Feeder 2 | ------- |
| Spare Feeder 3 | ------- |

    - Turbine UPS Power Distribution

| Description |  |
| --- | --- |
| Zoekfontein | Zuikerbosch/Forebay |
| Turbine 1 PLC Feeder | ------- |
| Turbine 2 PLC Feeder | ------- |
| Flow Meter Feeder | ------- |
| Generator 1 Control Panel | ------- |
| Generator 2 Control Panel | ------- |
| Turbine Hall Flood Alarm Panel | ------- |
| Spare Feeder 1 | ------- |
| Spare Feeder 2 | ------- |
| Spare Feeder 3 | ------- |

    - Control Room UPS Power

| Description |  |
| --- | --- |
| Zoekfontein | Zuikerbosch/Forebay |
| Socket Outlets | Socket Outlets |
| Security Alarm System | Security Alarm System |
| Common Services PLC | Common Services PLC |
| IT and Network Servers | IT and Network Servers |
| CCTV system | CCTV system |
| Access Control System | Access Control System |
| Fire Detection System | Fire Detection System |
| Intruder Detection System | Intruder Detection System |
| Spare Feeder 1 | Spare Feeder 1 |
| Spare Feeder 2 | Spare Feeder 2 |
| Spare Feeder 3 | Spare Feeder 3 |

    - 110 V DC Power

| Description |  |
| --- | --- |
| Zoekfontein | Zuikerbosch/Forebay |
| Generator 1 Excitation System | ------- |
| Generator 2 Excitation System | ------- |
| MV Switchboards | MV switchboards |

Note all LV switchboards to have 110V DC control voltage.

  - Construction Requirements

    - The width of each tier shall be at least 800mm wide such that such that the bus bar droppers, terminals and trunking can be accommodated on the rear chassis plate with space for internal wire connections and cable connections and that the wire numbers and terminal number alignment is clearly visible.

    - All front and rear doors shall be hinged and provided with a minimum of two square key locks of which one shall have a padlockable facility.

    - Rear panel doors to be properly labelled.

    - Gland plates to be adequately sized for the expected cables to be installed in that tier.

    - Gland plates on incomers shall be non-magnetic to allow for glanding of single core cables if required. The gland plate thickness to be adequate to prevent deformation and buckling due to the weight of the cables glanded.

    - The distance between the connection point of the single core cables on the load side bus bar of the incomers and the gland plate shall be adequate to meet installation and minimum cable bending requirements.

    - All terminals to be numbered on both sides of the terminal. All wires to have wire numbers.

    - All cable/field terminations on the incomers and bus section to be taken to terminals on the rear of the tiers in question for connection of control cables.

    - 110 V DC and 231 V AC UPS distribution sections shall not have door interlocked isolators. Internal distribution circuit breakers to be provided with a cover and individual circuit breaker lockout facility.

    - Sections with a large number of distribution breakers shall be provided with a custom type busbar arrangement on the source side instead of multiple wire jumpers.

    - 110 V DC wiring (both positive and negative) to be carried out with grey insulated wiring. Attention shall be paid to the Rand Water standard for the other wiring insulation colours required.

    - A mechanically interlocked dual contactor is preferred to the integral changeover unit in the generator changeover circuit. All circuit breakers and contactors shall be 4 pole.

    - Trunking in tiers to be adequately sized for the expected number of cable tails to be inserted in them, such that the trunking is not more than 70% occupied when all wiring has been installed and connected.

    - Each supply circuit breaker in the 400V distribution board shall have an auxiliary contact wired to the PLC panel for “ON” status indication purposes. All contacts in a tier shall be marshalled to a terminal strip in the tier for connection to the Common Services PLC by multicore cable. The auxiliary contacts shall switch 24VDC which shall be obtained from the PLC panel.

# 400 V DISTRIBUTION SWITCHBOARD ROOM REQUIREMENTS

  - Switchgear Room Requirements

    - The switchgear room shall be sized such that the following minimum clearances are provided to walls of the room when the final switchboard is installed:

    - Rear clearance		1100 mm and not exceeding 1500mm

    - Side and front clearances	2500 mm

  - The correct positioning of control, communications and power cable entries to the switchgear from either a cable basement or cable duct below shall be specifically determined. The switchgear placement taking into account the switchgear clearances required in clause 11.1.1 shall be complied with.

  - Purpose formed cable ducts or an entry into a cable basement shall be provided below the switchgear to meet amongst other the following requirements:

    - The depth of the cable ducts shall be such that cables below the switchgear shall be installed vertically against the cable duct wall. All cables must be installed on suitably sized cable racking, No doubling up of cables, on cable rack, permitted

    - The minimum bending radii requirement for all cables installed in the cable duct shall be met.

    - The separation requirements to any communication cables to prevent EMC interference shall be complied with.

    - Wherever possible the cable duct width shall be such that no additional supports for the switchgear straddling the duct shall be required. If additional support is required it shall be horizontal across the duct and not to the duct floor.

    - Suitable chamfering of 90° bends in the cable ducts shall be provided to cater for cable bending radii.

    - No PLC panel shall be housed in any medium or low voltage switchgear room.

# DISTRIBUTION TRANSFORMERS

  - Step up and step down transformers are required as follows:

Specific requirements for each transformer:

| Requirement | Zoekfontein Transformers | Zuikerbosch Transformers |
| --- | --- | --- |
| Application | Outdoor/Indoor | Outdoor/Indoor |
| Rating (kVA) | TBA, to enable 110% of the combined electrical capacity of two turbines to be transported | TBA, to enable 110% of the combined electrical capacity of two turbines to be transported |
| Primary Voltage (kV) | TBA as per generator output voltage | TBA |
| Secondary Voltage (V) | TBA | 11 |
| Tertiary Voltage (V) | 400 | 400 |
| Power frequency withstand voltages (kV) | As per SANS/IEC | As per SANS/IEC |
| Breakdown insulation level (kV) | As per SANS/IEC | As per SANS/IEC |
| Impedance voltage | Standard | Standard |
| Type | Sealed or Free Breathing | Sealed or Free Breathing |
| Winding Conductors | Copper or Aluminium | Copper or Aluminium |
| Insulation Grading | Uniform | Uniform |
| Insulation Class | F | F |
| Winding Type | Double Wound | Double Wound |
| Temperature Rise | Top Oil 60°C above 40°C ambient at full kVA loading | Top Oil 60°C above 40°C ambient at full kVA loading |
| Conservator | TBA | TBA |
| Vector Group | dY | Yd |
| Loss Type | Low Loss | Low Loss |
| Tappings | 0%, +/-2,5%, +/-5% | 0%, +/-2,5%, +/-5% |
| Winding in which tappings are installed | Primary | Primary |
| Tap Selector | Manual Off Load with Padlocking Facility | Manual Off Load with Padlocking Facility |
| Cooling | ONAN | ONAN |
| Dehydrating breather | TBA | TBA |
| Gas and oil actuated relay | TBA | TBA |
| Gas and oil actuated relay specification | A single-float Buchholz relay fitted with contacts for alarm and trip conditions. The relay shall be fitted with accessible test and sample valves. | A single-float Buchholz relay fitted with contacts for alarm and trip conditions The relay shall be fitted with accessible test and sample valves. |
| Indicating thermometer with trip and alarm relay | Yes | Yes |
| Thermometer pocket | Yes | Yes |
| Oil Level Sight Glass | Yes | Yes |
| Pressure Relief Vent | Yes | Yes |
| Skid underbase | Yes | Yes |
| Drain Valve | Yes | Yes |
| Earth Terminals | Yes, Two Off | Yes, Two Off |
| Cable Terminal Boxes | Weatherproof, Air Filled, Primary, Secondary and Tertiary | Weatherproof, Air Filled, Primary, Secondary and Tertiary |
| Power cables- Primary | TBA mm2, 3 core, Type A, XLPE, TBA kV | TBA mm2, 3 core, Type A, XLPE, TBA kV |
| Power cables- Secondary | TBA mm2, 3 core, Type A, XLPE, TBA kV | TBA mm2, 3 core, Type A, XLPE 6.35/11kV |
| Power cables- Tertiary | TBA mm2, 4 core, PVCPVCSAWPVC 600/1000V | TBA mm2, 4 core, PVCPVCSAWPVC 600/1000V |
| Gland Plates | Non-magnetic- Aluminium or Stainless Steel for single core cables | Non-magnetic- Aluminium or Stainless Steel for single core cables |
| Transformer Differential Protection Current Transformers | One set on primary and secondary windings suitably rated, 5P20, secondary current 1 A | One set on primary and secondary windings suitably rated 5P20, secondary current 1 A |
| Tertiary Neutral Current Transformer for Backup earth fault protection ) This CT must be installed in the separate N terminal box and must be placed around the earth cable running from the N busbar to the transformer earth stud. (Star point) | One off 300/1, 10VA, 5P20 | One off 300/1, 10VA, 5P20 |
| Tertiary Neutral Connection | In separate terminal box with Backup CT | In separate terminal box with Backup CT |
| Terminal Box for CT secondary signal | Yes, fitted with 2,5 mm2 terminals and wiring (Terminals to be numbered on both sides.) | Yes, fitted with 2,5 mm2 terminals and wiring |
| Current Transformers for Restricted Earth Fault Protection | Not Required | Not Required |
| Transformer Paint Colour | Dark Admiralty Grey G12 to SANS 1091 or Avocado Green C12 to SANS 1091. Conservator to be painted white | Dark Admiralty Grey G12 to SANS 1091 or Avocado Green C12 to SANS 1091. Conservator to be painted white |
| Overall Average Paint Thickness | 100µm | 100µm |
| Routine Tests as per SANS 780 | Yes | Yes |
| Oil Filling | Yes, Oil to SANS 555 | Yes, Oil to SANS 555 |

# TRANSFORMER BAY REQUIREMENTS

  - Bay Requirements

    - Each transformer bay shall be sized such that the minimum clearances all around the transformer shall be 1200 mm.

    - A blast wall shall be constructed between all transformers. The future transformer bay shall be the centre bay. The blast wall height shall extend a minimum of 1000 mm above the highest point of each transformer.

    - The blast wall structural integrity shall be such that it will not suffer any structural damage in the event of a catastrophic transformer failure.

    - The transformer plinths shall be from reinforced concrete and not be oversized to ensure that all main power cables can be terminated vertically onto their respective gland plates.

    - Cast cable ducts, with cable duct covers, and cable racking, shall be required for all MV, LV and control cabling.

    - The minimum bending radii shall be adhered to for power cables terminated onto the gland plates.

    - A bund area shall be provided to cater for the full transformer oil volume and to ensure that no leakage seeps outside this bunded area. A sump shall be provided at the lowest point to ensure that the oil spillage can be pumped and disposed of in a controlled way.

    - A separate system shall be provided to enable rainwater to be drained away in a controlled way e g a lockable valve arrangement.

    - Cable entries between bays and into the main building shall be by a cast in cable sealing system e g Roxtec.

    - Once all cables have been installed the bund area shall be filled with crushed stone of a designed maximum size to ensure that no cable outer PVC sheaths are damaged. If cable ducts are utilised then only the area around the transformer needs stone and not the cable ducts.

    - Correct positioning of control, communications and power cable entries between bays and into the main building shall be specifically determined to ensure that power cable failures do not damage any control cables or earth conductors.

    - The separation requirements to any communication cables to prevent EMC interference shall be complied with.

# 110 V DC BATTERY CHARGERS AND STATIONARY BATTERIES

  - Battery and Charger Design Criteria

    - General

The stationary battery system and battery charger shall be designed in accordance with the following design guides:

      - IEEE 485-2010- IEEE Recommended Practice for sizing lead-acid batteries for stationary applications

      - IEEE 946-2004 - IEEE Recommended Practice for the Design of DC Auxiliary Power Systems for Generating Systems

      - SANS 60896-11, Stationary lead-acid batteries – Part 11: Vented types - General requirements and methods of test

      - SANS 60896-21:2004- Stationary lead-acid batteries Part 21: Valve regulated types —Methods of test

      - SANS 60896-22:2004- Stationary lead-acid batteries Part 22: Valve regulated types —Requirements

      - SANS 1652:2013- Battery chargers ― Industrial type

      - RC 01475- Rand Water Standard for 110V DC auxiliary and battery charging systems

    - The stationary battery systems shall be designed for 110 V DC.

    - Battery System

      - The battery system shall be sized and designed for the following worst case load profile which is in the event of a total power failure of 8 hours.

      - At the start of the power failure the number of circuit breakers indicated shall be tripped within one minute of each other.

      - Thereafter the standing DC load shall be supplied by the battery until 8 hours have elapsed.

      - After eight hours the number of circuit breakers indicated shall be closed within one minute of each other.

      - The battery system cell voltage shall not be lower than 1,75 V/cell at the end of the eight-hour period.

      - The maximum system DC voltage shall be 125 V DC.

      - The minimum system DC voltage shall be 95 V DC.

      - The following design factors shall be used in sizing the battery:

- Temperature De-Rating	1.00.

- Design Margin		1.15.

- Ageing Factor			1.25.

      - The batteries shall have a 10/12 year design life when operated within the expected float charge voltage range and at 20ºC ambient temperature. Long life and high reliability are particular requirements.

      - Valve regulated lead acid batteries shall have a Standard Flammability rating of FV1 as per IEC 60707.

      - The closing and tripping requirements per switchboard for the specified load profile are as follows:

|  | Zoekfontein | Zuikerbosch/Forebay |
| --- | --- | --- |
| Incomers to Trip | 2 | 2 |
| Incomers to Close | 2 | 2 |
| Outgoing Feeders to Trip | 4 | 5 |
| Outgoing Feeders to Close | 4 | 5 |

Each switchboard tier shall have a separate cabelled DC supply, fed from the relevant section in the 400V distribution boards.

      - The continuous and momentary DC loads per switchboard shall be determined once the switchgear design has been finalised.

    - Battery Charger

      - The Ampere Hours removed from the battery in the load profile specified in clause 13.1.3.1 shall be used in sizing the battery charger.

      - A recharge factor of 1,15 shall be used.

      - The battery charger shall recharge the battery in 8 hours.

      - A design margin of 10% shall be used in the sizing calculations.

      - Temperature and altitude correction shall be taken into account in determining the battery charger rating.

      - The charger output current shall not exceed 25% of the final battery rated Ampere Hour capacity.

      - The continuous available current limit rating of the battery charger may be taken into account in sizing the battery charger, where the calculated rating required exceeds the next lowest standard rating, e g a with a calculated rating of 26,5 A and 25 A battery charger with a 110% continuous current limit can be used as its output will be 27,5 A.

  - The battery charger and battery shall comply with Rand Water standard specification RC   01475- STANDARD FOR 110VDC AUXILIARY AND BATTERY CHARGING SYSTEMS

  - Where there is a conflict between clauses 5.4.5 and 5.5.6 of the standard specification and the design criteria above, the design criteria shall take preference.

  - Battery Specification

  - Battery Installation System

    - A battery cabinet with slide out trays housing the batteries is preferred.

    - The slide out trays shall be corrosion resistant and the mechanism shall be constructed utilising high quality bearings on the extensible arms of the arm.

    - Allowance shall be made for movement of cable connections without snagging for withdrawal of the battery trays.

    - Sufficient distance shall be allowed for the connection of cables from the battery charger and to the DC distribution board.

    - Adequate ventilation shall be provided for heat dissipation from the batteries within the cabinet.

  - Testing Requirements

    - Battery

    - The battery shall undergo a Capacity Test as specified in Clause 14 of SANS IEC 60896-11 in the suppliers works.

    - The battery shall then be recharged by the charger supplied under this contract within the required period of eight hours.

  - Battery Charger

    - The battery charger shall undergo the following tests as specified in clause 5 of SANS 1652:

    - Dielectric strength test

    - Insulation resistance test

    - DC output voltage adjustment range test

    - DC output voltage regulation test

    - Power efficiency test

    - Short-circuit test on output terminals

    - Ripple voltage limits and ripple current limits test

    - The batteries shall be installed in an enclosed, metal battery cabinet

    - Site Testing and Commissioning

    - The combined battery charger and battery system shall be tested on site to check functionality, settings, protection functions, communication functions where applicable and correct functioning of alarms.

    - Battery and battery charger system will be supplied for each Medium Voltage switchboard

# BATTERY ROOM REQUIREMENTS

  - Battery rooms shall provide easy access for batteries and battery cabinets. In addition, battery rooms shall be dry, well lit, well ventilated and protected against the ingress of dust and foreign matter.

  - Battery rooms shall be situated as near to the associated loads as possible.

  - Battery rooms shall be situated on the coolest side of the building wherever possible.

  - Floor Construction.

    - Expansion joints shall be avoided.

    - The floor shall be given a uniform fall, end to end, of not less than 1:200, by applying a cement screed to the concrete. Across this lower end of the floor, an epoxy lined concrete channel shall be provided, sloping towards the outlet.

    - This outlet shall discharge into a PVC drainpipe that shall be built through the external wall of the battery room, and shall lead to a dedicated drainage system, designed and installed to prevent contamination of groundwater.

    - To prevent fluid discharge from the battery room, a lip of at least 25 mm shall be placed on the inside of the door entrance. Alternatively a water channel, complete with a non-corrosive grid cover, shall be installed along the wall.

    - In lead-acid battery rooms, the electrolyte shall be sulphuric acid (H2SO4). The floor shall be given a protective coating of an approved acid-resistant epoxy coating applied in accordance with the manufacturer’s specifications to prevent damage by sulphuric acid spillages.

    - An access passage at least one metre wide between cabinets or other equipment shall be provided.

  - Walls

    - Walls shall be continuous from floor to ceiling and be securely anchored. The walls of lead acid battery rooms shall be protected against electrolyte splashes, by applying an approved light coloured, acid resistant enamel paint.

  - Windows

    - Windows shall preferably not be provided in battery rooms.

  - Ceilings.

    - The ceilings shall be flat preferably and be at least 2, 5 m above floor-level.

    - Being considerably lighter than air, the hydrogen given off during battery charging will rise and accumulate under the high points of ceilings and overhead structures. All such high points shall be vented to the atmosphere.

    - Ceilings shall be given the same paint treatment as walls (see clause 15.5.1).

  - Doors

    - The battery room door shall have the applicable fire and security rating and shall be not less than 800 mm wide and 2000 mm high. The door shall have one leaf that opens outwards.

  - Cable Entry Facilities

    - Cable openings shall be through the floor.

    - The cable opening shall be adjacent to the wall and stands where applicable.

    - PVC or cement cable pipes curved to the bending radius of the cable shall be cast into the floor in such a way that the entry of the cables into the battery room is perpendicular to the floor.

    - To prevent fluids or foreign matter from entering the pipe, its upper end shall project at least 50mm above the finished floor surface without causing a tripping hazard.

  - Ventilation.

    - Battery rooms shall preferably be so positioned and designed that they are subjected to only very slight changes in temperature. A

    - The nominal temperature in the battery room shall be 25 °C and the temperature shall be kept as close to this as possible. If the temperature exceeds 35 °C, special consideration shall be given to controlling the air temperature. Air used for ventilating battery rooms shall not exceed 25 °C.

    - Hydrogen gas from battery rooms shall be extracted or ventilated to a safe area, i.e. outdoors or to an area where the gas will always dissipate into the atmosphere without possible danger of the gas accumulating in any part of that area.

    - The maximum hydrogen concentration expected in the battery rooms shall not exceed 1% of the room volume.

    - If forced ventilation is required to achieve the volumetric concentration in clause 15.10.4 the fan motors shall comply with Class I Division II ‘non-sparking’ motors to comply with SANS 10108:2017.

    - The power source for the forced ventilation shall be of the same reliability as the supply to the battery charger e g essential services.

  - Battery Room Lighting.

    - The luminaires shall be of the type Exe class 1 Div 1 (T1 – T4)

    - The power source for the forced ventilation shall be of the same reliability as the supply to the battery charger e g essential services.

    - The fittings chosen shall preferably be installed on the ceiling, and shall provide sufficient light output to illuminate the tops of the batteries to a level not less than a maintained 100 lux, in accordance with the OHS Act for battery and charging equipment rooms.

    - The luminaires shall not be mounted directly over the battery stands or cabinets.

    - The luminaires shall be positioned in parallel with the battery stands or cabinets. This precaution will facilitate maintenance on the fittings, and will also minimize the obvious dangers of working over the cells.

# TURBINE AND GENERATOR AUXILIARIES PANEL

Function:  To supply power and local controls to associated equipment.

Specific requirements:

| Description | RW Requirement |
| --- | --- |
| Panel supply voltage | 400VAC |
| Panel control voltage | 231VAC |
| Panel current rating | TBA A |
| Panel IP rating | IP65 |
| Panel material | Mild Steel |
| Panel painting system details. | Powdercoated B26, structured. As per the RW specifications. (min 70µm paint thickness) |
| Panel form classification | 3b |
| Panel short circuit rating (3 sec) kA | 10kA |
| Panel location | Pump Pit Walk ways |
| Panel access | Front |
| Panel mounting location | Floor standing against the wall in the turbine chamber walkway |
| Cable entry location | Bottom |
| Certification required | Assembly assessors certification |
| Power supply fed from | 400V Distribution board |

  - There shall be a 400V Turbine Auxiliary Panel per turbine. The panel shall supply power and controls to turbine associated equipment such as:

- Cooling water pump panels,

- Lubrication oil pumps (where required),

- Generator Space Heaters,

- Isolation Valves associated with the turbine

- PLC panel (if required)

- One Spare Circuit

  - The incomer circuit shall consist of a suitably rated ammeter and moulded case circuit-breaker, with door interlocked handle, rated to the maximum demand of the panel.

  - All circuit breakers statuses shall be monitored by a potential free auxiliary contact of the applicable circuit breaker. All contacts shall be marshalled to a common terminal strip for connection by multicore cable to the PLC panel.

  - The 400V auxiliary supply shall be installed on the walkway directly in front of the corresponding turbine set. The contractor shall ensure that all the turbine auxiliary supplies have been included in the design of the panel.

# COOLING WATER PUMP LOCAL CONTROL PANELS

  - Specific requirements:

| Description | Preferred |
| --- | --- |
| Panel supply voltage | 400VAC |
| Panel control voltage | 231VAC |
| Panel current rating | TBA A |
| Panel IP rating | IP65 |
| Panel material | 3CR12 |
| Panel painting system details. | Powdercoated B26,structured to SANS 1091 |
| Panel form classification | 1 |
| Panel short circuit rating (3 sec) kA | 10 kA |
| Panel location | At cooling water pump |
| Panel access | Front |
| Panel mounting location | Installed on a unistrut support complete with cable racking |
| Cable entry location | Bottom |
| Certification required | Assembly assessors certification |
| Power supply fed from | Pump Set Auxiliary Distribution Board |

  - The panels shall be installed as close as possible to the cooling water pumps.

  - The panel shall be equipped, as a minimum, with a suitably rated circuit breaker, isolator, contactor, overload protection, pushbuttons, trunking, terminals, pad lockable door interlock handle, selector switch, square key door catches, LEDs and labels.

  - The stop pushbutton shall be red in colour, of the lock with twist release type and shall be capable of being padlocked in the stopped position.

# VALVE AND MOTOR ISOLATING PANELS

  - Specific requirements:

| Description | Preferred |
| --- | --- |
| Panel supply voltage | 400VAC |
| Panel control voltage | As per drawing |
| Panel current rating | TBA A |
| Panel IP rating | IP65 |
| Panel material | 3CR12 |
| Panel painting system details. | Powdercoated B26 to SANS 1091 |
| Panel form classification | 1 |
| Panel short circuit rating (3 sec) kA | 10 kA |
| Panel location | Pedestal or wall mounted at valve or motor with cable racking |
| Panel access | Front |
| Cable entry location | Bottom |
| Power supply fed from | Distribution Board |

  - Every motorised device (less than 35kW) or motorised valve shall have an isolating panel which allows for the local isolation of the motor or valve actuator.

  - The panels shall be equipped, as a minimum, with a suitably rated isolator, trunking, terminals, terminal numbers, wire numbers, pad lockable door interlock isolator handle, square key door catches, labels and support brackets.

  - If a 4-20mA signal is utilized to control the valve actuator then, in addition to the above, each VIP (Valve Isolating Panel) shall include additional terminals and two suitably rated surge arrestors.

  - The main isolator shall have a potential free auxiliary contacts wired to terminals for PLC indication and interlocking purposes.

# SUMP PUMP CONTROL PANELS

  - Specific requirements:

| Description | Preferred |
| --- | --- |
| Panel supply voltage | 400VAC |
| Panel control voltage | 24VDC derived from 231 V AC main supply upstream of the main panel isolator |
| Control circuit supply | Dedicated Dual redundant 5 A 24 V DC rated power supply in panel |
| Panel current rating | TBA A |
| Panel IP rating | IP65 with double door arrangement |
| Panel material | 3CR12 |
| Panel painting system details. | Powdercoated B26,structured to SANS 1091 |
| Panel form classification | 1 |
| Panel short circuit rating (3 sec) kA | 10 kA |
| Panel location | Outdoors or Indoors |
| Main Circuit Isolator | Yes, Door handle operated, pad lockable |
| Local Remote Selector Switch | Yes |
| Pump Running Indication | Yes |
| Pump Tripped Indication | Yes |
| Thermal Overload Relay | Yes |
| Local Start/Stop Facility | Yes |
| Pump Motor control/ Isolating Panel | Yes |
| Remote signals | Yes as per schematics with the following as a minimum: Local Selected E Stop Activated Control Supply Off Overload Trip Chamber Flooded (Sump High High level) Isolator ON/OFF These signals shall be potential free for use with a separate PLC 24 V DC supply. |
| Terminals | Yes |
| Panel access | Front |
| Panel mounting location | Installed on a unistrut support complete with cable racking and as part of the rain canopy at valve chamber. See installation of distribution boards |
| Cable entry location | Bottom |
| Certification required | Assembly assessors certification |
| Power supply fed from | As per single line diagrams |

  - The panel shall be equipped, as a minimum, with suitably rated circuit breakers, isolator, trunking, terminals, 24VDC power supplies, padlockable door interlock handle, selector switch, square key door catches, LEDs and labels.

  - The panels shall be installed at an appropriate level above the sump to ensure that it is possible to operate the sump pump with the sump flooded, without the need to enter into the water.

  - The panel doors shall be constructed with hinges and square key catches one of which shall be pad lockable.

  - Three float level switches shall be provided with suitably rated changeover contacts installed at a low level to stop the pump, high level to start the pump and high-high level for a remote alarm and PLC interface.

# FLOOD ALARM PANEL, SIREN AND LEVEL SWITCHES

  - Where there is a risk of flooding especially at the turbine hall suitably rated sump pumps shall be provided as determined by the mechanical engineer.

  - Specific requirements:

| Description | Preferred |
| --- | --- |
| Panel supply voltage | 24VDC |
| Panel control voltage | 24VDC |
| Panel current rating | TBA A |
| Panel IP rating | IP65 |
| Panel material | 3CR12 |
| Panel painting system details. | Powdercoated B26,structured to SANS 1091 |
| Panel form classification | 1 |
| Panel short circuit rating (3 sec) kA | 6kA |
| Panel location | Indoors/Outdoors |
| Panel access | Front |
| Panel mounting location | Installed on a unistrut support complete with cable racking |
| Cable entry location | Bottom |
| Certification required | Assembly assessors certification |
| Power supply fed from | Control Room UPS or Common Services PLC |

  - The panel shall also be equipped, as a minimum:

    - A suitably rated circuit breaker and auxiliary relays

    - suitably rated circuit breaker and auxiliary relays

    - 24VDC power supplies

    - Trunking, terminals, pushbutton, labels

    - Hinged door with square key door catches one of which shall be pad lockable

    - Reset circuit for the audible and visual alarms

    - An audible alarm, with a range of 1000m and rated for continuous operation, together with an orange flashing light shall be installed on top of each panel

  - Level switches as per schematic diagrams for low and high level provided with suitably rated changeover contacts.

# TURBINE BUILDING AND SUBSTATIONS CABLE INSTALLATION REQUIREMENTS

  - The contractor shall be responsible for the supply, delivery, installation and commissioning of all medium voltage power cables as listed below and low voltage and control cabling, including terminations and earthing. The work shall include terminations, joints, glands etc.

  - Cables - supply and install

    - Separate items will be scheduled for each type, size and number of cores of cables supplied and/or installed.  The rates shall apply for installation of cables at all levels.  Should cables be required to be installed at levels above two metres completed working platforms (and ground level) an additional rate will be applied reflecting actual costs for scaffolding, scaffold planks, boarding, labour to erect scaffolding etc.

    - The supply of cables shall include full compensation for the procurement, delivery to site, unloading and on site storage, protection, security, handling, craneage etc.

    - Installation of cables shall include full compensation for the unloading and on site storage, protection, handling, craneage, measurement of cable runs, cutting, laying and installing the cable in accordance with the specification (including cable jacks and rollers), the supply and fixing of all clamps, specific trefoil clamps for single core cables, cable straps or cable ties etc and fixing the cable to cable racking complete with identification tagging and labelling.

    - Cable drum handling and the installation shall follow the requirements of SANS 10198 and the prescriptions of the cable manufacturer.

    - All power and control cables supplied shall comply with SABS 1507 and shall bear the SABS mark. Cables shall be 600/1 000V PVC, PVC, SWA, PVC with copper conductors and flame retardant, outer sheaths. Cables shall have the voltage rating, cable mm2 size and number of cores indicated at regular intervals on the outer PVC sheath.

    - The medium voltage cables specification shall be Cu cable to SANS 1339, Type A and Type B designed to suit application. Cables shall have the voltage rating, cable mm2 size and number of cores indicated at regular intervals on the outer PVC sheath.

    - The Contractor shall be responsible for the supply, installation, termination, jointing (where required) of the medium voltage cables and control cables.

    - Cables from the medium voltage switchgear shall preferably be run directly to the generator terminals.

  - Earth Conductors.

    - Earth conductors in the turbine building shall be copper coated steel conductors.

    - Where earth conductors are buried in the cable trenches, bare copper earth conductors shall be installed.

    - For the incoming feeders from the generators a minimum of 2 off 70 mm2 earth conductors per feeder shall be installed. For the transformer feeders a minimum of one 70 mm2 earth conductor per feeder shall be installed.

    - In areas where earth conductors would be visible preferably copper coated steel wire shall be used or black PVC insulated copper conductors as an alternative.

  - Medium Voltage Cable Terminations and Joints

    - Medium Voltage cable accessories and installations shall comply with SANS 876:2016 and NRS053. Installations shall comply with accessory suppliers’ requirements.

    - Terminations and joints shall be carried out by qualified and trained installers. Training certificates of the installer from the accessory supplier shall be submitted for acceptance by Rand Water before any installation commences.

    - Lugs for connection to indoor equipment shall be by hexagonal type lugs with an approved hydraulic crimping tool.

    - A Quality Control Plan for each termination and joint shall be submitted for acceptance. Rand Water shall be given an opportunity to indicate witness and hold points for line items on the Plan.

    - As far as possible cable slack shall be left at each termination and joint through “snaking” of the cable just before the termination or joint to enable future ends and joints on the cable to be made.

  - Testing of Cables.

    - Each installed set of medium voltage cables comprising a complete feeder shall be given an AC, VLF pressure test in accordance with SANS 1339. DC testing is not allowed. A test certificate shall be provided.

    - Once the medium voltage cables have been installed, terminated, jointed, commissioned, system voltage applied and has been in service for three months, the Contractor shall conduct non-intrusive, on-line partial discharge field measurements on each set of cables comprising a complete feeder.

    - The Contractor shall supply a comprehensive test report for the partial discharge test conducted field measurements which shall include the following, as a minimum:

      - Cable condition assessment

      - Quantity of discharge rate and sensitivity in pC or mV

    - The contractor shall repair any defects, re-do joints and terminations to obtain acceptable test values if the partial discharge results indicate that the cable installation is defective. This shall include the identification of the faulty cable, ends or joints, disconnection, excavation, and re-instatement to the original standard of installation, all at the contractors’ cost. The ACLF pressure test and online partial discharge test shall also be repeated at the cost of the contractor.

    - Payment for the cable terminations will only be finalized once the online partial discharge test reports, with acceptable values are received.

    - Each low voltage cable shall be given an insulation resistance test between cores and to earth and a continuity test for each core. Test certificates shall be provided.

    - Each earth conductor shall be given a continuity test. Test certificates shall be provided.

  - All low voltage and control cables shall be included in the cable installation. All loads required for the turbine generator set and others as specified in clause 9.2 shall be included.

  - The contractor shall be responsible for the design, supply, delivery and installation of a cable racking system for the entire substation and turbine plant.

    - The design shall include but not be limited by the following

      - Minimise crossing of cables

      - Taking into account de rating of cables for non-standard installation conditions

      - Maximise access to all cable racks

      - Separation for instrumentation and control cables

      - Mechanical strength in general and in the event of cables faults

      - Earthing of all cable racks

    - The design, supply and delivery, as well as the erection of the required rack or tray system  shall include unistrut supports, straight lengths, bends, elbows, tees, reducers, fixing brackets, fixing materials and touch up cold galvanizing painting.

    - All cables shall be installed on a cable racking system. Cables installed in cable ducts or cable sleeves or cable ducts, whether internal or external to a building, shall be installed on a cable racking system. No cable shall be installed directly into a cable duct.

    - External cables between valve chambers shall be installed in heavy duty sleeves.

    - The Contractor shall provide for cable racking for all MV cables entering and/or used in the turbine or substation building by others and shall coordinate the installation of all cables on cable racks.

    - The Contractor shall produce a detailed cable racking design detailing: racking types, layout, orientation, sizes, cable layout on the rack and routes, for approval.

    - All cable racking shall be earthed.

  - Cable Sealing System.

    - The contractor shall design, supply and install a cable sealing system at all locations where cables enter and exit the substation or turbine building below ground level. Expanded foam will not be accepted.

    - The system shall be of the Roxtec modular cast in system or equivalent. A minimum of 15% spare capacity shall be incorporated in the final installation.

    - The requirement for Automation cables shall also be considered and spare capacity shall be calculated after all cables have been allowed for.

# RETICULATION TO ZUIKERBOSCH PUMPING STATION

  - The reticulation to Zuikerbosch pumping station will be governed by servitude requirements and may be by underground cable and/or by overhead line. The contractor shall determine the optimum solution in the detail design and shall provide detail calculations and a report to support the final recommendation.

  - A 12 core multimode fibre optic cable shall be installed between Zoekfontein and Zuikerbosch/Forebay, including terminations and joints carried out in compliance to Rand Water and National standards. Also, a normal 12 core armoured screened PVC cable for interlocks and indication shall be used

  - Where an overhead line is proposed then it shall comply with all applicable SANS NRS standards

    - All cable terminations on the line shall be equipped with a fused pull stick link, surge arrestors and an earthing system to a maximum of 10 Ω resistance to earth.

    - Fuse ratings shall be matched to the load requirements.

  - Servitude conditions

    - The contractor shall comply fully with all servitude conditions.

  - Cable Trenches for underground cables

    - The contractor shall be responsible for providing all cable trenches for the medium voltage supply cable from Zoekfontein to Zuikerbosch.

    - The proposed medium voltage reticulation route is immediately to the east of the existing Zoekfontein to Zuikerbosch canal.

    - The contractor shall plan his final routes and shall carry out service detection along the proposed route to check the route selection.

    - All cable trenches shall be prepared and cables installed as follows:

      - Trenches shall be excavated to a depth of 1200 mm below Normal Ground Level.

      - Backfill with sifted material with maximum stone size 5 mm and compact a 150 mm layer to 93% MODAASHTO. River sand is not allowed.

      - After installation and testing of medium voltage cables and earth conductors backfill shall be carried out in three compacted layers of 150 mm with sifted material with maximum stone size 5 mm to 90% MODAASHTO.

      - After installation and testing of any control, low voltage power and fibre optic cables backfill shall be carried out in one compacted layer of 150 mm with sifted material with maximum stone size 5 mm to 90% MODAASHTO.

      - After installation of interlocking recycled plastic trench covers cables backfill shall be carried out in one compacted layer of 150 mm with sifted material with maximum stone size 5 mm to 90% MODAASHTO.

      - After installation of danger tape (one tape per 500 mm width of trench) backfill shall be carried out in two compacted layers of 150 mm with sifted material with maximum stone size 5 mm to 90% MODAASHTO, to final natural ground level.

    - The contractor shall prepare a quality control plan with witness and hold points at the following stages per kilometre of cable run:

      - Excavation of cable trenches and preparation of surface bed.

      - Laying of layer of medium voltage power cables and earth conductors and testing of cables and conductors.

      - Backfilling of layer above layer of medium voltage cables and compaction.

      - Laying of LV power, control and fibre cables at second layer and testing of the cables.

      - Backfilling of layer above layer of control cables and compaction.

      - Installation of interlocking recycled plastic trench covers.

      - Backfilling to danger tape layer.

      - Installation of danger tape(s).

      - Final backfilling layer.

    - Road Crossings

      - Where there is a road crossing heavy duty sleeves with a diameter of 200 mm shall be installed for medium voltage cables and 110 mm diameter for other cables and earth conductors.

      - Wherever possible the sleeves for medium voltage cables shall be installed at between 900 and 1000 mm below normal road level and other cables between 500 and 600 mm below final road level.

      - The separation between medium voltage and low voltage cables shall not be less than 400 mm.

      - There shall be provision for two spare 200 mm sleeves and three spare 110 mm sleeves, once all cables have been allowed for, in the crossing.

      - Once all the sleeves have been placed in their correct positions the entire road crossing shall be encased in 25 MPa at 28 days mass concrete. The concrete cover shall extend rectangularly over sleeves not less than 500 mm at either end and lengthwise of the sleeves (at the road edges) shall extend not less than 500 mm on either side.

      - Precautions shall be taken in the formwork and caps on sleeves that wet concrete cannot enter the sleeves. The installation of sleeves and the formwork for the casting of the mass concrete shall be a witness and hold point.

      - Any road shall be reinstated as per drawing B6477.

  - Canal Crossings

    - There are a total of 65 canal crossings with structures varying between 6 m and 70 m in width.

    - There are also two crossings where the canal is closed with vegetation with widths of 375 and 500 m.

    - The crossings shall be planned with cables running in sleeves where possible and suitably protected against vandalism and theft, including minimizing visibility.

    - The power cable and earth and the fibre optic cable shall all run in separate sleeves.

  - Service Crossings

    - All major service (Large Diameter Pipelines) crossing shall be carried out in rigid heavy duty sleeves, preferably at right angles, or as close as possible to it, to the pipeline route. The sleeves shall be such that they can be excavated and support themselves while a pipeline is installed at a lower level below.

    - The sleeves shall extend by 2000 mm past the edge of the Pipeline.

    - Where sleeves have to be joined it shall be carried out with proprietary heavy duty couplers.

    - The sleeves shall be cast in a concrete block at both ends to secure the sleeves. Measures shall be taken to prevent the ingress of wet concrete into the ends of the sleeves, during casting of the concrete.

  - Cable Trench Protective Covers

    - 1800 mm x 290 mm x 24 mm thick recycled interlocking plastic trench covers with Danger embossed on it in yellow and red shall be installed or a conveyor belt type protective blanket shall be installed in medium voltage cable trenches as specified in clause 22.5 above.

    - The plastic trench covers shall extend over the entire length and width of the cable trench; width wise by a further 500 mm on either side.

  - Cable Markers

    - Concrete cable markers shall be provided on all cable trenches.

    - The markers shall be a concrete type block with an area on top for a steel plate where the cable details and route direction can be engraved.

    - Concrete cable markers shall be installed at each change of direction and every 100 m along a straight run.

    - The markers shall be installed such that they protrude no more than 50 mm above Normal Ground Level.

    - Once the cable marker is installed at the correct position and level it shall be encased in concrete around its base to prevent it from being dislodged.

  - Single Core Trefoil Clamps

    - Where require proprietary single core cable Trefoil Clamps correctly selected for the cable size shall be supplied and installed for single core cables.

    - Trefoil clamps shall be installed not exceeding every 3 meters and at smaller intervals if required by the installation conditions.

    - Single Core Cable Induced Voltages

    - Drain resistors to discharge induced voltage in the cable sheaths of single core cables shall be designed for the single core cables installed.

# ZUIKERBOSCH SITE RETICULATION

  - A suitably rated 11kV feeder cable shall be provided from the Zuikerbosch/Forebay substation to Engine Room 4A/4B.

  - All the cable and cable installation requirements applicable in Clause 22 shall apply to this installation

  - Service detection shall be carried out along the envisaged route to determine the optimum routing.

# MIMIC DISPLAY PANELS, METERING AND POWER QUALITY

  - Mimic display panels are required to allow for the visual status indication and remote switching of all MV circuit breakers as well as the LV incomers and bus-section circuit breakers.

  - At either side of the mimic panels the tiers shall be provided for the following:

    - Zoekfontein- Time of use metering on each outgoing feeder to Zuikerbosch

    - Zoekfontein- Power quality instrumentation on the incoming switchboard from the turbine generators as listed in 24.28

    - Zuikerbosch- Time of use metering on all outgoing feeders

  - The mimic display shall include for a separate interface panel mounted beneath the mimic display for terminals linking the incoming cables to the mimic panel indication and control.

  - The mimic display shall be floor standing with front access only against the wall in the Turbine and Forebay Substation Control Rooms. The panels shall be clearly visible to operating personnel at each control room.

  - The mimic display shall be mounted in a hinged flap/door to allow for easy access to the rear of the mimic display. The hinged flap/door shall have gas struts and a sturdy mechanical mechanism to enable it to be left open during testing.

  - Sufficient wiring slack shall be allowed to enable the flap/door to be fully opened.

  - The mimic display tiles utilized shall be 24 mm x 24 mm and shall be black in colour.

  - The panel shall be sheet metal, powder coated B26, structured, to SANS 1091.

  - Control switches shall be of the Trip/Neutral/Close type with spring loaded to the default neutral position.

  - The indication LED lighting cluster for reticulation type circuits (excluding pump sets) shall be arranged in the form of a cross interrupting the line of the circuit in question with the following indication description and colour:

    - OPEN- Green

    - CLOSED- Red

    - READY- White

    - TRIPPED- Orange

  - In the case of a bus-section the TRIPPED indication is not applicable but the lighting cluster shall still be in the form of a cross.

  - The indication LED’s for the Turbine Generator sets shall be in the form of a semaphore interrupting the mimic artwork line. The horizontal indication shall be Green indicating Open status and the vertical indication shall be Red indicating the running or Closed status.

  - The main title of the respective mimic panels shall be ZOEKFONTEIN TURBINE PLANT and ZUIKERBOSCH FOREBAY HYDRO POWER SUBSTATION.

  - The interface panel shall be equipped with interposing relays and 231VAC/24VDC power supplies to ensure that the indication voltage on the mimic display is not greater than 24VDC. A dual 231V/24 VDC supply shall be provided with supplies split from two sources derived from the incoming UPS supply. Each power supply shall be capable of supply the entire load of the mimic panel.

  - The voltage for the Trip/Neutral/Close switches shall be 110 V DC derived from the Medium Voltage switchgear panels and Low Voltage Switchgear Incomers and Bus-Section.

  - A lamp test facility with a pushbutton shall be provided, rated to illuminate all indication simultaneously when the button is operated. The circuit shall operate at 24 V DC.

  - An audible alarm buzzer and visual indication operating at 24 V DC shall be built into the mimic together with a reset pushbutton. The buzzer and indication activation shall be driven by PLC outputs on the Common Services PLC and shall be wired to outgoing terminals on the mimic.

  - The siren, lamp test and audible alarm shall be clustered together and located in the right hand bottom corner of the mimic panel.

  - The preferred maximum height of the mimic panel shall be 2 000mm.

  - Medium Voltage bus bar alive indication shall be provided and shall be linear red LED’s located at the intersection of the incoming feeder line with the bus bar line. One bus bar alive indication shall be provided per bus/Incomer.

  - Bus bar alive indication is not required for the low voltage distribution board.

  - Medium Voltage lines on the mimic artwork shall be 5 mm wide and green in colour.

  - Low Voltage lines shall be 5 mm wide and orange in colour (400V).

  - Pump Set lines shall be 5 mm wide and light blue in colour including the motor.

  - Suitable descriptions for each circuit shall be engraved on the tiles in suitable positions related to the circuits. Descriptions to be approved by the Engineer.

  - The functionality required per type of circuit is as follows:

| Type | Open indication | Closed indication | Tripped indication | Ready to close | Close control | Open control |
| --- | --- | --- | --- | --- | --- | --- |
| MV Turbine Generator Incomers | - Yes | - Yes | - Yes | - No | - No | - No |
| MV Bus-Sections | - Yes | - Yes | - No | - Yes | - Yes | - Yes |
| MV Transformer Feeders | - Yes | - Yes | - Yes | - Yes | - Yes | - Yes |
| 11kV Reticulation Feeder | Yes | Yes | Yes | - Yes | - Yes | - Yes |
| 400V Incomers | - Yes | - Yes | - Yes | - Yes | - Yes | - Yes |
| 400V Bus-section | - Yes | - Yes | - No | - Yes | - Yes | - Yes |

  - Time of Use Metering

Time of Use Energy Meters shall have the following features:

    - Whole current, CT and CT/VT operated

    - Accuracy 0.5 fully compliant to EMC regulations BS EN 50081-1 and BS EN 50082-1.

    - Input

      - Voltage range: 57.5 - 240V (3 phase 4 wire) or 100 - 415V (3 phase 3 wire)

      - Maximum current (Imax): 10A

      - Standard current (In): 1 or 5A.

    - Operating condition specification

      - Frequency: 50Hz

      - Temperature Range: -20°C to +55°C

    - Comprehensive and complex tariff structure with the following:

      - 32 Time of Use registers

      - 8 Maximum demand registers

      - 12 Seasons

      - 24 Season changeover dates

      - 96 Switching times

      - 64 Exclusion dates

      - Programmable deferred tariff

      - Programmable integration period

      - Load profile storage for any measured quantity

      - 12 sets of historical stored data

    - 2 line dot matrix multilingual display with wide viewing angle

    - Measured integrated quantities

      - kWh total import/export

      - kVArh lagging import/export

      - kVArh leading import/export

      - kVAh (calculated)

    - Instantaneous instrumentation values

      - All Line Currents

      - All Line Voltages

      - Active Power (kW)

      - Reactive Power (kVA)

      - Demand (kVA)

      - Power Factor

    - Communications

      - Communications via optical port or communications module

      - Data stream mode communications

      - Allowance of up to 90 days of data to be collected in less than 30 seconds

      - Communications modules to be RS232 or RS485. A range of PSTN, or a GSM or GPRS modem plug into a module

    - Storage

      - 450 days of load profile data

    - Internal clock and calendar with battery back-up

    - 2 module slots for plug-in modules for extended functionality

    - Concealed Utility/Reset pushbutton with a high security design

    - Inputs Outputs and Registers

      - 4 relay outputs

      - 3 customer defined registers -derived from measured quantities

      - Facility for 4 inputs from external meters

    - Approvals EN 61268-1996

    - Each time of use meter shall be equipped with a GPRS modem.

  - Power Quality Instrument Specification

    - Eskom approval and acceptance for PQ measurements

    - CT input 1A or 5A

    - VT input 110 V three phase start connected

    - IEC 61000-4-30:2014 Class-A and NRS 048 PQ Parameter measurement

    - IEC 61000-4-7 Harmonic & Inter-Harmonic Measurement

    - IEC 61000-4-15 Flicker Measurement

    - Voltage and current monitoring

    - Active and reactive power monitoring

    - Frequency, positive and negative sequence system monitoring

    - Event recorder to record and store three months of data

    - Able to operate from a 110VDC control power supply

    - Measuring accuracy Class 0.2

    - Trending capabilities

    - Permanent GPS time synchronisation

    - Multi-Touch colour LED display

    - On-board GPS & real-time clock

    - Minimum two USB 2.0 peripheral ports

    - Minimum two Gigabit Ethernet ports.

# UNINTERRUPTIBLE POWER SUPPLIES (UPS) AND BATTERY SYSTEMS

  - Specific Requirements

| Description | Requirement |
| --- | --- |
| UPS input voltage | 400VAC Three Phase (Can be single phase if less than 10kVA) |
| UPS output voltage | 400VAC Three phase or Single Phase 231VAC |
| Load Ratings | 120 % of the total installed load |
| Turbine UPS Location | In 400V distribution board room or dedicated UPS room |
| Control Room UPS Location | Zoekfontein or Zuikerbosch/Forebay Control Room (also see Small Power and Lighting section) |
| Administration Office Block UPS | Administration Office Block (also see Small Power and Lighting section) |
| Type | True On-Line, Double Conversion |
| Battery type | Long Life > 5 years |
| Static Bypass | Yes for all UPS’s |
| Maintenance Bypass | Yes for all UPS’s |
| Battery capacity | 30 minutes standby at Full Load Rating of UPS’s |
| Configuration | UPS and Battery in separate compartments |
| Compliance | SANS and IEC Specifications listed elsewhere |
| Certification required | Test reports |
| Power supply fed from | Essential Services Circuits |
| Power Supply Transients | Immune or protected by surge protection against power supply spike and dips in a high lightning activity environment Compliance with maximum Rectifier input surge rating of ANSI C41.62 Cat B, which is 6kV 1.2/50us: 3 kA @ 8/20us or the IEC equivalent thereof |

  - The UPS shall have a Ethernet communications port and software to allow for connection to a PLC and SCADA system. The UPS status, alarms and metering values shall be communicated to the PLC via this communications link.

# EMERGENCY STANDBY DIESEL GENERATOR

  - The contractor shall be responsible for the design, supply, delivery, offloading, installation, testing, commissioning, putting into operation and maintenance of an emergency standby diesel generator complete with automatic changeover at Zoekfontein and Zuikerbosch/Forebay as per Rand Water’s Diesel generator specification.

  - The contractor shall design the emergency standby diesel generator to be rated as follows:

    - The final essential services load list of generator shall be verified and checked against the generator rating taking into account standing loads and switching loads from e g valve actuators

  - The generators shall be of the enclosed type to reduce noise levels.

    - At Zoekfontein black start load requirements for the turbines shall be taken into account

    - The generator shall operate at between 60 and 80% of its full load rating with design load connected. No spare capacity shall be allowed for as the remaining capacity will be considered spare.

    - If the design loading is significantly variable the requirement for any dummy loads shall be investigated and a designed for as, but this is not preferred.

  - The generator shall be designed for automatic changeover in the event of a power failure.

  - The generator shall be provided with a four pole circuit breaker and contactor changeover system.

  - The output of the generator shall be equipped with adjustable IDMT and instantaneous earth fault protection.

  - The emergency standby diesel generators shall be installed in the diesel generator rooms and shall supply power to the respective 400V distribution boards, essential services distribution section.

  - The generator unit shall have a Modbus TCP/IP communications port and software to allow for connection to a PLC and SCADA system. The generator unit status, alarms and metering values shall be communicated to the PLC via this communications link.

  - The contractor shall ensure that the power supplies to all essential equipment have been included, and that where possible starting loads such as those for valve actuators do not occur simultaneously.

  - A double skinned containment area for diesel and oil spillages shall be provided.

    - A level sensor for high levels in outer bund area shall be supplied.

    - Controlled drainage of spillage with a low level sump area suitable for a portable pump

    - Low level outlet with a drain plug to flush the bund area when required

  - Fuel management and Theft Prevention

    - Intelligent Monitoring of Fuel Intake and Consumption via Running Hours and alarming of discrepancies

  - Generator Room Requirements

    - The generator orientation shall facilitate ease of removal of the set for maintenance and re-fuelling

    - Air flow arrangement to the engine shall be taken into account.

    - Exhaust ducting shall be taken overhead and out of the room with a proper design with compensation.

    - A minimum of 1000 mm shall be provided all around the generator for ease of access.

    - If a dummy load is required this shall be placed taking into account safety and ease of heat dissipation from the room.

  - Specific requirements:

| NO | DESCRIPTION | REQUIREMENT |
| --- | --- | --- |
| 1 | GENERAL DATA |  |
|  | Continuous Rated Output Power At Sea Level (kW) |  |
|  | Continuous Rated Output Power At Sea Level (kVA) |  |
|  | Percentage De-Rating For Site Conditions, In Accordance With BS 551.4: - For Altitude - For Temperature - For Humidity - Total De-Rating |  |
|  | Continuous Rated Output Power At site (kW at 0.8 Power Factor) |  |
|  | Continuous Rated Output Power At site (kVA) | TBA kVA based on the loads to be supplied including sequential starting loads of valve actuators |
|  | Power Factor | 0.8 |
|  | Efficiency | Min. 90% @ 75% Load |
|  | AC Voltage | 380Vac/400Vac/230Vac |
|  | Frequency | 50 Hz |
|  | Number Of Phases | 3-Phase with Neutral |
|  | Connection Method | Star |
|  | Duty Type | Heavy Duty |
|  | Canopy Material (Indoor Installation) | 3CR12 and Powder Coated |
|  | Canopy Internal Material | Flameproof |
|  | Continuous Running Time @ Full Load | Min. 12 Hours |
|  | Insulating And Dielectric Materials | Fireproof, Non-Toxic And Environmental Friendly |
|  | Applicable Standards/Specification | European And South African |
|  | Type Of Technology | ATS & AMF |
|  | OTHERS |  |
| 2 | OPERATION MODE |  |
|  | Start/Shutdown Method | Auto Start (AMF&ATS) And Auto Shutdown |
|  | Operation Condition (Load Application) | Withstand Sudden Load Change And Maintain Stable Operation |
|  | Negative Phase Sequence Current | Up To 10% |
|  | Load Acceptance | As Soon As Reaching Rated Speed and Voltage |
|  | Effects Of Sudden Load Change | Insignificantly Small |
|  | Intervention Running At Less Than 60% Load |  |
|  | Overload Capability | 10% for 1 hour |
| 3 | NOISE LEVEL (DBA) SABS 0103 |  |
|  | Canopy (Indoor Installation) | Not Greater Than 65 DBA |
| 4 | ENGINE DATA (BS 5514 AND SANS 60034) |  |
|  | DC Voltage | 12Vdc/24Vdc |
|  | Exhaust System Material | 3CR12 Corrosion-Resistant Steel |
|  | Exhaust Cladding Material | Galvanized Mild Steel |
|  | Fuel Type | Diesel |
|  | Fuel Storage | Eight hours running at full connected load |
|  | Lubrication Oil Type | As per Engine Manufacturer Preference |
|  | AVR | Constant Voltage |
|  | Mounting | Heavy Duty Anti-Vibration |
|  | OTHERS | Engines to be supplied with replaceable elements for oil, fuel, air filter assemblies |
| 5 | ALTERNATOR DATA (BS 5000 Part 99 and BS 4999 Parts 20 and 32) |  |
|  | Manufacturer’s Name, Type Number (Model) and Year of Manufacturer |  |
|  | Terminal Voltage and Frequency | 380Vac/400Vac/230Vac @ 50Hz |
|  | Guaranteed Voltage Regulation From No-Load To Full-Load @ 0.8 PF | Within 1% of steady state in less than 300 ms |
|  | Transient Voltage Dip on Load Application | - 10% of rated voltage |
|  | Insulation Class | H |
|  | IP Protection | Minimum 22 |
| 6 | STARTING BATTERY (SANS 8528-4) |  |
|  | Manufacturer’s Name |  |
|  | Battery Type (Heavy Duty) | Lead-Acid Low Maintenance Type |
|  | Battery Voltage | 12Vdc/24Vdc |
|  | Battery Quantity | 1 |
|  | Battery Capacity (Ah) | 100 |
|  | Battery Starting Capacity | Six 10 Second Start Attempts |
|  | Boost Charge When The Battery Voltage Drops | Less Than 20% Of Battery Capacity |
|  | Battery Life Span | 5 years |
|  | OTHERS | Supply Battery Tray and Leads |
| 7 | CONTROL PANEL |  |
|  | Control Type/Technology | Microprocessor |
|  | Alarm, Monitoring and Fault Indication | Code and Description |
|  | Communication Protocol | Open Communication (Ethernet; Modbus; Profibus) |
|  | Ambient Temperature | 40°C |
|  | IP Protection | 55 |
|  | OTHERS |  |
| 8 | PROTECTION |  |
|  | Engine Oil Pressure | Remote Alarm & Shutdown |
|  | High Engine/Oil Temperature | Remote Alarm & Shutdown |
|  | High Water Temperature | Remote Alarm & Shutdown |
|  | Low oil pressure | Local and Remote Alarm & Shutdown |
|  | Battery Voltage | Remote Alarm |
|  | Under/Over Frequency Protection | Remote Alarm & Shutdown |
|  | Under/Over Voltage Protection | Remote Alarm & Shutdown |
|  | Overload Protection | Remote Alarm & Shutdown |
|  | Start Fault | Remote Alarm & Shutdown |
|  | Emergency Stop | Remote Alarm & Shutdown |
|  | Battery Charger Fault | Remote Alarm |
|  | Low Fuel Level (30%) | Remote Alarm |
|  | Loss Of Speed Signal | Remote Alarm & Shutdown |
|  | Under/Over Speed Protection | Remote Alarm & Shutdown |
|  | Electrical Phase Sequence | Remote Alarm & Shutdown |
|  | Earth Fault | Remote Alarm & Shutdown |
|  | Over-current | Remote Alarm & Shutdown |
|  | Auto Start Failure | Remote Alarm & Shutdown |
|  | Start Failure After 3 Attempts | Remote Alarm & Shutdown |
|  | Water Jacket Heater Failure | Remote Alarm & Shutdown |
| 9 | MONITORING |  |
|  | Generator Working Status and Alarms | Yes |
|  | Generic Sensors: - Smoke Detection - Humidity, etc. - Diesel tank level 0-100% | Yes |

# SMALL POWER AND LIGHTING INSTALLATIONS

  - The contractor shall design, supply and install a separate small power and lighting system, including emergency/escape lighting (the contractor shall as far as possible utilize approved LED type light fittings), distribution boards etc. for the entire Zoekfontein and Zuikerbosch/Forebay installations per the supplied typical building layouts, relevant standards and Rand Water specifications.

  - Drawings shall be completed in the format and with the symbols as indicated in typical drawing RA 20941, including the distribution board arrangement of circuits.

  - The design requirements are specified above in the Electrical Design section of the document.

  - Separate distribution boards shall be provided where required for Raw Power, Essential Services Power and UPS power painted as specified in this document complete and populated with all equipment. Alternatively, be one board split /compartmentalised into 3 sections.

  - The following powder coated colour finishes in accordance with SANS 1091 shall be applied on the relevant sections:

    - “Raw” power – Orange B26

    - UPS power - Royal Blue F01

    - Emergency power – Signal Red A11

  - UPS Systems

    - There will be two Uninterruptible Power Supply systems specifically for the Turbine Control Room and surrounding rooms and one for the Administration Office Block. The contractor shall allow for room in the Control Room for accommodating the UPS systems and batteries.

    - The two UPS systems will be separately supplied from the Essential Services Section of the 400 V Distribution Board.

    - The UPS systems shall be rated for 120% of the installed load. Actual load ratings shall be used and a reasonable diversity shall be applied to socket outlets to prevent the UPS system to be excessively oversized.

    - Control Room UPS loads.

  - The UPS battery systems shall be capable of supplying the full rating of the UPS for 30 minutes.

  - Lighting and emergency lighting

    - Provision shall be made for all internal and exterior lighting and emergency lighting requirements in all areas by means of LED type light fittings complying with SABS/SANAS accredited laboratory approved test authorities.

    - A detailed lux level report and Relux/Dialux (or similar) design shall be provided as part of the design deliverables for Rand Water’s acceptance and the contractor shall ensure the lux levels complies to the National and Rand Water standards.

    - All recessed lights shall consist of an extended cord and plug assembly.

    - The lighting installation over the triple volume section shall consist of LED type plug in high bay luminaires mounted above the level of the hoisting gantries. All equipment shall be positioned to enable personnel easy access for maintenance and repairs, by means of step ladders or by utilisation of the platforms on the crane gantries.

  - Socket Outlets

    - Provision shall be made for all normal, UPS and emergency power socket outlets as required, and as specified below. Offices and the control room shall be provided with all three types of outlets. IP65 rating shall be applicable to all areas where the socket outlets will be exposed to moisture and water.

    - The general purpose 16 amp single phase socket outlets shall be so placed as to cover a radius of 6 meters in any direction and the following shall be provided for each work station in any office and control room:

      - Shuttered RJ45 Cat 6 Data outlet

      - Normal Power outlet

      - Red dedicated Essential Power outlet

      - Black dedicated UPS power outlet

    - An IP65 double 16 amp single phase socket outlet shall be provided at each turbine.

  - Welding Socket Outlets

    - 32 A 5 pin (3 phases Neutral and Earth) welding plug outlet complete with output plug top shall be provided at each transformer and at each turbine. The 32amp welding plug shall be equipped with an integral isolator and a 30mA earth leakage unit.

  - Water Heater and HVAC Isolators

    - Provision shall be made for all 2, 3 or 4 pole isolators required for Hydro boil units, geysers, heat pumps, HVAC and other relevant equipment as directed by the Architect and the Mechanical Engineer.

  - General Wiring

    - The installation of the lighting, power, fire detection system, CCTV system, Data system and intrusion alarm system shall comprise of a combination of suitably sized insulated SABS approved general purpose house wire.

    - The contractor shall ensure volt drop calculations are done to confirm relevant conductor size selection.

    - No joining of any cable shall be allowed in the conduits.

    - Wiring channels, wire basket, power skirting, conduits and termination box outlet

    - The conduits for any outlets cast into reinforced slabs shall be galvanized. PVC conduits in floor slabs will not be accepted.

    - The installation of the lighting, power, fire detection system, Biometric access control, CCTV system, Data system and intrusion alarm system shall comprise of a combination of suitably sized wire channels, power skirting, wire baskets, termination boxes and galvanized conduits located at various and strategic heights and positions around the perimeter of the pump pit and in the lift out ceiling or access floor voids of the all areas where provided.

    - All conduiting shall be built in and in this regard the Contractor shall liaise with the Architect and Structural Engineer as to the optimal positioning of conduiting.

    - No surface mounted conduits shall be allowed on any brick wall.

  - Valve Chamber Lighting and Small Power Installation

    - The lighting installation in the valve chambers may comprise of a surface mounted galvanized system.

    - The contractor shall provide for a 30 mA earth leakage protected 230 Volt standard IP65 rated normal power socket outlet integral to each valve chamber distribution board.

    - Each chamber shall consist of a surface mounted IP 65 rated single lever light switch situated close to the valve chamber entrance.

    - The contractor shall provide for a surface mounted galvanized conduit system with galvanized saddles, wiring and earthing, to relevant standards complete with surface mounted IP65 rated vapour proof 1200mm in length LED type light fittings mounted in the chamber in such a manner as to allow for ease of maintenance and removal of roof if applicable.

    - The contractor shall ensure that an average lux level as per SANS specifications is achieved at all working planes.

  - Interface to HVAC Systems

    - The HVAC design and installation shall be done by the mechanical engineer and the contractor shall provide for all required power outlets and circuits up to and including the IP65 rated lockable isolator next to the external condenser units. From the isolator a return conduit link shall be provided to the internal unit.

  - Labelling

    - Provision shall be made for the installation of engraved labels on all distribution boards, light switches, socket outlets, isolators, fire sensors, fire break glass units, fire sirens and relevant equipment.

    - Detailed laminated legends sheets shall be provided in each distribution board.

    - The label on the distribution boards shall be encased in an approved label holder and the information on the label shall be in accordance with the latest SANS 10142-1 guidelines.

    - Certificates of Compliance

    - Certificates of Compliances shall be provided for all required installations.

    - Provision shall be made for the installation of engraved labels on all distribution boards, light switches, socket outlets, isolators, fire sensors, fire break glass units, fire sirens and relevant equipment.

    - Detailed laminated legends sheets shall be provided in each distribution board.

# LIGHTNING PROTECTION AND EARTHING

  - A specialist earthing contractor shall design, supply and install a lightning protection system and earth mat comprising of a trenched/rod system for the Zoekfontein Turbine Plant and the Zuikerbosch/Forebay Substation and all ancillary structures and equipment supplied under this contract.

  - The installation shall meet the requirements of SANS 10313, SANS 62305 Parts 1 to 4 and SANS 62561 Parts 1 to 7 and where applicable IEEE 80.

  - The Contractor shall ensure that all electrical items including but not limited to MV and 400V switchgear, transformers, auxiliary panels, flood alarm panels, valve isolating panels, PLC panels, cable racking, generators, motors and ancillary equipment etc, are adequately earthed. All electrical equipment shall be earthed utilizing black insulated copper wire or copper coated steel conductor. No bare copper earth wire will be accepted

  - Earthing

    - Earthing shall generally be done in accordance to SANS 10142-1, SANS 10199, SANS 10292 and SANS 1063 and where applicable IEEE 80.

    - The contractor shall utilise a recognised proprietary software package to design the earthing and lightning protection systems to SANS, IEC and where applicable IEEE standards, also based on soil resistivity data. Attention shall also be given to allowable step and touch potentials as per SANS and IEC standards. The output of design calculations and its traceability to the final designs shall be provided in the design deliverables and the final documentation.

    - All electrical equipment shall be earthed utilizing anti-theft type copper cladded steel wire. No bare copper earth wire will be accepted, except for the underground earthing system.

  - Lightning Protection

    - The installation shall be done in accordance with SANS 10313, SANS 62305 Parts 1 to 4, SANS 10199, SANS 1063 and SANS 62561 Parts 1 to 7 and.

    - A specialist service provider registered with ELPA (Earthing and Lightning Protection Association) shall design, supply and install a lightning protection system for all buildings and structures.

    - The designs shall be provided in PDF and Auto Cad formats on Rand Water drawing templates to be approved by Rand Water prior to construction.

    - The Soil Resistivity testing shall be done at every installation where a lightning protection system shall be installed and these results shall be used to base the designs on. Provide for complete reports on findings.

    - The contractor shall allow for a complete and full installation of the lightning protection including design, supply, delivery, installing in terms of the standards and strapping and supporting as necessary.

    - The specialist shall supply test certificates and documentation verifying the installation and readings obtained for the lightning protection.

# AREA LIGHTING

  - Area lighting shall be provided at the Zoekfontein Turbine Plant and at the Zuikerbosch/Forebay Substation. The contractor shall design, supply, manufacture, install and commission same as per the requirements following.

  - The lighting installations shall be designed in accordance with SANS 10114-1:2005, SANS 10389-1:2003 and The Occupational Safety and Health Act.

  - The area requiring floodlighting is as follows:

    - A minimum of up to 30 m all around the perimeter of the two buildings.

    - The lighting specification shall be as follows:

    - Minimum maintained average illuminance level (lux)(E horizontal average) 20 lux

    - Minimum uniformity ratio:	E minimum horizontal/ E horizontal average 0,25

    - Minimum uniformity ratio:	E minimum horizontal/ E maximum horizontal 0,125

    - Maximum glare rating: 55

  - A maintenance factor of 0,8 shall be applied when designing the installation.

  - The entire installations shall be controlled by a photocell/daylight switch to switch on the installation under dark conditions. A manual bypass facility shall be provided to override the photocell when required.

  - Light fittings shall be of the energy efficient, long life LED type. The fitting application shall be of the bulkhead or low bay type, with the following requirements:

    - SABS approved.

    - Corrosion resistant fitting, IP 65 rated

    - Minimum lamp design life of 50 000 hours

    - LED Wattage rating to suit the overall lighting design

    - Internal protection circuits to safeguard the fittings against fluctuating voltages

    - Powder coated, die cast aluminium, non-corrosive body

    - Non-discolouring, impact resistant diffuser attached to body with stainless steel screws

  - All area lighting masts shall be supplied from the Essential Services section of the 400 V Switchboard and provision shall be made for the required circuits in the switchboard.

  - The installation shall be so planned that maintenance can be carried out efficiently and safely on the installation.

# OPERATING AND MAINTENANCE MANUALS

  - The contractor shall produce draft operating and maintenance manuals for acceptance.  Details of all electrical equipment supplied under this contract shall appear in the manuals.

    - The following drawings and information shall be supplied by the Contractor, as a minimum, for acceptance by the Engineer within the required time period specified elsewhere in the contract documents, but before manufacture of the plant commences and after approval these drawings shall be supplied as final drawings.

    - General arrangement drawings of all applicable equipment to be supplied and installed.

    - Outline and foundation drawings for all the equipment to be supplied.

    - Full schematic diagrams of all circuits of all equipment to Rand Water RW-EES-002-Rev 0 standard, based on tender drawings.

    - Complete wiring and connection diagrams of all circuits.

    - All technical information on the equipment to be supplied.

    - Full details of configuration software for the programmable equipment and full details of calculations for the protection settings of relays. Electronic and hard copies of all software shall be provided.

    - Equipment schedules of all components coded to Rand Water WKS numbering systems.

    - Full QA plan for the testing of the equipment at the factory and on site prior to the putting into service of the plant.

    - The Contractor shall provide three copies of the operating and maintenance manuals within the required time specified elsewhere in the contract documents after the draft copy has been approved.

    - Three approved sets of all technical information/manuals including test and calibration data and detailed operating instructions necessary for the correct operation and maintenance of all equipment being supplied under the Contract. Unique manuals shall be compiled to cover this contract only and all extraneous material shall be omitted.

    - Approved test certificates and detailed test reports for all equipment shall be supplied.

    - Approved factory test, cold and hot commissioning certificates, inclusive of all test results. Specific primary and secondary injection test certificates, insulation resistance tests, major circuit breaker main contact resistance and closing and opening speed tests, are specifically included.

    - Accredited assembly assessor’s relevant certification for each low voltage electrical distribution board.

    - Certificates of Compliance to the OHS Act for all installations where required.

    - Commissioning documentation to Rand Water standards and requirements

    - Approved “as built” schematic diagrams of all circuits of all equipment in hard and electronic copy (AutoCAD dwg format) to Rand Water template standards, and approved by an ECSA registered Professional Engineer

    - Approved as built detailed cable schedules with all core connections, installed cable lengths and full cable type and size details

    - Detailed cable test certificates (insulation resistance, continuity) with all test results

    - Earthing and lightning protection installation results and certificates

    - Approved configuration and settings for all programmable equipment with hard copies approved by an ECSA registered Professional Engineer.

    - Approved "as built" drawings approved by an ECSA registered Professional Engineer.

    - Full details of all labels of all equipment

    - Layouts and sizes of equipment

    - Recommended spares and suppliers’ contact details

    - Detailed operating and maintenance instructions for all equipment and systems

    - Special tools requirements

    - Installation instructions

    - After approval of the draft manuals the contractor shall issue 3 paper sets of final approved operating and maintenance manuals and shall transfer the same to 3 sets of CDs or DVDs in .pdf format

# TOOLS AND SPARES

  - The following spares shall be supplied as follows:

    - For each Medium Voltage Switchboard

      - One Spare circuit breaker per switchboard

      - Two racking handle for the circuit breaker.

      - One trolley to lift and lower the circuit breaker if it is of the mid-mount type.

      - One complete set of maintenance tools for the breaker.

      - A full set of earthing devices or earthing trucks.

      - One wall-mounted cabinet, per switchboard, for the storage of loose equipment mentioned in this list. The door(s) shall be padlockable.

      - One ladder with castor wheels per switchboard to access equipment mounted at above 1,8 meter level

      - At least five spare HRC fuses of each rating for secondary circuits and three voltage transformer high voltage HRC fuses per two voltage transformers.

      - One cable test unit (jumpers, if required).

      - Two each of no-volt release coil; shunt trip-coil; and closing coil.

      - One spare generator and transformer protection relay and two feeder protection relays in total.

      - 400V distribution boards

      - One racking tool for the moulded case circuit breaker.

      - One trolley to lift and lower the moulded case circuit breaker.

      - Two each of no-volt release coil; shunt trip-coil; and closing coil.

      - A spare motorised mechanism and electronic trip unit per distribution board

      - Four LEDs of every colour as utilized in the distribution board

      - Two pushbuttons of every colour as utilized in the distribution board

      - Two selector switches as utilized in the distribution board

    - Each Uninterruptible Power Supply and Battery Charger

      - One set of Control Cards

    - Standby Generator

      - One Spare Controller per generator

# QUALITY ASSURANCE REQUIREMENTS

  - Quality Assurance Plan and Procedures (QAP)

    - The manufacturer shall submit to Rand Water a short form copy of quality assurance procedures manual for appraisal by the Engineer at time of tendering.

    - After award of the order the manufacturer shall submit a full quality assurance plan for approval by the Engineer. Rand Water shall be given the opportunity to indicate hold and witness points on the plan.

    - Such QAP in association with a manufacturing programme shall be submitted to Rand Water within three weeks of the order being awarded, at which time the Engineer shall indicate witness and inspection points required.

  - Inspection During Manufacture

    - The Engineer or his appointed representative shall be permitted to carry out, during normal working hours, periodic inspections of the control panel and equipment covered by this specification over and above the witness and hold points indicated on the QAP.

# ELECTRICAL BOQ FOR CONSIDERATION BY THE CONTRACT (NOT EXHAUSTIVE)

Attached to this Electrical Specification is an electrical BOQ, it is presented for additional information and for Contractor’s consideration while compiling the main BOQ which will form part of the returnable in the Bid Document.

# APPLICABLE DRAWINGS

| Item No | Drawing No | Description |
| --- | --- | --- |
|  | R0_40271 Sheets 1 and 2 | Zoekfontein to Zuikerbosch Typical Medium Voltage Single Line Diagram |
|  | RB_20092 | 400V Schematic Diagrams: Typical Motor Feeder Circuit For Motors Rated Up To 70kW |
|  | RB_20093 | 400V Schematic Diagrams: Typical Boundary Valve Chamber Distribution Board, Single Line Diagram |
|  | RB_20094 | 400V Schematic Diagrams: Typical Motor Heater And Flood Alarm Control Circuit |
|  | RB_20095 | 400V Schematic Diagrams: Typical Auxiliary Supplies Circuit |
|  | RB_20099 | 400V Schematic Diagrams: Typical Cooling Water Pump Control Circuit |
|  | RB_20100 | 400V Schematic Diagrams: Typical Sump Pump Control Circuit |
|  | RB_21023 | 400V Schematic Diagrams: Typical Motor Feeder Circuit With Motor Protection Relay |
|  | RB_21032 | 400V Schematic Diagrams: Typical UPS And Bypass Circuit |
|  | RB_21044 | 400V Schematic Diagrams: Typical Boundary Valve Distribution Board, Single Line Diagram |
|  | RB_20146 | Typical Cable Schedule, Electrical Cable Numbers and Details |
|  | RO_20611 | Typical Mimic Panel Wiring diagrams and lamp test facility |
|  | RB_21022 | Typical Floor Standing Mimic Display for an Engine Room |
|  | RO_20612 | Typical Small Mimic Display for an Engine Room |
|  | RB 6443 | Typical Cable Trench Cross Sectional Layout |
|  | B 6477 | Re-instatement details for black top road |

# APPLICABLE STANDARDS

  - RAND WATER STANDARDS

|  | Standard Number | Description |
| --- | --- | --- |
|  | RC-01422 Rev B | Area lighting installation |
|  | RC-01462 | Standard for Medium Voltage Asynchronous Motors |
|  | RC 01475 | Standard For 110VDC Auxiliary and Battery Charging Systems |
|  | RC 01519 | Standard For Mimic Control Panels |
|  | RW-EES-002-REV-1B | Electrical Engineering Standard for Electrical Drawings |
|  | RW-00320-S-001-Rev D | General Electrical Specification for the Design & Selection of Electrical Equipment |
|  | RW-00320-AS-116 Rev C | Standard for Earthing and Suppression |
|  | RW-00320-AS-488 Rev B | Engineering Standard for the Control of Plant and Equipment |
|  | RW-00320-AS-492 | Standard Electrical Specification for LV Squirrel Cage Induction Motors |
|  | RW-00320-AS-494 Rev B | General Electrical Specification for Uninterruptible Power Supplies |
|  | RW-00320-AS-495 | General Electrical Specification For Automatic Mains Failure Diesel Generators |
|  | RW-00320-AS-496 | General Electrical Specification for the Installation of Plant and Equipment |
|  | SAM EAM 00003 Spec | General Electrical Specification for Building Lighting and Small Power Installations |
|  | RW/00320-AS-978 | Medium Voltage Switchgear and Ancillary Equipment |
|  | RW-00320-S-001 Rev D | General Electrical Specification for the Design and Selection of Electrical Plant and Equipment |
|  | RW-01200-S-022 Rev 2 | Specification for Plant Codification Labels |
|  | SAM EAM 00001 Spec | Specification for Control Panels And Factory Built Assemblies of Low Voltage Switchgear and Control Gear |

  - NATIONAL AND INTERNATIONAL STANDARDS

    - GENERAL

| No | Standard No | Description |
| --- | --- | --- |
|  | SANS 1019 | Standard voltages, currents and insulation levels for electricity supply |
|  | SANS IEC 60529 | Degrees of protection provided by enclosures (IP code) |
|  | SANS 60050 | International Electro technical vocabulary. Chapter 441: Switchgear, controlgear and fuses |
|  | SABS ISO 9001, Parts I, II and III. | Quality systems |
|  | SANS 1091 | National colour standard for paint |
|  | OHS Act | Occupational Health and Safety Act (Act 85 0f 1993) |
|  | SANS 10142-1:2012 | The wiring of premises Part 1: Low-voltage installations |

    - CABLES AND CABLE INSTALLATION (LV, MV & EARTHING)

| No | Standard No | Description |
| --- | --- | --- |
|  | SANS 1507:2002 | Electric cables with extruded solid dielectric insulation for fixed installations (300/500 V to 1900/3300 V) |
|  | SANS 1507-1: 2002 | Electric cables with extruded solid dielectric insulation for fixed installations (300/500 V to 1900/3300 V) Part 1: General |
|  | SABS 1507-2: 2002 | Electric cables with extruded solid dielectric insulation for fixed installations (300/500 V to 1900/3300 V) Part 2: Wiring cables |
|  | SANS 1507-3: 2002 | Electric cables with extruded solid dielectric insulation for fixed installations (300/500 V to 1900/3300 V) Part 3: PVC distribution cables |
|  | SANS 1507-4: 2002 | Electric cables with extruded solid dielectric insulation for fixed installations (300/500 V to 1900/3300 V) Part 4: XLPE cables |
|  | SANS 1507-5: 2002 | Electric cables with extruded solid dielectric insulation for fixed installations (300/500 V to 1900/3300 V) Part 5: Halogen free distribution cables |
|  | SANS 1507-6: 2002 | Electric cables with extruded solid dielectric insulation for fixed installations (300/500 V to 1900/3300 V) Part 6: Service cables |
|  | SANS 10198-1:2004 | The selection, handling and installation of electric power cables of rating not exceeding 33 kV Part 1: Definitions and statutory requirements |
|  | SANS 10198-2:2004 | The selection, handling and installation of electric power cables of rating not exceeding 33 kV Part 2: Selection of cable type and methods of installation |
|  | SANS 10198-3:2004 | The selection, handling and installation of electric power cables of rating not exceeding 33 kV Part 3: Earthing systems - general provisions |
|  | SANS 10198-4:2005 | The selection, handling and installation of electric power cables of rating not exceeding 33 kV Part 4: Current ratings |
|  | SANS 10198-5:2004 | The selection, handling and installation of electric power cables of rating not exceeding 33 kV Part 5: Determination of thermal and electrical resistivity of soil |
|  | SANS 10198-6:2004 | The selection, handling and installation of electric power cables of rating not exceeding 33 kV Part 6: Transportation and storage |
|  | SANS 10198-7:2004 | The selection, handling and installation of electric power cables of rating not exceeding 33 kV Part 7: Safety precautions |
|  | SANS 10198-8:2004 | The selection, handling and installation of electric power cables of rating not exceeding 33 kV Part 8: Cable laying and installation |
|  | SANS 10198-9:1988 | The selection, handling and installation of electric power cables of rating not exceeding 33 kV Part 9: Jointing and termination of extruded solid dielectric-insulated cables up to 3,3 kV |
|  | SANS 10198-10:1988 | The selection, handling and installation of electric power cables of rating not exceeding 33 kV Part 10: Jointing and termination of paper-insulated cables |
|  | SANS 10198-11:1988 | The selection, handling and installation of electric power cables of rating not exceeding 33 kV Part 10: Jointing and termination of screened polymeric-insulated cables |
|  | SANS 10198-12:1988 | The selection, handling and installation of electric power cables of rating not exceeding 33 kV Part 12: Installation of earthing system |
|  | SANS 10198-13:1995 | The selection, handling and installation of electric power cables of rating not exceeding 33 kV Part 13: Testing, commissioning and fault location |
|  | NRS 028 | Cable lugs and ferrules for copper and aluminium conductors - Preferred requirements for applications in the electricity supply industry |
|  | NRS 053 | Accessories for medium-voltage power cables (3,8/6,6 kV to 19/33 kV) |
|  | VC 8075 | Safety of electric cables with extruded solid dielectric insulation for fixed installations (300/500 V to 1 900/3 300 V) |
|  | SANS 1574 | Electric cables- Flexible cords and flexible cables |

    - OVERHEAD LINES

| No | Standard No | Description |
| --- | --- | --- |
|  | NRS 033:1996 | Electricity distribution - Guidelines for the application design, planning and construction of medium voltage wooden pole overhead power lines above 1 kV an up to and including 22 kV |
|  | SABS 177-1:1990 | Insulators for overhead lines of nominal voltage exceeding 1 000 V — Part 1: Ceramic and glass string insulators units and insulator strings and sets. |
|  | SABS 0280:1998 | Code of practice for overhead power lines for conditions prevailing in South Africa |
|  | SABS 753 | Pine poles and cross arms for power distribution |
|  | SABS 754 | Eucalyptus poles and cross arms for power distribution |
|  | IEC 60305:1995 | Insulators for overhead lines with a nominal voltage above 1 000 V — Ceramic or glass insulator units for a.c. systems. Characteristics of insulator units of the cap and pin type |
|  | SANS 14788:2007 | Outdoor distribution cut-outs Part 1: Drop-out fuse-link assemblies or solid-link assemblies - Pole-mounted types - For nominal a.c. voltages up to and including 33 kV |
|  | NRS 035-2:2014 | Outdoor distribution cut-outs Part 2: Expulsion fuse-links - For nominal a.c. voltages up to and including 33 kV |

    - MEDIUM VOLTAGE SWITCHGEAR

| No | Standard No | Description |
| --- | --- | --- |
|  | SANS 62271-100:2009/IEC 62271-100:2008 | High-voltage switchgear and controlgear: Part 100: Alternating-current circuit-breakers |
|  | SANS 62271-102:2003/IEC 62271-102:2001 | High-voltage switchgear and controlgear: Part 102: Alternating current disconnectors and earthing switches |
|  | SANS 62271-103:2012/IEC 62271-103:2011 | High-voltage switchgear and controlgear Part 103: Switches for rated voltages above 1 kV up to and including 52 kV |
|  | SANS 62271-200:2012/IEC 62271-200:2011 | High-voltage switchgear and controlgear Part 200: AC metal-enclosed switchgear and controlgear for rated voltages above 1 kV and up to and including 52 kV |
|  | SANS 60044-1:2003/IEC 60044-1:2003 | Instrument transformers Part 1: Current transformers |
|  | SANS 60044-2:2003/IEC 60044-2:2003 | Instrument transformers Part 2: Inductive voltage transformers |
|  | SANS 60255- Parts 1 to 25 | Electrical Relays |

    - LOW VOLTAGE SWITCHGEAR

| No | Standard No | Description |
| --- | --- | --- |
|  | SANS IEC 60439- 1 | Low voltage switchgear and controlgear assemblies Part 1: Type-tested and partially type-tested assemblies |
|  | SANS IEC 60439- 2 | Low voltage switchgear and controlgear assemblies Part 2: Particular requirements for busbar trunking systems (busways) |
|  | SANS IEC 60439- 3 | Low voltage switchgear and controlgear assemblies Part 3: Particular requirements for low voltage switchgear and controlgear assemblies intended to be installed in places where unskilled persons have access to their use- Distribution boards |
|  | SANS IEC 60439- 4 | Low voltage switchgear and controlgear assemblies Part 4: Particular requirements for assemblies for construction sites (ACS) |
|  | SANS IEC 60439- 5 | Low voltage switchgear and controlgear assemblies Part 5: Particular requirements for assemblies intended to be installed outdoors in public places- Cable distribution cabinets (CDC’s) for power distribution in networks |
|  | BS 5486-12:1989 | Low-voltage switchgear and controlgear assemblies. Specification for particular requirements of type tested miniature circuit- breaker boards |
|  | SANS IEC 60947-1 | Low Voltage Switchgear and Control Gear Part 1: General Rules |
|  | SANS IEC 60947-2 | Low Voltage Switchgear and Control Gear Part 2: Circuit Breakers |
|  | SANS IEC 60947-3 | Low Voltage Switchgear and Control Gear Part 3: Switches, disconnectors, switch-disconnectors and fuse-combination units |
|  | SANS IEC 60947-4-1 | Low Voltage Switchgear and Control Gear Part 4: Contactors and motor-starters Section 1: Electromechanical contactors and motor-starters |
|  | SANS IEC 60947-4-2 | Low Voltage Switchgear and Control Gear Part 4: Contactors and motor-starters Section 2: A C semiconductor motor controllers and starters |
|  | SANS IEC 60947-4-3 | Low Voltage Switchgear and Control Gear Part 4: Contactors and motor-starters Section 3: A C semiconductor controllers and contactors for non-motor starters |
|  | SANS IEC 60947-5-1 | Low Voltage Switchgear and Control Gear Part 5: Control Circuit devices and switching elements- Electromechanical control circuit devices |
|  | SABS 763-1988 | Hot dip (galvanized) zinc coating |
|  | SABS 1473-1 | Low-voltage switchgear and controlgear assemblies Part 1: Type-tested and partially type-tested assemblies |
|  | SABS 1473-2 | Low-voltage switchgear and controlgear assemblies Part 2: Busbar trunking systems |
|  | SABS 1973-3 | Safety of assemblies with a rated prospective short-circuit current of up to and including 10 kA |
|  | SANS 1973-1:2007 | Low-Voltage Switchgear And Control Gear ASSEMBLIES Part 1: Type-Tested ASSEMBLIES With Stated Deviations And A Rated Short-Circuit Withstand Strength Above 10 kA Use with: SANS 60439-1:2004 |
|  | SANS 1973-3:2008 | Low-Voltage Switchgear And Control Gear ASSEMBLIES Part 3: Safety Of ASSEMBLIES With A Rated Prospective Short-Circuit Current Of Up To And Including 10 kA |
|  | SANS 1973-7:2008 | Low-Voltage Switchgear And Control Gear ASSEMBLIES Part 7: Requirements For Testing Under Conditions Of Arcing Due To Internal Fault Use with: SANS 60439-1:2004 |

    - BUSBARS

| No | Standard No | Description |
| --- | --- | --- |
|  | SANS 1195 | Busbars and Busbar Connections |

    - CIRCUIT BREAKERS & EARTH LEAKAGE PROTECTION

| No | Standard No | Description |
| --- | --- | --- |
|  | VC 8035 | Compulsory Specification for Earth Leakage Units |
|  | VC 8036 | Compulsory Specification for Circuit Breakers |
|  | SANS 156 | Moulded-case Circuit-Breakers |
|  | SANS 767-1 | Earth leakage protection units Part 1: Fixed earth leakage protection circuit-breakers |
|  | SANS 767-2 | Earth leakage protection units Part 1: Single phase, portable units |

    - SURGE ARRESTORS AND PROTECTION

| No | Standard No | Description |
| --- | --- | --- |
|  | SANS 60099-4:2009 | Surge Arresters Part 4: Metal-Oxide Surge Arresters Without Gaps For A.C. Systems |
|  | SANS 61643-1:2006 | Low-voltage surge protective devices Part 1: Surge protective devices connected to low-voltage power distribution systems - Requirements and tests |
|  | SANS 61643-11:2011 | Low-voltage surge protective devices Part 11: Surge protective devices connected to low-voltage power systems - Requirements and test methods |
|  | SANS 61643-12:2009 | Low-voltage surge protective devices Part 12: Surge protective devices connected to low-voltage power distribution systems - Selection and application principles |
|  | SANS 61643-21:2009 | Low voltage surge protective devices Part 21: Surge protective devices connected to telecommunications and signaling networks - Performance requirements and testing methods |
|  | SANS 61643-22:2005 | Low-voltage surge protective devices Part 22: Surge protective devices connected to telecommunications and signaling networks - Selection and application principles |
|  | SANS 61643-321:2004 | Components for low-voltage surge protective devices Part 321: Specification for avalanche breakdown diode (ABD) |
|  | SANS 61643-341:2004 | Components for low-voltage surge protective devices Part 341: Specification for thyristor surge suppressors (TSS) |
|  | SANS 60099-1:1999 | Surge Arresters Part 1: Non-Linear Resistor Type Gapped Surge Arresters For A.C Systems |
|  | SANS 60099-5 | Surge arresters Part 5: Selection and application recommendations |

    - EARTHING

| No | Standard No | Description |
| --- | --- | --- |
|  | SANS 0292 | Earthing of low-voltage (LV) distribution systems |
|  | SANS 0199 | The design and installation of an earth electrode |
|  | SANS 1063 | Earth rods and couplers |
|  | IEEE 80 | IEEE Guide for Safety in AC Substation Grounding |

    - LIGHTING

| No | Standard No | Description |
| --- | --- | --- |
|  | SANS 10114-1 | Interior lighting Part 1: Artificial lighting of interiors |
|  | SANS 10398-1 | Exterior lighting Part 1: Artificial lighting of exteriors |

    - LIGHTNING PROTECTION

| No | Standard No | Description |
| --- | --- | --- |
|  | NRS 042 | Guide for the protection of electronic equipment against damaging transients - For applications in the electricity supply industry |
|  | SANS 10313 | The protection of structures against lightning |
|  | SANS 62305-1 | Protection against lightning Part 1- General principles |
|  | SANS 62305-2 | Protection against lightning Part 2-Risk Management |
|  | SANS 62305-3 | Protection against lightning Part 3-Physical damage to structures and life hazard |
|  | SANS 62305-4 | Protection against lightning Part 4-Electrical and electronic systems within structures |
|  | SANS 61312-1 | Protection against lightning electromagnetic impulse Part 1: General principles |
|  | SANS 61312-2 | Protection against lightning electromagnetic impulse (LEMP) Part 2: Shielding of structures, bonding inside structures and earthing |
|  | SANS 61312-4 | Protection against lightning electromagnetic impulse Part 4: Protection of equipment in existing structures |
|  | SANS IEC 61662 | Assessment of the risk of damage due to lightning |

    - BUILDING ELECTRICAL INSTALLATIONS

| No | Standard No | Description |
| --- | --- | --- |
|  | SANS 10142-1 | The wiring of premises Part 1: Low-voltage installations |
|  | SANS 1239 | Plugs, socket outlets and couplers for industrial purposes |