ANNEXURE A : TECHNICAL SPECIFICATION

- EXTENT OF WORK

APPOINTMENT OF A SERVICE PROVIDER TO RENDER SERVICE AND MAINTENANCE OF DIESEL GENERATOR UNITS AT ATNS OR TAMBO CONTROL CENTRE, BRUMA AND AVIATION TRAINING ACADEMY (ATA) FOR A PERIOD OF FIVE (5) YEARS

  - ROLE AND OBJECTIVES

    - Diesel Generator maintenance service bid is aimed at assisting ATNS accomplish its risk management objectives by ensuring that all ATNS OR TAMBO Control Centre,  Bruma and Aviation Training Academy (ATA) diesel Generators are maintained, serviced, repaired and restored to their normal operating conditions.

    - The objective of this bid is to appoint a suitable Diesel Generator maintenance service provider that can provide assurance to ATNS Management in discharging its responsibilities regarding Diesel Generator Maintenance Service. The bidder must demonstrate the capability to perform effective Diesel Generator Maintenance Services in accordance with all legal and statutory requirements.

  - SCOPE OF WORK

    - Service providers are herewith invited to submit proposal for the maintenance services of Diesel Generator Units at ATNS OR Tambo local/remote sites, Bruma and Aviation Training Academy (ATA).

  - THE PROPOSALS SHOULD BE FOR THE FOLLOWING:

    - Maintenance Services of the ATNS OR Tambo local/remote sites, Bruma and Aviation Training Academy (ATA) Diesel Generators; (Routine Checks are to be done every three (3) months – Quarterly Base or as agreed with ATNS Management)

    - Attendance and reporting to the ATNS Management on a six monthly for any significant findings identified during the service and maintenance activities.

    - The performance of any other AD-HOC requirement requested by management on quotation basis (Provide pricing Rates over five (5) Years on table C-10). This includes callout and emergency responses.

    - AD-HOC Diesel Generator Underground tanks integrity checks (Provide pricing Rates over five (5) Years on table C-8)

    - Provide hired diesel generator sets when necessary or requested subject to approval of a quotation. Provide pricing Rates over five (5) Years on table C-9.

    - Carry out any additional work over and above the scheduled maintenance service, which ATNS may require to maintain the sites in a proper and safe working condition.

    - Supply any parts or components that may be required for maintenance purpose, during the period of this agreement.

    - If uneconomical to maintain or to repair; Supply new Diesel Generator Unit to replace the failed units on critical equipment.

    - Commissioning of the new Diesel Generator Unit and provide site acceptance test documents.

    - Recommend on required repairs after maintenance/inspections.

    - Conduct all necessary Electrical installation and provide certificate of compliance (COC) when necessary.

    - Provide a 12 Month maintenance and guarantee on all new installations

The successful service provider will be required to perform the activities below.

- The Diesel Generator Quarterly Services includes but is not limited to the following activities:

  - Check the air filters.  Change oil and filters or change filter element when performing oil and filter changes.

  - Check the lubricating oil level and top-up if required.

  - Clean the plant and its components as necessary.

  - Grease and oil moving parts, as necessary.

  - Replace the lubricating oil filter elements at recommended intervals (we recommend every 2 years or 250 hours, whichever occurs first).  The readings on the engine running hour meter shall determine the number of hours run by the plant between oil changes.

  - Check and adjust the valve settings and the fuel injection equipment, as necessary.

  - Check the batteries and top-up the electrolyte, as necessary.

  - Report to the Customer on any part that has become unserviceable for any reason and as soon as possible submit to the customer a quotation for the repair or replacement of the part.

  - Advise the Customer when a minor or major engine/alternator overhaul is due and submit a quotation for this service.

  - Check and adjust battery charger voltage/current settings.

  - Check and adjust alternator output voltage.

  - Check operation and setting of cooling water pre-heater.

  - Check operation of pre-lube pump.

  - Check operation and setting of genset protections and alarms.

  - Operate the plant off load and immediately thereafter on load for 15 minutes at the end of each visit.  The Customer must give appropriate warnings to the operators of services powered from the essential distribution board.

  - Top-up the fuel tank to the "full" mark at the end of the test run, utilising, if available, fuel supplied by the customer.

  - Ensure that the bypass switch is set to "Standby" and that the duty selector switch is set to "Auto" before leaving the standby plant room.

  - Enter in the logbook in the standby plant room the date of the visit, the tests carried out, the adjustments made and any other details that may be appropriate.

Service & Maintenance of Diesel Generator units will be performed at the following sites.

| Location | MAKE | MODEL | Rating kVA | S/N | Distance to Site (Km) | ADDRESS |
| --- | --- | --- | --- | --- | --- | --- |
| OR Tambo - ATNS Control Centre Substation 1 | Scania | DC1241 | 400 | 6504374 | 0 | O. R. Tambo International Airport Gate 14, Bonaero Drive, Bonaero Park, 1622 |
| OR Tambo - ATNS Control Centre Substation 2 | Scania | DC1241 | 400 | 650429 | 0 | O. R. Tambo International Airport Gate 14, Bonaero Drive, Bonaero Park, 1622 |
| OR Tambo - ATNS Control Centre, SSS Building 1 | Perkins | YB37527 | 100 | U781091H | 0 | O. R. Tambo International Airport Gate 14, Bonaero Drive, Bonaero Park, 1622 |
| OR Tambo - ATNS Control Centre, SSS Building 2 | Perkins | YB37527 | 100 | U781068H | 0 | O. R. Tambo International Airport Gate 14, Bonaero Drive, Bonaero Park, 1622 |
| OR Tambo - ATNS Control Centre S-Band 1 Radar Site 1 | John Deere | 60608TF003 | 125 | CD60608T397030 | 0 | O. R. Tambo International Airport Gate 14, Bonaero Drive, Bonaero Park, 1622 |
| OR Tambo - ATNS Control Centre S-Band 1 Radar Site 2 | John Deere | 6068TF003 | 125 | CD6068T397032 | 0 | O. R. Tambo International Airport Gate 14, Bonaero Drive, Bonaero Park, 1622 |
| OR Tambo - ATNS Control Centre VHF Transmitter Station 1 | Perkins | CM51027 | 22 | V168425J | 0 | O. R. Tambo International Airport Gate 14, Bonaero Drive, Bonaero Park, 1622 |
| OR Tambo - ATNS Control Centre VHF Transmitter Station 2 | Perkins | CM51027 | 22 | V160431J | 0 | O. R. Tambo International Airport Gate 14, Bonaero Drive, Bonaero Park, 1622 |
| OR Tambo - ATNS Control Centre VHF Receiver Station | Bundu Power | BPD1553 | 15 | DPK2023125683 | 0 | O. R. Tambo International Airport Gate 14, Bonaero Drive, Bonaero Park, 1622 |
| OR Tambo - ATNS Control Centre (Mobile set) | Perkins | KR31409U | 15 | O53500H | 0 | O. R. Tambo International Airport Gate 14, Bonaero Drive, Bonaero Park, 1622 |
| Isando Transmitter site | Cummins | 6CTA8.3-G | 153 | 21345950 | 13 | Zuurfontein 33-Ir Portion 147, Kempton Park |
| ATNS Head Office - Bruma | Doosan | MJB355MA4-B | 600 | MY24156 | 24 | East gate Office Park Block C South Boulevard Road Bruma |
| ATNS Aviation Training Academy | Volvo | TWD1643GE | 700 | 16010175 | 0 | O. R. Tambo International Airport Gate 14, Bonaero Drive, Bonaero Park, 1622 |
| Bapsfontein Receiver Site | Yong Feng sheng | 363CSL1607 | 120 |  | 28 | Bapsfontein Farm |
| Bapsfontein Receiver Site | Yong Feng sheng | 363CSL1607 | 120 |  | 28 | Bapsfontein Farm |
| Potgietersrus Radar Station | Cummins | 6BT59-G2 | 100 | 2/290907 | 280 | Makapan’s Valley Heritage Site; |
| Wakkerstroom Radar Site | Yong Feng sheng | GF3-88 | 88 |  | 350 | Wakkerstroom town |

Table B-1: Site Locations and Diesel Generator Ratings

  - Service & Maintenance of Diesel Generator fuel tanks and integrity checks

| ADDRESS | SET | QTY | DAY TANK | RESERVOIR |
| --- | --- | --- | --- | --- |
| OR Tambo - ATNS Control Centre Substation 1 | 1 | 1 | 500L | 9000 L (underground) |
| OR Tambo - ATNS Control Centre Substation 2 | 2 | 1 | 500 L | 9001 L (underground) |
| OR Tambo - ATNS Control Centre, SSS Building 1 | 1 | 1 | 500 L | 4500 L (underground) |
| OR Tambo - ATNS Control Centre, SSS Building 2 | 2 | 1 | 500 L | 4501 L (underground) |
| OR Tambo - ATNS Control Centre S-Band 1 Radar Site 1 | 1 | 1 | 260 L | 4500 L (Top of a structure) |
| OR Tambo - ATNS Control Centre S-Band 1 Radar Site 2 | 2 | 1 | sharing | 4500 L (Top of a structure) |
| OR Tambo - ATNS Control Centre VHF Transmitter Station 1 | 1 | 1 | 460 L | NIL |
| OR Tambo - ATNS Control Centre VHF Transmitter Station 2 | 2 | 1 | 460 L | NIL |
| OR Tambo - ATNS Control Centre VHF Receiver Station | 1 | 1 | 460 L | NIL |
| Isando Transmitter site | 1 | 1 | 300 L | 700 L (Mounted on the wall ) |
| ATNS Head Office - Bruma | 1 | 1 | 1000L | 1000L |
| ATNS ATA | 1 | 1 | 1000L | 1000L |
| Bapsfontein Receiver Site | 1 | 1 | 350L | 5500L |
| Potgietersrust Radar Station | 1 | 1 | 500 L | 2500 L (Top of a structure) |
| Wakkerstroom Radar Site | 1 | 1 | 500 L | 4500 L (Top of a structure) |

Table B-2: Diesel Generator fuel tanks