| Schedules A and B |  |  |  |  |
| --- | --- | --- | --- | --- |
|  |  | List of requirements for a typical Unit, and request for specific information |  |  |
|  |  | Please indicate compliance or else list alternatives/limitations if any | A | B |
| Item |  | Description |  |  |
|  |  | Transformer details |  |  |
|  |  | Serial No. |  |  |
|  |  | Project No. |  |  |
|  |  | Site Name |  |  |
|  |  | Rating: MVA | 80/10 |  |
|  |  | Voltage: kV HV/LV/TV | 132/88/22 |  |
|  |  | Vector group: | Yna0d1 |  |
|  |  | Tapping range: | +5 -15% |  |
|  |  | Steps: | 17 |  |
|  |  | Impedance HV/LV: Tap1 / Nominal / Tap17 | 11.8%/12%/13% |  |
|  |  | Impedance Max/Min: |  |  |
|  |  | LV Testing to IEC |  |  |
|  |  | Ratio | Yes |  |
|  |  | Impedance | Yes |  |
|  |  | Magnetisation | Yes |  |
|  |  | Vector group | Yes |  |
|  |  | Tan delta and Capacitances, windings to earth & between windings | Yes |  |
|  |  | Insulation resistance to earth and between isolated components | Yes |  |
|  |  | Winding resistance | Yes |  |
|  |  | Swept frequency response analysis (SFRA) | Yes |  |
|  |  | Bushing Tan delta and Capacitance | Yes |  |
|  |  | Current Transformer tests; Magnetization, ratio, resistance | Yes |  |
|  |  | OLTC Speed Trace | Yes |  |
|  |  | Tapchanger continuity/Open circuit | Yes |  |
|  |  | Drive mechanism operational test | Yes |  |
|  |  | Issue complete test report | yes |  |
|  |  | HV Testing to IEC |  |  |
|  |  | Lightning impulse withstand | Yes |  |
|  |  | Switching impulse withstand | Yes |  |
|  |  | Long duration AC test (with partial discharge) | Yes |  |
|  |  | Applied voltage/ Separate source | Yes |  |
|  |  | No load loss | Yes |  |
|  |  | Load loss | Yes |  |
|  |  | Bushing Partial Discharge | Yes |  |
|  |  | Issue complete test report | Yes |  |
|  |  | Windings |  |  |
|  |  | Take specifications and manufacture new HV windings | Yes |  |
|  |  | Take specifications and manufacture new LV windings | Yes |  |
|  |  | Take specifications and manufacture new TV windings | Yes |  |
|  |  | Replace all existing Insulation | Yes |  |
|  |  | Core |  |  |
|  |  | Replace all core insulation | Yes |  |
|  |  | Replace damaged core sheets | Yes |  |
|  |  | Restack and rebind core | Yes |  |
|  |  | Bushings |  |  |
|  |  | Supply new RIP Bushings according to Eskom requirements | Yes |  |
|  |  | Modify tank and leads to accommodate new Bushings | Yes |  |
|  |  | Tapchanger Repair/replacement | Yes |  |
|  |  | Control cable replacement | Yes |  |
|  |  | Marshalling kiosk replacement | Yes |  |
|  |  | Component replacement | Yes |  |
|  |  | Dry out facilities |  |  |
|  |  | Type of dryout facilities utilised | Supply details |  |
|  |  | Guarenteed dryness level | <0.5% |  |
|  |  | Method of proof | Supply details |  |
|  |  | Tanks |  |  |
|  |  | Tank repair | Yes |  |
|  |  | Coded welders | Yes |  |
|  |  | Tank modification | Yes |  |
|  |  | Shot blasting | Yes |  |
|  |  | Painting to paint procedure 240-75655504 or better | Supply details |  |
|  |  | Transport |  |  |
|  |  | Impact recorders fitted | Yes |  |
|  |  | Pressurized with dry air and gauges, together with dry air bottles | Yes |  |
|  |  | Crane capability |  |  |
|  |  | Maximum lifting capability | Supply details |  |
|  |  | Crane height capability | Supply details |  |
|  |  | Slow speed capability | Yes |  |
|  |  | Scale fitted | Yes |  |
|  |  | Workshop Details |  |  |
|  |  | Location and distance to nearest town | Supply details |  |
|  |  | Road access and load restrictions, height restrictions, mass restrictions | Supply details |  |
|  |  | Clean condition areas | Yes |  |
|  |  | Organogram | Supply details |  |
|  |  | Floor layout | Supply details |  |