{"text_format":"3","workbook":"xls","n_sheets":9,"sheets":["VVVVa","1 P&G","2 MV transformers, etc","3 MV overhead","4 Overhead support","5 LV Overhead","6 House conn","7 Dismantling","9 Summary"],"not_rendered":{"external_links":1,"defined_names":10},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"VVVVa","index":0,"n_rows":0,"n_cols":0,"rows_kept":0,"hidden":true,"flags":["formulas_cached_only"]}

{"sheet":"1 P&G","index":1,"n_rows":43,"n_cols":7,"rows_kept":43,"merged":[[2,5,2,6],[3,1,4,2],[3,5,3,6]],"flags":["formulas_cached_only"]}
[]
[null,"BILL NO 1 - PRELIMINARY AND GENERAL"]
[]
[null,"Nomlacu  Electrification BoQ Phase 2",{"$nulls":3},"PRICE (EXCL VAT)"]
[]
[null,1.1,"Provision for compliance with all the General Conditions of Contract, Special Conditions of Contract, All necessary insurances required to adequately cover the works, Workmans Compensation, Travelling, Out-of-Town Allowance, Maintenance and Guarantee ","Sum",1,0,0]
[null,1.2,"Establish facilities on site. The Contractor shall provide a fenced space with fence at least 1.8m high with a lockable gate for a temporary Site Office and Stores where all drawings and Specifications will be kept, as well as the provision of safe and secure staorage - The length of the fence shall be 300m","Sum",1,0,0]
[null,1.3,"Facilities for Contractor :"]
[null,null,"a)  Offices & storage sheds","Sum",1,0,0]
[null,null,"b)  Establishment of staff accommodation, office accommodation on site for site meetings and a Clerk of Works including office furniture and telephone / telefax as specified and facilities.","Sum",1,0,0]
[null,null,"c)  Ablution & latrine facilities","Sum",1,0,0]
[null,null,"e)  Water supplies, electric power & communications","Sum",1,0,0]
[null,1.4,"Removal of all items indicated above upon completion of construction and making good and restoring of the Site to the satisfaction of the Project Manager.","Sum",1,0,0]
[null,1.5,"Provision of \"As Built\" drawings.","Sum",1,0,0]
[null,1.6,"The Contractor shall make an order for one project signboard bearing the name of the project, the name and logo of the Client, and the Contractor.","Sum",1,0,0]
[null,1.7,"Provision for Legal and Contractual Compliance.","Sum",1,0,0]
[null,1.8,"Provision of personal protective equipment and clothing for all the contractor's staff, including sub-contractors.","Sum",1,0,0]
[null,1.9,"Provision of safety measures, e.g.. Fall arrest systems, shoring for safety purposes etc.","Sum",1,0,0]
[null,{"v":1.1,"d":"1.10"},"Compliance with OH&S Act & Construction Regulations.","Sum",1,0,0]
[null,1.11,"Compliance with the Requirements for the Expanded Public Works Programme (incl. monthly reports).","Sum",1,0,0]
[null,1.12,"The Contractor shall make allowance to receive, transport to site, offload and stack the materials supplied to the contract. The rate shall also include the implementation and maintenance of a Materials Management System for the duration of the contract.","Sum",1,0,0]
[null,1.13,"On Completion of the project, all dismantled materials (transformers, mini-subs etc.) shall be reconciled and quantified. Once authorised by the Consultant/Project Manager, this materials shall be transported to Eskom New Germany stores using the correct material return forms.","Sum",1,0,0]
[null,1.14,"Operate and Maintain Facilities on Site(Time Related Items)"]
[null,null,"Facilities for Contractor:"]
[null,null,"a)  Offices & storage sheds","Month",4,0,0]
[null,null,"b)  Ablution & latrine facilities","Month",4,0,0]
[null,null,"d)  Water supplies, electric power & communications","Month",4,0,0]
[null,1.15,"Provision of office accommodation on site for site meetings and a Clerk of Works including office furniture and telephone / telefax as specified.","Month",4,0,0]
[null,1.16,"Contract management and full time supervision of the works","Month",4,0,0]
[null,1.17,"Outage Management ","Month",2,0,0]
[null,1.18,"Community Liaison Officer conversant in Zulu and local cultural norms","Month",4,{"v":4500,"d":"R 4,500.00"},{"v":18000,"d":"R 18,000.00"}]
[null,1.19,"Provision for a trainee in electrical Engineering - Client to appoint Student ","Month",4,{"v":5500,"d":"R 5,500.00"},{"v":22000,"d":"R 22,000.00"}]
[null,{"v":1.2,"d":"1.20"},"Social Facilitation Fees (Service Provider directly accountable to Client to ISD Services)","Month",4,{"v":10000,"d":"R 10,000.00"},{"v":40000,"d":"R 40,000.00"}]
[null,1.21,"Contractor to make a provision for a project Sample line to Eskom standard as per latest revision. This is available at Eskom T & Q department in New Germany.","Sum",null,{"v":1750,"d":"R 1,750.00"},0]
[null,1.22,"Contractor shall provide security guard/s to ensure the substation site including offices, storage sheds and all material are protected from theft or any damage. The Contractor needs to ensure that the above mentioned is guarded 24hrs a day.","Month",4,{"v":4000,"d":"R 4,000.00"},{"v":16000,"d":"R 16,000.00"}]
[null,1.23,"Special Services - All special services, service provider to be appointed by Consultant"]
[null,null,"Detailed Land Suvery which include re-pegging and profiling for As-Builts that will be submitted to Eskom for Memos and Commissioning stage ","Sum",1,{"v":30000,"d":"R 30,000.00"},{"v":30000,"d":"R 30,000.00"}]
[null,"1.23.1","Allow for compliance with the WMM Municipality Environmental Specification on MV/LV Environmental studies application & DAFF tree cutting licence ","Sum",1,{"v":20000,"d":"R 20,000.00"},{"v":20000,"d":"R 20,000.00"}]
[null,"1.23.2","Provision for Pre-marketing & Detailed Marketing Service by the accredited sub-contractor appointed by client .","Sum",1,{"v":20000,"d":"R 20,000.00"},{"v":20000,"d":"R 20,000.00"}]
[null,"1.23.3","Provision for Clerk of Works Services to ensure the quality of the project and to ensure that the contractor purchases Eskom approved material from approved suppliers.","Sum",1,{"v":30000,"d":"R 30,000.00"},{"v":30000,"d":"R 30,000.00"}]
[null,1.25,"Social Facilitation Fees (Service Provider directly accountable to Client to ISD Services)","Sum",0,0,0]
[null,1.25,"Professional Fees (Professional Service Provider directly accountable to Client to Provide Consulting Services)","Sum",0,{"v":740000,"d":"R 740,000.00"},0]
[null,null,"Total - Failure to include the highlighted provisional sums to the totals, the BOQ will be deemed as incomplete and the bidder will be disqualified.",{"$nulls":3},0]

{"sheet":"2 MV transformers, etc","index":2,"n_rows":39,"n_cols":11,"rows_kept":39,"merged":[[2,6,2,10],[3,1,4,2],[3,6,3,10]],"flags":["formulas_cached_only"]}
[]
[null,"BILL NO 2 - MEDIUM VOLTAGE SWITCHGEAR, SECTIONALISERS, TRANSFORMERS, ETC"]
[]
[null,"Nomlacu  Electrification BoQ Phase 2",{"$nulls":4},"PRICE (EXCL VAT)"]
[{"$nulls":3},"DDT Ref.","Unit","Quantity","Supply Rate","Supply Total","Install   Rate","Install Total","Total Price (R)"]
[{"$nulls":10},""]
[null,null,"Transformers (Coastal Spec.) - pole mounted",{"$nulls":7},""]
[null,null,"Installation of existing or new supplied transformers on an appropriate structure and secure as required including the termination of cables and conductors, the provision of suitable lugs for 35, 50  or 70mm conductor as required & all accessories.  Excluding cable, conductors, and the transformer structure.  Include transport, offloading/loading, safe storage from appropriate stores."]
[null,"2.1","NEW Transformer 16kVA, 22kV/240V",3021,"No",1,0,0,0,0,0]
[null,"2.2","NEW Transformer 32kVA, 22kV/460V",3021,"No",2,0,0,0,0,0]
[null,"2.3","NEW Transformer 64kVA, 22kV/460V",3021,"No",1,0,0,0,0,0]
[null,"2.4","NEW Transformer 50 Kva, 22kV/415V",3021,"No"]
[null,"2.5","NEW Transformer 100kVA, 22kV/415V",3021,"No",1,0,0,0,0,0]
[null,"2.6","Existing transformers staying in same position only connecting LV",3021,"No",0,null,0]
[null,"2.7","NEW Transformer 16kVA Auxi, 22kV/230V",3021,"No",0,0,0,0,0,0]
[null,"2.8","Auto recloser",3021,"No",0,0,0,0,0,0]
[null,null,"Medium Voltage Surge Arrestors"]
[null,null,"Supply, deliver, off load on site and safely store on site the following surge arrestors, complete with galvanised steel mounting brackets for securing the surge arrestor, nuts, bolts, washers and lock washers as specified. Secure the surge arrestors and brackets to the transformer as specified including the termination of conductors. Excluding the conductors and transformer.  Discharge current 10kA."]
[null,"2.9","Arr Distr 22kV 10kA Cl 1 3100 HE24r, 31mm/kV, coastal.",3100,"No",11,0,0,0,0,0]
[]
[null,null,"Medium Voltage Sectionalisers and Links"]
[null,null,"Supply and install link isolators as detailed including the installation of crossarm brackets and the termination of conductors and including the drilling of holes in wooden poles as required.  15K fused links."]
[null,"2.10","Solid Links, Single Pole (2.5m X-arm)",1848,"No",1,0,0,0,0,0]
[null,"2.11","Fused Links, Single Pole (2.5m X-arm)",1848,"No",5,0,0,0,0,0]
[]
[null,null,"Neutral Surge Arrestor"]
[null,null,"Supply and install a LV surge arrestor including lugs and galvanised bolts"]
[null,"2.12","6kV, 10kA Surge Arrestor",3088,"No",5,0,0,0,0,0]
[null,"2.13","6kV, 10kA Auxiliary Surge Arrestor",3088,"No",{"$nulls":4},0,0]
[null,null,"Transformer & Equipment Earthing"]
[null,null,"Supply and install all materials for the complete earthing of transformer structures for ABC networks as specified. Included in the rate shall be all required spikes, insulated copper conductor, galvanised conduits, staples, bare copper, excavations, backfilling, etc. The rate shall allow for all required MV earth electrodes, consisting of four earth spikes in accordance with the Distribution specifications, Part 2.  Additional earth spikes/conductor shall be measured elsewhere if required."]
[null,"2.14","MV Earth",1860,"No",5,0,0,0,0,0]
[null,"2.15","Auto Recloser Earthing details",1831,"No",0,0,null,0,null,0]
[]
[null,null,"TOTAL : Carried forward to summary",null,null,"TOTALS",0,0,0,0,0]
[]
[]
[]
[{"$nulls":6}," "]

{"sheet":"3 MV overhead","index":3,"n_rows":63,"n_cols":11,"rows_kept":63,"merged":[[2,6,2,10],[3,1,4,2],[3,6,3,10]],"flags":["formulas_cached_only"]}
[]
[null,"BILL NO 3 - MEDIUM VOLTAGE OVERHEAD DISTRIBUTION SYSTEM"]
[{"$nulls":6},{"v":0,"d":"R 0.00"}]
[null,"Nomlacu  Electrification BoQ Phase 2",{"$nulls":4},"PRICE (EXCL VAT)"]
[{"$nulls":3},"DDT Ref","Unit","Quantity","Supply Rate","Supply Total","Install   Rate","Install Total","Total Price (R)"]
[{"$nulls":10},""]
[null,null,"Conductor",{"$nulls":7},""]
[null,null,"Supply and Take delivery off, safely store on sealed drums with ends adequately secured and transport to site conductor as specified. String conductor as specified including splices, jumper conductor ties, strain clamps, suspension clamps, tensioning, sagging, etc.",{"$nulls":7},""]
[{"$nulls":10},""]
[null,"Note ","The following dimensions will all be \"Conductor Length\" with 10% is allowed for slack & wastage.  Additional wastage/slack is for Contractor's account.",{"$nulls":7},""]
[null,"3.1"]
[null,"3.1.1","Oak - 3 Phase - Conductor length",3136,"m",0]
[null,"3.1.2","Fox _ ACSR ( Ungreased) 3 Phase",3136,"m",{"v":3500,"d":"3,500"},0,0,0,0,0]
[null,"3.1.3","Fox _ ACSR ( Ungreased) 2 Phase",3136,"m",400,0,0,0,0,0]
[null,null,"MV STRUCTURES"]
[null,"Note","Allow for the  following structures and insulator assemblies in accordance with the specifications as shown in the drawings. Include the specified crossarms, drilling of holes and treating of such holes, the provision of the U-nails and earthwire in accordance with Eskom specifications. All jumpers to links and transformers to be installed with PVC black pipe.  Supply and installation of 15m of 3/3.35x1100MPa steel wire for a BIL for each pole structure as per Eskom specification. Exclude the supply and planting of poles, stays and struts which are measured elsewhere. Insulators as per EI090SS. Include BIL insulation co-ordination for shared MV & LV structures as per 03TB-34 or later approved Eskom standard."]
[]
[null,null,"Supply and install all material as specified for the construction of the following MV structures. Including bonding of hardware and earthing. All excavations, poles, crossarms and stays are measured elsewhere.  "]
[]
[null,null,"Note: RX refers to statutory road crossings with the relevant DDT0257-10kN-31mm/kV post insulator, full wrap tie or DDT0251-40kN-31mm/kV longrod with pistolgrips."]
[]
[null,null,"MV STRUCTURES General Arrangement"]
[]
[null,3.2,"2 Phase - Delta / 2,5m Wood X-arm - Intermediate - 0° Deviation","1340B","No",2,0,0,0,0,0]
[null,3.3,"2 Phase - Delta / 2,5m Wood X-arm - Intermediate - 0° Deviation(RX)","1340B","No",0,null,0,null,0]
[null,3.4,"2 Phase - Delta / 2,5m Wood X-arm - Strain - 0° Deviation",1343,"No",1,0,0,0,0,0]
[null,3.5,"Delta / 2,5m Wood X-arm - Strain - 0° Deviation(RX)",1343,"No",0,null,0,null,0]
[null,3.6,"Delta / 2,5m Wood X-arm - Strain - Medium(1°-60°) Deviation",1344,"No",1,0,0,0,0,0]
[null,3.7,"Delta / 2,5m Wood X-arm - Strain - Medium(1°-60°) Deviation(RX)",1344,"No",0,null,0,null,0]
[null,3.8,"Delta / 2,5m Wood X-arm - Strain - Terminal",1346,"No",1,0,0,0,0,0]
[null,3.9,"Delta / 2,5m Wood X-arm - Strain - Terminal(RX)",1346,"No",0,{"v":2331.48,"d":"R 2,331.48"},0,null,0,0]
[null,"3.10.","Delta / 2,5m Wood X-arm - Intermediate - 0° Deviation","1740B","No",10,0,0,0,0,0]
[null,3.11,"Delta / 2,5m Wood X-arm - Intermediate - 0° Deviation(RX)","1740B","No",null,null,0,null,0]
[null,3.12,"Delta / 2,5m Wood X-arm - Strain - 0° Deviation",1743,"No",3,0,0,0,0,0]
[null,3.13,"Delta / 2,5m Wood X-arm - Strain - 0° Deviation(RX)",1743,"No",null,null,0,null,0]
[null,3.14,"Delta / 2,5m Wood X-arm - Strain - Medium(1°-60°) Deviation",1744,"No",7,0,0,0,0,0]
[null,3.15,"Delta / 2,5m Wood X-arm - Strain - Medium(1°-60°) Deviation(RX)",1744,"No",null,null,0,null,0]
[null,3.16,"Delta / 2,5m Wood X-arm - Strain - Medium(60°-90°) Deviation ",1745,"No",null,null,0,null,0]
[null,3.17,"Delta / 2,5m Wood X-arm - Strain - Medium(60°-90°) Deviation  (RX)","1745","No",null,null,0,null,0]
[null,3.18,"Delta /  2,5 Wood X-arm - Strain - Terminal (RX)","1746","No",7,0,0,0,0,0]
[null,3.19,"Delta / 4,5m Wood X-arm - Intermediate - 0° Deviation ","1766","No",1,0,0,0,0,0]
[null,null,"Amount carried over to next page",{"$nulls":7},0]
[{"$nulls":6},"  "]
[]
[null,"Item","Description",null,"Unit"," Quantity","Supply Rate",null,"Install   Rate",null,"Total Price (R)"]
[null,null,"Amount brought forward from previous page",{"$nulls":7},0]
[null,null,"Auxiliary Structures"]
[null,3.33,"3Ph, Take off (2.5m X-arm)",1804,"No",7,0,0,0,0,0]
[null,3.34,"3Ph, Take off  2.5m X-arm Wooden X-arm(RX)","1804","No",null,null,0,null,0]
[null,3.35,"2Ph, Take off (2.5m X-arm)",1814,"No",2,0,0,0,0,0]
[null,3.36,"2Ph, Take off (2.5m X-arm)(RX)",1814,"No",null,null,0,null,0]
[null,3.41,"2ph or 3 ph 200A link assembly-(without crossarm)",3086,"No",5,0,0,0,0,0]
[null,3.42,"Section Links-cut-out-2,5m Wood X-arm single pole",1848,"No",3,0,0,0,0,0]
[null,3.43,"Transformer - Pole mounting Single Pole (16-100kVA) - General Arrangements",1860,"No",2,0,0,0,0,0]
[null,3.44,"Transformer - Pole mounting out-of-line (16-100kVA) includes 1860 module, etc… as per EI067-MVL) and excludes transformer.",1866,"No",3,0,0,0,0,0]
[null,3.45,"Transformer - Out- of- Line 100kVA to 200KVA","1865B","No",5,0,0,0,0,0]
[null,3.46,"MV Test (per transformer installation)  Ref. SCSASABZ1",null,"No",5,null,0,0,0,0]
[null,3.47,"MV Phasing of line, ensure correct phasing.",311,"Sum",5,null,0,0,0,0]
[null,null,"Supply and install MV Full tension Joints as per the DDT Standards",{"$nulls":4},0,null,0]
[null,3.48,"Fox - Line splice",3228,"Ea",null,null,0,null,0]
[null,3.49,"Allow for MV joints between different conductor types",3073,"Ea",null,null,0,null,0]
[null,"3.50'","Insulation Co-ordination and Bonding.  The unit rate shall allow for the complete installation of a BIL lightning downwire on existing structures, including the excavation around the pole, the installation of a 3x3.5mm galvanised BIL downwire, installed down the pole in accordance with the Eskom standard, 03TB-34.",310,"Ea",13,0,0,0,0,0]
[null,null,"Amount carried over to next page",{"$nulls":3},{"v":0,"d":"R 0.00"},{"v":0,"d":"R 0.00"},{"v":0,"d":"R 0.00"},{"v":0,"d":"R 0.00"},0]

{"sheet":"4 Overhead support","index":4,"n_rows":97,"n_cols":11,"rows_kept":97,"merged":[[2,6,2,10],[3,1,4,2],[3,6,3,10],[34,6,35,6]],"flags":["formulas_cached_only"]}
[]
[null,"BILL NO 4 - SUPPORT FOR OVERHEAD RETICULATION"]
[]
[null,"Nomlacu  Electrification BoQ Phase 2",{"$nulls":4},"PRICE (EXCL VAT)"]
[{"$nulls":3},"DDT Ref","Unit","Quantity","Supply Rate","Supply Total","Install   Rate","Install Total","Total Price (R)"]
[{"$nulls":10},""]
[null,null,"Poles and Crossarms",{"$nulls":7},""]
[null,null,"Supply and safely store the following poles. Transport to site of works and install pole in excavated hole, including cutting and scafing, kicking blocks, bonding, treating, etc. Excavations and compaction are measured elsewhere."]
[null,"4.1","7m Pole, 120-139mm top diameter ","0050","No",0]
[null,"4.2","9m Pole, 160-179mm top diameter ","0055","No",110,0,0,0,0,0]
[null,"4.3","9m Pole, 180-199mm top diameter","0055","No"]
[null,"4.4","10m Pole, 160-180mm top diameter","\"0052","No"]
[null,"4.5","10m Pole, 200-219mm top diameter","0052","No",5,0,0,0,0,0]
[null,"4.6","11m Pole, 160-179mm top diameter","0051","No",10,0,0,0,0,0]
[null,"4.7","11m Pole, 180-199mm top diameter","0051","No",18,0,0,0,0,0]
[null,"4.8","11m Pole, 200-219mm top diameter","0051","No",2,0,0,0,0,0]
[null,"4.9","12m Pole, 160-179mm top diameter","0052","No",5,0,0,0,0,0]
[null,"4.10","12m Pole, 180-199mm top diameter","0052","No"]
[null,"4.11","12m Pole, 200-219mm top diameter","0052","No"]
[null,null,"13m Pole, 180-199mm top diameter","0052","No"]
[null,null,"Supply and install the following wooden cross arms."]
[null,"4.12","2.5m, 140-159mm Diameter","0061","No",55,0,0,0,0,0]
[null,null,"3.5m, 140-159mm Diameter","0061","No",2,0,0,0,0,0]
[null,"4.13","Steel platform for 50kVA and 100kVA","0061","No",2,0,0,0,0,0]
[null,"4.14","4.5m, 140-159mm Diameter","0061","No",7,0,0,0,0,0]
[null,"4.15","6m,160-179mm Diameter","0061","No"]
[null,null,"Stays, Flying Stays and Anti-Climbing Devices"]
[null,"Note","The unit price for a standard stay and an aerial stay shall exclude the wooden poles, but include the stay wire, stay rods, insulators, stay plate, stay guards, bitumastic paint, guy grip dead end, earthing of stay, line splice, precast concrete slabs, pole clamp, nuts bolts and washers etc. "]
[null,null,"The following stays shall be in accordance with the specification and shall include a stay plate"]
[null,"4.16","MV Stay (DDT0341 rev 9, BIL 40kV & 150kV)","0341","No",30,0,0,0,0,0]
[null,"4.17","LV Stay","0341","No",100,0,0,0,0,0]
[null,null,"The following flying stays shall be in accordance with the specifications and shall include poles & excavation."]
[null,"4.18","MV Flying Stay","0343","No"]
[null,"4.19","LV Flying Stay",1168,"No"]
[]
[null,null,"The following struts shall be in accordance with the specifications and shall include poles & excavation."]
[null,"4.20","MV Strut","0342","No",5,0,0,0,0,0]
[null,"4.21","LV Strut",1167,"No",20,0,0,0,0,0]
[]
[null,null,"Amount carried over to next page",{"$nulls":6},0,0]
[]
[]
[null,"Item","Description","DDT Ref","Unit","Tender Quantity","Supply Rate",null,"Install   Rate",null,"Total Price (R)"]
[null,null,"Amount brought forward from previous page",{"$nulls":6},0,0]
[{"$nulls":10},""]
[null,null,"Excavations and Compaction",{"$nulls":7},""]
[{"$nulls":10},""]
[null,"Note","The excavations for service connections are measured elsewhere",{"$nulls":7},""]
[{"$nulls":10},""]
[null,null,"Determination of pole positions, excavate, and supply a mechanical boring device if required. The rate shall include backfilling, compaction to 93% MOD AASHTO density, and where necessary the supply and transportation of suitable ground as may be required to receive the desired compaction, except where cement is specified.  Any damage to existing services shall be made good by the Contractor at his own expense and to the approval or the PM(C).",{"$nulls":7},""]
[{"$nulls":10},""]
[null,null,"Before excavation work begins the Contractor shall evaluate the stability of the ground before excavation begins.  Contractor shall use warning signs, positioned next to an excavation within which persons are working or carrying out inspections.  Ref CR (11)"]
[]
[null,"4.22","Hole for 7m pole - 1.3m deep","0332","No",0]
[null,"4.23","Hole for 9m pole - 1.5m deep","0332","No",110,null,null,0,0,0]
[null,"4.24","Hole for 11m pole - 1.8m deep","0332","No",35,null,null,0,0,0]
[null,"4.25","Hole for 12m pole - 2.0m deep","0332","No"]
[null,null,"Hole for 13m pole - 2.3m deep","0332","No",0]
[null,"4.26","Hole for MV stay - 1.5m deep","0350","No",30,null,null,0,0,0]
[null,"4.27","Hole for LV stay - 1.4m deep","0350","No",100,null,null,0,0,0]
[null,"4.28","Hole for MV strut - 1.8m deep","0342","No",5,null,null,0,0,0]
[null,"4.29","Hole for LV strut - 1.3m deep","0342","No",20,null,null,0,0,0]
[null,"4.30","Provision for Rock drilling of  holes (Irrespective of depth of hole, each hole to be verified by ODG Technologies Clerk of works, Client representative  and Project manager as per internal or external invoice) - This rate includes importing soil and transport - Specialist service provider to be appointed by Consultant",null,"No",50,null,0,{"v":1950,"d":"R 1,950.00"},{"v":97500,"d":"R 97,500.00"},{"v":97500,"d":"R 97,500.00"}]
[null,"4.30.1","Provision for Blasting of holes (Irrespective of depth of hole, each hole to be verified by ODG Technologies Clerk of works, Client representative  and Project manager as per internal or external invoice) - This rate includes importing soil and transport - Specialist service provider to be appointed by Consultant",null,"Each",null,null,0,{"v":2300,"d":"R 2,300.00"},0,0]
[]
[null,null,"Bush Clearing"]
[]
[null,"4.31","Provision for bush clearing by the acredited sub-contractor. Specialist service provider to be appointed by Consultant",null,"m",100,null,0,{"v":850,"d":"R 850.00"},{"v":85000,"d":"R 85,000.00"},{"v":85000,"d":"R 85,000.00"}]
[]
[null,null,"Pole Labels"]
[null,null,"Supply and install labels on all poles in accordance with the specifications including the provision of all fixing materials.  Allow for pick-up, loading/offloading, transport from appropriate Eskom store.   Labels to the Eskom Standard SCSSCAAP5, TQGHSP05 and TQCSS005.  Dynatape, masking tape or Hand written with permanent marker type labels are not to be considered for operational labelling under any circumstances."]
[null,"4.32","Equipment labels ",null,"No",12,0,0,0,0,0]
[null,"4.33","Mosdorfer fuse rating labels (transformers)",null,"No",5,0,0,0,0,0]
[null,"4.34","Fuse - \"Warning. Open all fuses before working on line\"",null,"No",5,0,0,0,0,0]
[null,"4.35","Transformer Max fuse notification label",null,"No",5,0,0,0,0,0]
[null,"4.36","Feeder Max Fuse notification label",null,"No",5,0,0,0,0,0]
[null,"4.37","Danger Labels (transformers, links, anti-climbings)",3202,"No",37,0,0,0,0,0]
[null,"4.38","LV Feeder Labels",null,"No",13,0,0,0,0,0]
[null,"4.39","Pole Top Box Phase Labels",null,"No",97,0,0,0,0,0]
[null,null,"TOTAL : Carried forward to summary",null,null,"TOTALS",{"$nulls":3},{"v":182500,"d":"R 182,500.00"},0]
[]
[]
[null,"Item","Description",null,"Unit","Tender Quantity","Supply Rate",null,"Install   Rate",null,"Total Price (R)"]
[null,null,"Amount brought forward from previous page",{"$nulls":6},{"v":182500,"d":"R 182,500.00"},0]
[]
[]
[null,null,"General Items"]
[]
[]
[null,null,"Supply and install labels Spiral Vibration Dampers as per the DT Standards",{"$nulls":7},""]
[null,"4.40","Spiral Vibration Dampers (Pine)",3175,"Each",0]
[null,"4.41","Spiral Vibration Dampers (35)",3175,"Each",0]
[null,"4.42","Supply and Install Anti-Climbing Devices as per the latest DDT Standards."]
[null,"4.43","Anti-Climbing Device as per 05TI09.  Including the removal of existing spikes.  Galvanised wire per DDT3170.  Galvanises staples per DDT3129. Install on trfr strs, struts, parallel MV stay wires, recloser str, OOL trfr strs, etc, structures where meter boxes or equipment is installed <2m above ground, any str having cable secured by means of strapping <0.5m apart, any climbable pole str, apparatus etc as per DDT standard.","0399","per str",37,0,0,0,0,0]
[null,"4.44","Supply and Install, where MV & LV Earths are on the same structure, UV protected black PVC pipe of length 1.2m on each earth downwire, cutting the top and bottom of the pipe at 45deg, split the pipe so as to insert the MV/LV earth and installing clout nails at the bottom and top. ",null,"per str",5,0,0,0,0,0]
[]
[null,null,"Total - Failure to include the highlighted provisional sums to the totals, the BOQ will be deemed as incomplete and the bidder will be disqualified.",null,null,"TOTALS",0,0,0,{"v":182500,"d":"R 182,500.00"},0]

{"sheet":"5 LV Overhead","index":5,"n_rows":99,"n_cols":11,"rows_kept":99,"merged":[[2,6,2,10],[3,1,4,2],[3,6,3,10]],"flags":["formulas_cached_only"]}
[44]
[null,"BILL NO 5 - LV OVERHEAD DISTRIBUTION LINES"]
[{"$nulls":6},{"v":0,"d":"R 0.00"}]
[null,"Nomlacu  Electrification BoQ Phase 2",{"$nulls":4},"PRICE (EXCL VAT)"]
[{"$nulls":3},"DDT Ref","Unit","Quantity","Supply Rate","Supply Total","Install   Rate","Install Total","Total Price (R)"]
[{"$nulls":10},""]
[null,null,"LV ABC (insulated neutral)",{"$nulls":7},""]
[{"$nulls":10},""]
[null,"Note","The LV insulated aerial bundle conductor system shall be in accordance with SABS 1418 and insulated in accordance with SABS 0198 and the Distribution Standard Part 3.  Ref. EI-092-LVL"]
[{"$nulls":10},""]
[null,"Note","The unit rate per meter shall include the tensioning and stringing of the bundle in accordance with the sag and stress tables provided by the manufacturer with all plant, equipment and accessories required to erect an LV overhead bundled distribution line i.e. Drum trailer, winch, wind-off pulleys, pulling rope/cable with connection, dynamometer, slide-lock, sheathed synthetic-fibre belt, woven snatch belt, snatch block, tackle, shackle, etc.",{"$nulls":7},""]
[{"$nulls":10},""]
[null,"Note","Measured lengths for stringing shall be net line route lengths and unit rates shall include for sag, off-cuts, etc.",{"$nulls":7},""]
[{"$nulls":10},""]
[null,null,"Supply, safely store and transport to site and string. The conductor will be delivered on sealed drums and adequate allowance shall be made for the correct handling thereof.  ",{"$nulls":7},""]
[{"$nulls":10},""]
[null,null,"Ensure correct tooling - D 51 Hydraulic Crimping Tool and dies, a 13mm tube spanner with T – bar, Phase separators, Slings, Wide Grooved Pulleys, Steel Pulling Socks, Pulling Swivels, Rickie, Come-along and Dynamometers."]
[]
[null,5.1,"Single phase ABC (35mm2,  2 core) - insulated neutral",3141,"m",1500,0,0,0,0,0]
[null,5.2,"Dual phase ABC (35mm2, 3 core) - insulated neutral",3141,"m",2200,0,0,0,0,0]
[null,5.3,"Dual phase ABC (70mm2, 3 core) - insulated neutral",3141,"m",2500,0,0,0,0,0]
[null,5.4,"Three phase ABC (35mm2, 4 core) - insulated neutral",3141,"m",1000,0,0,0,0,0]
[null,5.5,"Three phase ABC (70mm2,  4 core) - insulated neutral",3141,"m",800,0,0,0,0,0]
[]
[null,null,"LV STRUCTURES"]
[]
[null,null,"Allow for the assembly of the following LV strain and suspension assemblies in accordance with the specifications shown in the drawings. Including all earthing, drilling of holes and treating of drilled holes. All LV ABC hardware, line connectors, PVC cable ties, nuts, bolts, washers, lock washers shall be allowed for in the appropriate item below. Excluding the supply and planting of poles, stays and struts, which are measured elsewhere.  Use strain assembly when crossing roads."]
[]
[null,null,"Supply and install all the materials as specified for the following:"]
[null,5.6,"Single Phase ABC Intermediate Assembly",1153,"No",10,0,0,0,0,0]
[null,5.7,"Single Phase ABC Terminal Assembly",1154,"No",20,0,0,0,0,0]
[null,5.8,"Single Phase ABC Strain Assembly (0-60 deg)",1155,"No",10,0,null,0,0,0]
[null,5.9,"Single Phase ABC Strain Assembly (60-90 deg)",1156,"No",10,0,0,0,0,0]
[null,"5.10.","Single Phase ABC Intermediate Suspension Assembly ",1158,"No",{"$nulls":4},0]
[null,5.11,"Single Phase ABC Tee from Intermediate",1157,"No",3,0,0,0,0,0]
[null,5.12,"Single Phase ABC Tee from Strain",1159,"No",18,0,0,0,0,0]
[null,5.13,"ABC X Intermediate - Strain Assembly",1160,"No",0,{"$nulls":3},0]
[null,null,"Amount carried over to next page",{"$nulls":4},0,null,0,0]
[]
[]
[null,"Item","Description","DDT Ref","Unit","Tender Quantity"]
[null,null,"Amount brought forward from previous page",{"$nulls":4},0,null,0,0]
[null,5.13,"Dual Phase ABC Intermediate Assembly",1145,"No",18,0,0,0,0,0]
[null,5.14,"Dual Phase ABC Terminal Assembly",1146,"No",15,0,0,0,0,0]
[null,5.15,"Dual Phase ABC Strain Assembly (0-60 deg)",1147,"No",13,0,0,0,0,0]
[null,5.16,"Dual Phase ABC Strain Assembly (60-90 deg)",1148,"No",10,0,0,0,0,0]
[null,5.17,"Dual Phase ABC Tee from Intermediate",1149,"No",4,0,0,0,0,0]
[null,5.18,"Dual Phase ABC intermediate Suspension ",1150,"No",0,null,0,null,0]
[null,5.19,"Dual Phase ABC Tee from Strain",1151,"No",5,0,0,0,0,0]
[null,"5.20","Dual Phase ABC intermediate Strain Assembly",1152,"No",0,null,0]
[null,"5,21","Three Phase ABC Intermediate Assembly",1100,"No",15,0,0,0,0,0]
[null,"5,22","Three Phase ABC Terminal Assembly",1120,"No",18,0,0,0,0,0]
[null,"5,23","Three Phase ABC Strain Assembly (0-60 deg)",1121,"No",6,0,0,0,0,0]
[null,"5,24","Three Phase ABC Strain Assembly (60-90 deg)",1122,"No",4,0,0,0,0,0]
[null,"5,25","Three Phase ABC Tee from Intermediate",1140,"No",6,0,0,0,0,0]
[null,"5,26","Three Phase ABC intermediate Suspension ",1141,"No",null,null,0]
[null,"5,27","Three Phase ABC  Tee from Strain",1142,"No",10,0,0,0,0,0]
[null,"5,28","Three Phase ABC X intermediate Strain",1143,"No",0]
[]
[null,null,"LV Fuse Switch Units"]
[]
[null,null,"Supply, deliver to site, off load on site and safely store. The fused switch shall be supplied complete with the pole mounting bracket, nuts, bolts, washers, etc. for securing the unit to the wooden pole. The fuses shall be supplied with the fuse switch unit. Fuse ratings shall be as shown on the drawings. Install the on load fused disconnecting switch on the transformer structure including the drilling of holes as required, including the termination of the LV ABC to the unit.  Fuse ratings below allow for 120% overload."]
[null,null,"One fuse unit is for the transformer and one unit per LV feeder for isolation/protection."]
[null,5.29,"80A Single Phase Load disconnecting switch MORSDORPHER ",309,"No",7,0,0,0,0,0]
[null,"5.30.","125A Dual Phase Load disconnecting switch MORSDORPHER ",309,"No",8,0,0,0,0,0]
[{"$nulls":10},0]
[null,null,"Amount carried over to next page",{"$nulls":4},0,null,0,0]
[]
[]
[null,"Item","Description","DDT Ref","Unit","Tender Quantity",{"$nulls":4},"Total Price (R)"]
[null,null,"Amount brought forward from previous page",{"$nulls":4},0,null,0,0]
[]
[null,null,"Earthing of LV Network"]
[null,"Note","All MV transformer earthing is measured elsewhere and all LV earths per structure are measured with the structure. This section is intended for LV earths at transformers."]
[]
[null,null,"Allowance shall be made for the testing (including earth loop impedance) of the earth resistance for the entire reticulation system in accordance with the TN-C-S earthing system as defined in the Distribution Standard Part 2 and any earth tests which may be required in terms of the standard and detailed specifications.  Use 2 x H-Crimps - neutral connection point.",637]
[null,5.31,"LV Earth (Crowsfoot)",627,"No",5,0,0,0,0,0]
[null,5.32,"LV Earth (single point)",642,"No",5,0,0,0,0,0]
[]
[null,null,"LV Pole Mounted Service Boxes (Outdoor)"]
[null,null,"Supply and install on a wooden and/or concrete pole a pole mounted distribution box as specified complete with pole mounting brackets, cable ties, PG clamps, miniture circuit breaker(s), neutral, phase and earth bars, insulated copper tails for connecting to LV ABC, insulation piercing connectors and factory installed cable openings. Included shall be the stainless steel strapping and buckles and terminations of the tails onto the LV ABC."]
[null,5.33,"BOX,POLE TOP SPLIT METER 2-WAY 50A D3055 ",3055,"No",80,0,0,0,0,0]
[null,5.34,"BOX,POLE TOP SPLIT METER 4-WAY 50A D3055 ",null,"No",19,0,0,0,0,0]
[null,null,"PADLOCK, ST GEN MASTER SR ORANGE",null,"No",99,0,0,0,0,0]
[]
[null,null,"Testing"]
[null,null,"Allowance shall be made for the testing of each LV ABC distributor on accordance with the project specification. Included shall be the provision of test certificates and all documentation as required."]
[]
[null,5.35,"LV Test, per zone.  Ref. SCSASABZ1",null,"No",13,null,0,0,0,0]
[]
[null,null,"General"]
[]
[null,5.36,"Supply and install ABC Full tension Joints as per the DT Standards - Single phase ABC (35mm2)",null,"Ea"]
[null,5.37,"Supply and install ABC Full tension Joints as per the DT Standards - Dual phase ABC (35mm2)",null,"Ea"]
[null,5.38,"Supply and install ABC Full tension Joints as per the DT Standards - Three phase ABC (35mm2)",null,"Ea"]
[null,5.39,"Phasing: Allow for verification of the customer phasing as per the Construction drawings.",null,"zone",123,null,0,0,0,0]
[]
[null,null,"TOTAL : Carried forward to summary",null,null,"TOTALS",0,0,0,0,0]
[{"$nulls":8}," "]

{"sheet":"6 House conn","index":6,"n_rows":42,"n_cols":11,"rows_kept":42,"merged":[[1,1,1,10],[2,6,2,10],[3,1,4,2],[3,6,3,10]],"flags":["formulas_cached_only"]}
[]
[null,"BILL NO 6 - HOUSE CONNECTIONS: R250 per connection will be held back by Eskom until the timeous delivery and population of the PCS file as required for the CDX download."]
[{"$nulls":6},{"v":0,"d":"R 0.00"}]
[null,"Nomlacu  Electrification BoQ Phase 2",{"$nulls":4},"PRICE (EXCL VAT)"]
[{"$nulls":3},"DDT Ref","Unit","Quantity","Supply Rate","Supply Total","Install   Rate","Install Total","Total Price (R)"]
[]
[null,null,"House Connections"]
[null,null,"Installation, testing, commissioning complete including CoC, IC's, sealing and as built drawing on completion. Includes installation of EMU in PTB, Ready Board, CIU LCD Keypad, Meter Seal and associated accessories. Make good house walls.  Poles and excavations are measured elsewhere.  Includes installation of meter.  "]
[null,"6.1","Overhead service connection direct to dwelling (from the pole top box to the pre-paid meter)  (Type A) to brick dwelling","0360","No",0]
[null,"6.2","Overhead service connection with service pole (from the pole top box to the pre-paid meter) (Type B) to mud dwelling","0361","No",123,0,0,0,0,0]
[]
[null,null,"Conductor"]
[null,"Note","Measured lengths for stringing shall be net line route lengths and unit rates shall include for sag, cut-offs etc."]
[]
[null,null,"Installation including all glands, lugs, shrouds, termination and connections as required.  Include safe storage, transport to site and stringing.  Connect power (L-N) from EMU to Ready Board (E/L & MCB) and Comms pair from EMU to CIU."]
[null,"6.3","Cable 1kV 1C 6mmSQ Concentric Cable with comms",null,"m",6150,0,0,0,0,0]
[null,"6.4","Cable 1kV 1C 10mmSQ Concentric Cable",null,"m",{"$nulls":4},0]
[]
[null,null,"Sundry Items"]
[null,null,"Recieve and safely store the following poles.  Transport to site of works and install pole in excavated hole, including cutting and scafing, kicking bolts, bonding, treating, etc.  Excavation and compaction are measured elsewhere."]
[null,"6.5","5m pole, 80-100mm top diameter","0058A","No",123,0,0,0,0,0]
[null,"6.6","7m Pole, 100-120mm top diameter","0050B","No",20,0,0,0,0,0]
[null,"6.7","9m Pole, 140-159mm top diameter","0055B","No",null,null,0]
[null,"6.8","LV Stay (Service Connection)","0341","No",null,null,0]
[null,"6.9","Intermediate Suspension / Strain assembly","0366/ 0384","No",246,0,0,0,0,0]
[null,"6.10","Install 'Unique Seals' supplied by Eskom and record on Control Sheet and PCS file.  Two seals per unit.  ",null,"No",123,null,0,0,0,0]
[null,"6.11","Supply and install Marketing Labels complete.  Labels to the Eskom Standard SCSSCAAP5 and TQGHSP05.",null,"No",738,0,0,0,0,0]
[null,"6.12","Submit populated Control Sheet and PCS CorDaptix information to the Project Engineer upon the successful energising  of a customer. Payment will only be made upon the successful loading of the Data onto Eskom's CorDaptix software system.  Resolve queries raised by Eskom and the Engineer.Including GPS Coordinates",null,null,123,null,0,0,0,0]
[null,null,"Metering System"]
[null,"6,13","DIN Rail Single Phase PLC Smart Split Meter",null,"No",123,0,0,0,0,0]
[null,"6,14","CIU, PLC 2, 230V, English",null,"No",123,0,0,0,0,0]
[null,"6,15","ReadyBoard, Smart Split meter 2x16A ",null,"No",123,0,0,0,0,0]
[null,"6,16","Wooden Backboard for Ready board mounting (for Tin and Mud houses)",null,"No",123,0,0,0,0,0]
[null,"6,17","Data Concentractor Kiosk",null,"No",6,0,0,0,0,0]
[null,"6,18","Concentrator cable  - 4mm 4core CU Armoured Service Cable",null,"m",9,0,0,0,0,0]
[null,null,"Determination of pole positions, excavate, and supply a mechanical boring device if required. The rate shall include backfilling, compaction to 93% MOD AASHTO density, and where necessary the supply and transportation of suitable ground as may be required to receive the desired compaction, except where cement is specified. Any damage to existing services shall be made good by the Contractor at his own expense and to the approval or the PM(C)."]
[null,"6,19","Hole for 5m service pole - 1.0m deep",null,"No",123,null,null,0,0,0]
[null,"6,20","Hole for 7m service pole - 1.3m deep",null,"No",20,null,null,0,0,0]
[null,"6,21","Hole for 9m service pole - 1.5m deep",null,"No",0]
[null,"6,22","Hole for service connection stay - 1.3m deep",null,"No",0]
[]
[null,null,"TOTAL : Carried forward to summary",null,null,"TOTALS",0,0,0,0,0]

{"sheet":"7 Dismantling","index":7,"n_rows":15,"n_cols":9,"rows_kept":15,"merged":[[2,6,2,8],[3,1,4,2],[3,6,3,8]],"flags":["formulas_cached_only"]}
[]
[null,"BILL NO 7 - DISMANTLING AND REMOVAL"]
[]
[null,"Nomlacu  Electrification BoQ Phase 2"]
[{"$nulls":3},"Detail Ref","Unit","Quantity","Install   Rate","Install Total","Total Price (R)"]
[{"$nulls":8},""]
[]
[null,null,"Recovering of Transformers, Structures, Insulators and Line Hardware"]
[null,null,"Allow for the disassembly , removal  transport to site store & to New Germany and booked back to stores with the relevant documentation.  Include the backfilling consolidation and levelling of soil from excavation at the site of recovery."]
[null,"7.1","Transformers",null,"No",2,0,0,0]
[null,"7.2","Woodpoles MV incl. crossarms, insulators & hardware",null,"No",13,0,0,0]
[null,"7.3","Stays assemblies complete (LV/MV)",null,"No",10,0,0,0]
[null,"7.4","Cross Arms, including assembly, accessories etc",null,"No",8,0,0,0]
[null,"7.5","MV/LV  Conductor",null,"m",3000,0,0,0]
[null,null,"TOTAL : Carried forward to summary",null,null,"TOTALS",0,0,0]

{"sheet":"9 Summary","index":8,"n_rows":28,"n_cols":13,"rows_kept":28,"merged":[[2,4,2,6],[3,1,4,2],[3,3,4,3],[3,4,4,6]],"flags":["formulas_cached_only"]}
[]
[null,"FINAL SUMMARY"]
[]
[null,"Nomlacu  Electrification BoQ Phase 2"]
[]
[null,"Item","Description","Check","Total Supply","Total Install","Total Price (R)"]
[]
[null,"1","PRELIMINARY AND GENERAL",null,null,0,0]
[]
[null,2,"MEDIUM VOLTAGE SWITCHGEAR, SECTIONALISERS, TRANSFORMERS, ETC.","Ok",0,0,0]
[null,3,"MEDIUM VOLTAGE OVERHEAD DISTRIBUTION SYSTEM","Ok",0,0,0]
[]
[null,4,"SUPPORT FOR OVERHEAD RETICULATION","Ok",0,0,0]
[]
[null,5,"LOW VOLTAGE OVERHEAD DISTRIBUTION LINES","Ok",0,0,0]
[{"$nulls":12}," "]
[null,6,"CUSTOMER SERVICES AND GENERAL","Ok",0,0,0]
[]
[null,7,"DISMANTLING",null,null,0,0]
[null,null,"TOTAL  INCLUSIVE OF PROVISIONAL SUMS (excluding VAT) ",null,0,0,0]
[null,null,"Cost Per Connection",{"$nulls":3},0]
[]
[]
[null,null,"Sub-total 1",{"$nulls":3},0]
[null,null,"Contingencies @ 10%",{"$nulls":3},0]
[null,null,"Sub-Total 2",{"$nulls":3},0]
[null,null,"Vat @ 15%",{"$nulls":3},0]
[null,null,"Total Project Cost inclusive of provisional sums",{"$nulls":3},0]