{"text_format":"3","workbook":"xls","n_sheets":16,"sheets":["Instructions","Mandatory Requirements","Questionnaire","Technical Schedules A&B","Safe Operation","Performance","Durability","Track Record - Offered","2V AGM Cells","12V AGM Cells","2V Gel Cells","12V Gel Cells","Temp Derating Factors","Customer Details","Deviation Schedule","Lists"],"not_rendered":{"external_links":1,"defined_names":12},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Instructions","index":0,"n_rows":44,"n_cols":2,"rows_kept":44,"merged":[[11,0,13,0],[15,0,16,0],[18,0,20,0],[22,0,27,0],[29,0,30,0],[32,0,33,0],[37,0,38,0]],"flags":["formulas_cached_only"]}
["Instructions for completing this workbook"]
[]
["1) The cells where information is required to be entered is unprotected in this workbook."]
["2) Complete all Light Green shaded areas with the relevant requested information. Where the colour shading is not shown, complete the accessible cells."]
["3) All information shall be submitted in electronic format and this workbook complete in MS Excel format as requested."]
["4) Any other format for the submission of the requested electronic information will NOT be accepted OR evaluated."]
["5) Reference files shall be posted under the relevant folder names indicated below for the different sections of this workbook."]
["6) Filenames shall be descriptive to indicate what information it contains."]
["7) The latest reference documents are indicated on the worksheet named \"Reference documents\""]
[]
["Completing the Worksheets"]
["Mandatory Requirements","1) Complete all questions in the space provided. (Note: All mandatory requirements need to be \"Yes\" in order to proceed with evaluation)"]
[null,"2) All mandatory requirements must be answer with a \"Yes\" before the tenderer can be evaluated further "]
[null,"3) Should the tenderer fail to meet ANY One of the mandatory requirements they will be disqualified"]
[]
["Questionnaire","1) Complete all questions in the space provided."]
[null,"2) Post all relevant electronic copies of documents under folder named, \"Questionnaire\"."]
[]
["Technical Schedules","1) Complete the worksheet as required. (Note: A minimum score of 80% is required for the offered product to be technically Acceptable)"]
[null,"2) Post all relevant electronic copies of documents under folder named, \"Technical Schedules\"."]
[null,"3) Worksheets titled \"Safe Operation\", \"Performance\" and \"Durability\" shall be fully completed with relevant Test Report information."]
[]
["Track Record - Offered","1) First list countries with similar climatic conditions as South Africa."]
[null,"2) Then list any other countries for which you have information."]
[null,"3) To make the list not too exhaustive, you may in addition to the track records provided for the four countries make mentioned of other countries and mention the references in the space provided."]
[null,"4) The track record provided shall be exclusively for the equipment offered."]
[null,"5) Any other relevant references that will aid in forming an idea of the track record of the company as a power electronics supplier can be entered under Section E Other References."]
[null,"6) Post all relevant electronic copies of documents under folder named, \"Track Record - Offered\"."]
[]
["Offered Equipment","1) Enter the cell information in the tables named \"2V AGM Cells\", \"12V AGM Cells\", \"2V Gel Cells\" and \"12V Gel Cells\"."]
[null,"2) Post all relevant electronic copies of documents under folder named, \"Offered Equipment\"."]
[]
["Temperature derating factors","1) Complete the table named \"Temp Derating Factors\" for different discharge rates indicating the time periods where applicable."]
[null,"2) Post all relevant electronic copies of documents under folder named, \"Temp Derating Factors\"."]
[]
["Customer Details","1) Complete this worksheet with all the details of contactable references."]
[]
["Deviation Schedule","1) Complete this worksheet with all relevant deviations."]
[null,"2) Post all relevant electronic copies of test certificates / documents under folder named, \"Deviation Schedule\"."]
[]
["Revisions to Rev 1:"]
["1) Main numbering level changed from 4 to 3 e.g. 4.3.5 previously will now be 3.3.5"]
["2) Additional clauses of Rev 2 of 240-51999453 indicated in RED on the Techical Schedule"]
["3) Clause 3.3.4 b): milli-ohm (mΩ) on Rev 1 Technical Schedule changed to ohm (Ω) as required by latest  Rev 2 of 240-51999453"]

{"sheet":"Mandatory Requirements","index":1,"n_rows":10,"n_cols":5,"rows_kept":10,"merged":[[0,0,0,3],[7,0,7,4]],"flags":["formulas_cached_only"]}
["Technical Gatekeepers (Note: All gatekeepers need to be \"Yes\" in order to proceed with evaluation)"]
[]
["#","Mandatory Technical Criteria Description","Reference to Technical Specification / Tender Returnable","Comply (YES/NO)","Comments"]
["1.       ","Is all information supplied in English? "]
["2.       ","Are completed Technical Schedules A&B for Eskom standard [1] 240-51999453, including any deviations, submitted? ","Normative Reference [1]"]
["3.","Tenderers shall have a permanent South African office for supply and support of standby batteries."]
["4.","Is Deviations to Referenced Technical Standard, submitted with the associated declaration signed by the duly authorised Tenderer’s representative? ","Annex D"]
["Threshold. Should the tenderer fail to meet ANY ONE of the above requirements they will be automatically disqualified. "]
[null,"Company Name:",null,"Date"]
[null,"Representative Name:",null,"Signature"]

{"sheet":"Questionnaire","index":2,"n_rows":47,"n_cols":4,"rows_kept":47,"merged":[[7,0,8,0],[7,3,8,3],[9,0,10,0],[9,3,10,3],[11,0,12,0],[11,3,12,3],[16,0,21,0],[35,0,36,0],[35,3,36,3],[37,0,38,0],[37,3,38,3],[39,0,40,0],[39,3,40,3]],"flags":["formulas_cached_only"]}
[null,"Question","Response","Proof to be submitted"]
["A","Tenderer"]
[1,"Company name"]
[2,"Address of Head Quarters"]
[3,"Contact details"]
[4,"Website adress"]
[5,"Company organogram",null,"Organogram"]
[6,"Does your company have ISO 9001:2008 or similar certification?",null,"Copy of Certificate"]
[null,"If yes, what is the expiration date of such certification?"]
[7,"Does your company have ISO 14001:2004 or similar certification?",null,"Copy of Certificate"]
[null,"If yes, what is the expiration date of such certification?"]
[8,"Does your company have OHSAS 18001:2007 or similar certification?",null,"Copy of Certificate"]
[null,"If yes, what is the expiration date of such certification?"]
[9,"If other certifications exist, please state them here.",null,"Copy of Certificate/s"]
[10,"Is there a formal agreement between your company and the manufacturer (OEM)?",null,"Copy of Certificate or Agreement"]
[11,"Have your staff been trained on the equipment been offered?",null,"Copy of Certificates or Agreements"]
[12,"Will your company be able to provide the following after sales support if and when required:"]
[null,"Technical support",null,"Company Organogram & CVs"]
[null,"Installation"]
[null,"Commissioning"]
[null,"Maintenance"]
[null,"De-commissioning"]
[13,"Does your company have the capability to perform local R&D?"]
[14,"Does your company have the capability to perform local faultfinding and repair?"]
[15,"What transport company will be used for deliveries?"]
[16,"Do they have the necessary licensing to operate as a dangerous goods transporter?",null,"Certificates / Dept. of Transport Lisence"]
[17,"What procedures are in place to manage field failures and ensure that these are effectively and timeously addressed.?",null,"Field Failure Management Procedure"]
[18,"What recycling procedure is place to ensure that redundant equipment is recycled in an environmentally friendly manner?",null,"Recycling Procedure & Certification"]
[]
["B","Manufacturer / OEM"]
[1,"Company name"]
[2,"Address of Head Quarters"]
[3,"Contact details",null,"Contact details of OEM assigned resource for this project"]
[4,"Website adress"]
[5,"Company organogram",null,"Organogram"]
[6,"Does your company have ISO 9001:2008 or similar certification?",null,"Copy of Certificate"]
[null,"If yes, what is the expiration date of such certification?"]
[7,"Does your company have ISO 14001:2004 or similar certification?",null,"Copy of Certificate"]
[null,"If yes, what is the expiration date of such certification?"]
[8,"Does your company have OHSAS 18001:2007 or similar certification?",null,"Copy of Certificate"]
[null,"If yes, what is the expiration date of such certification?"]
[9,"If other certifications exist, please state them here.",null,"Copy of Certificate/s"]
[10,"Where is the equipment R&D performed?"]
[11,"Where is the equipment manufactured?"]
[12,"Where will equipment be send that cannot be repaired locally?"]
[13,"What procedures are in place to manage field failures and ensure that these are effectively and timeously addressed.?",null,"Field Failure Management Procedure"]
[14,"What recycling procedure is place to ensure that redundant equipment is recycled in an environmentally friendly manner?",null,"Recycling Procedure & Certification"]

{"sheet":"Technical Schedules A&B","index":3,"n_rows":245,"n_cols":6,"rows_kept":245,"merged":[[1,0,1,3],[3,0,3,5],[5,0,6,0],[5,1,6,1],[5,2,6,3],[5,4,5,5],[9,0,12,0],[25,0,26,0],[27,0,30,0],[27,1,30,1],[27,3,30,3],[37,0,39,0],[40,0,42,0],[54,0,55,0],[57,0,60,0],[57,1,60,1],[57,3,60,3],[61,0,64,0],[61,1,64,1],[61,3,64,3],[90,0,91,0],[90,1,91,1],[90,2,91,2],[118,0,121,0],[118,1,121,1],[118,3,121,3],[125,0,136,0],[145,0,146,0],[160,0,164,0],[167,0,170,0],[167,1,170,1],[167,3,170,3],[171,0,177,0],[185,0,187,0]],"flags":["formulas_cached_only"]}
[]
["Reference refers to the filename or document title and the page number/s and clause number in the document where the said compliance is indicated or mentioned."]
[]
["240-51999453, Standard specification for Valve-regulated Lead-acid Cells, Rev 2"]
[]
["ITEM","DESCRIPTION","SCHEDULE A",null,"SCHEDULE B"]
[{"$nulls":4},"Compliance","Reference / Conditions"]
[3,"APPLICATION DESCRIPTION INFORMATION",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
[3.1,"GENERAL",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["a)","Plate types",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
[null,"Flat Plate","Yes"]
[null,"Planté plate","No"]
[null,"Tubular plate","Yes"]
["b)","Fully commissioned","Yes"]
["c)","Cells capacity tested prior to shipment","Yes"]
["d)","Capacity test results available","Yes"]
["e)","All accessories supplied","Yes - as specified"]
["f)","Supply of all additional equipment and services","Yes - as specified"]
["g)","Direct link between Eskom and OEM","Yes - as specified"]
["h)","OEM letter key contents","Yes - as specified"]
[{"$nulls":4},"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
[3.2,"ELECTRICAL PERFORMANCE REQUIREMENTS",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.2.1","General",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["b)","Reference temperature",20,"°C"]
["3.2.2","Rated capacity",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["b)","Discharge period",10,"h"]
[null,"End-of-discharge voltage per cell",1.8,"V"]
["c)","Required capacity ranges","Provide detail on 2V AGM Cell Worksheets","Ah"]
[null,null,"Provide detail on 12V AGM Cell Worksheets"]
[null,null,"Provide detail on 2V Gel Cell Worksheets"]
[null,null,"Provide detail on 12V Gel Cell Worksheets"]
["3.2.3","Discharge tables and capacity rating factors",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["a)","Discharge curves and tables","Yes as specified"]
["b)","Kt Factors","Yes as specified"]
["3.2.4","Charging voltages",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["a)","Suitability for floating operation","Yes"]
["b)","Recommended float voltage range at reference temperature","Specify","V"]
["c)","Boost charge voltage range per cell (range)","Specify","V"]
[null,"Recommended boost charge frequency","Specify"]
[null,"Conditions requiring boost charge","Specify"]
["d)","Equalize charge voltage range per cell","Specify","V"]
[null,"Recommended equalize charge frequency","Specify"]
[null,"Conditions requiring equalize charge","Specify"]
["3.2.5","Tolerance to AC components of the DC supply",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["a)","Maximum allowable ripple current and the effect thereof on expected battery life","Specify"]
["b)","Effect on expected battery life where ripple is > 5%C10 during float charge and 20%C10 during boost charge or equalise charge","Specify"]
["3.2.6","Effect of temperature",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["a)","Effect of temperature on expected battery life","Specify"]
["b)","Temperature derating factors for the temperature range of -5 °C to +45 °C","Specify on \"Temperature Derating Factors\" worksheet"]
["c)","Temperature compensation factor/s to prevent over- and undercharging of cells.","Specify","mV/°C"]
[{"$nulls":4},"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
[3.3,"SAFE OPERATION REQUIREMENTS","Complete table on Worksheet \"Safe Operation\"",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.3.1","Test in accordance with standard","SANS 60896-21",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.3.2","Gas emission (at float voltage and at 2,40 Vpc)","Specify",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.3.3","High current tolerance","Pass",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
[null,"Value of the measured current ","Specify","A","XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.3.4","Short-circuit current and DC internal resistance",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["a)","Value of the short-circuit current, Isc","Provide detail on 2V AGM Cell Worksheets","A","XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
[null,null,"Provide detail on 12V AGM Cell Worksheets"]
[null,null,"Provide detail on 2V Gel Cell Worksheets"]
[null,null,"Provide detail on 12V Gel Cell Worksheets",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["b)","Value of the internal resistance, Ri, at the reference temperature of 25 °C at recommended SG and fully charged float voltage","Provide detail on 2V AGM Cell Worksheets","W","XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
[null,null,"Provide detail on 12V AGM Cell Worksheets"]
[null,null,"Provide detail on 2V Gel Cell Worksheets"]
[null,null,"Provide detail on 12V Gel Cell Worksheets",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.3.5","Internal ignition from external spark sources","Pass",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.3.6","Protection against ground short propensity","Pass",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.3.7","Content and durability of required markings",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["b)","Information shall remain readable and remain in place","Pass",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["c)","Approved cleaning agent ","Specify",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["d)","Minimum technical information","As specified",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["e)","ISO warning symbols ","As specified",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["f)","Environmental protection and recycling symbols ","As specified",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["g)","ISO 1043-1 material symbol ","As specified",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["h)","ISO symbol durability","As specified",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.3.8","Valve operation","Pass",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.3.9","Flammability rating of materials","Specify",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.3.10","Intercell connector performance","Specify",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
[{"$nulls":4},"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
[3.4,"PERFORMANCE REQUIREMENTS","Complete table on Worksheet \"Performance\"",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.4.1","Test conditions and methods of test","As specified in SANS 60896-21",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.4.2","Discharge capacity performance",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["b)","The sample cells shall have at least delivered an actual capacity (Ca) of ≥ 0,95 Crt.","Pass",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.4.3","Charge retention during storage",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["b)","Each individual test unit shall have a retained capacity of at least ≥ 0,7 Crt after six months of storage.","Pass",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.4.4","Float service with daily discharges",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["b)","The tenderer shall report the capacity available and total number of cycles achieved under float voltage settings (Caf) and boost voltage settings (Cab) for reliable mains power, unreliable mains power and very unreliable mains power.","Specify",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.4.5","Recharge behaviour",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["b)","The effective available capacity, as a percentage of the original capacity after a recharge for 24 h and 168 h using only the recommended float voltage setting shall be at least 90% and 98%, respectively.","Pass",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.4.6","Critical depth of discharge",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["b)","The tenderer shall state the maximum depth of discharge in both ampere-hours and V/cell at which the load disconnection device shall be activated.","Specify","Ah","XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
[{"$nulls":3},"V/cell","XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
[{"$nulls":4},"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
[3.5,"DURABILITY REQUIREMENTS","Complete table on Worksheet \"Durability\"",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.5.1","Test conditions and methods of test","As specified in SANS 60896-21",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.5.2","Service life at reference temperature",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["b)","The tenderer shall state the days at the reference temperature, on float charge, of the units to a residual capacity of 0,8 Crt after a 3 h rate discharge test.","Specify","days","XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.5.3","Service life at elevated operating temperature",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["b)","The tenderer shall state the days at 40 °C, on float charge, of the units to a residual capacity of 0,8 Crt after a 3 h rate discharge test.","Specify","days","XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.5.4","Impact of stress temperature",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["b)","The tenderer shall report the days at elevated temperature, on float charge, of the units to a residual capacity of 0,8 Crt after both 3 h rate and 0,25 h rate discharge tests.","Specify","days","XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.5.5","Impact of abusive over-discharge",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["b)","The unbalanced string over-discharge capacity (Caod) shall be ≥ 0,80 Crt for the string.","Pass",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["c)","The cyclic over-discharge capacity (Caoc) shall be ≥ 0,90 Crt for the string.","Pass",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.5.6","Thermal runaway sensitivity",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["b)","The units shall achieve at least one week below 60 °C at 2,45 V/cell and at least 24 h below 60 °C at 2,60 V/cell.","Pass",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["c)","The tenderer shall state the ultimate time to 60 °C or ultimate temperature after 168 h at 2,45 V/cell and 2,60 V/cell.","Specify","h or °C","XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.5.7","Capacity impact of low temperature service",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["b)","The available capacity shall be > 0,95 Crt with no bulging, fractures and other induced mechanical damages.","Pass",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.5.8","Dimensional stability at elevated internal pressures and temperatures",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["b)","The tenderer shall state dimensional changes in percentage and in millimetres.","Specify",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.5.9","Stability against mechanical abuse",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["b)","No leakage shall be detectable after two times two drops.","Pass",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
[{"$nulls":4},"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
[3.6,"OTHER REQUIREMENTS",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.6.1","Cell numbers",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["a) - e)","Labels","As specified"]
["f)","When called for by the purchaser, individual cells shall be uniquely labelled with a barcode, the detailed requirements of which shall be supplied by Eskom.","No"]
["3.6.2","Recommended torque values","Provide detail on 2V AGM Cell Worksheets","N.m"]
[null,null,"Provide detail on 12V AGM Cell Worksheets"]
[null,null,"Provide detail on 2V Gel Cell Worksheets"]
[null,null,"Provide detail on 12V Gel Cell Worksheets"]
["3.6.3","The tenderer shall state the recommended cell orientation (upright or sideways) for each offered cell/battery, which will not affect its expected performance.","Specify"]
[{"$nulls":4},"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
[3.7,"OPERATIONAL REQUIREMENTS",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.7.1","Altitude",2200,"m"]
[null,"Relative humidity (non-condensing)","10 – 85 non-condensing","%"]
[null,"Lightning incidence","High"]
[null,"Pollution","Medium - high with conductive particles when wet"]
[null,"Outdoor air temperatures:",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
[null,"Maximum",45,"°C"]
[null,"Average",35,"°C"]
[null,"Minimum",-10,"°C"]
[null,"Battery room air temperatures:",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
[null,"Maximum",40,"°C"]
[null,"Daily average",30,"°C"]
[null,"Minimum",-5,"°C"]
["3.7.2","Application","Information",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.7.3","Charging regimes","Information",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
[null,"Proposed charging regimes and settings","Information",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
[null,"Requirements","Information",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
[null,"The tenderer shall state whether the charging regimes and settings proposed  are accepted.","Specify"]
[null,"If the charging regimes and settings proposed  are not accepted, then alternative charging regimes and settings shall be recommended and submitted as part of the tender documentation.","Specify"]
["3.7.4","Commissioning",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["a)","Cells and batteries shall be commissioned in line with the requirements of 240-56177186.","Information",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["b)","The tenderer shall state the acceptance of these conditions.","Specify"]
[null,"If these conditions are not accepted, then the tenderer shall include commissioning instructions as part of the tender documentation, indicating the differences between the procedures as described in 240-56177186.","Specify"]
["3.7.5","Maintenance",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["a)","Cells and batteries shall be maintained in line with the requirements of 240-56356452 and 240-56535959.","Information",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["b)","The tenderer shall state the acceptance of these conditions.","Specify"]
["c)","If these conditions are not accepted, then the tenderer shall include maintenance instructions as part of the tender documentation, indicating the differences between the maintenance instructions as described in 240-56356452 and 240-56535959.","Specify"]
["d)","Out-of-Step conditions and remedial actions","Specify"]
["3.7.6","Accessories",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["a)","Cells shall be supplied complete with all necessary intercell connectors, nuts, bolts and washers (including flat and spring washers).","Yes"]
["b)","The material used for the bolts, nuts and washers shall be suitable for the application and ensure a reliable connection for the life of the equipment.","Specify"]
["c)","The bolts, nuts and washers shall be suitable for the connections, and shall not deform or sheer under the recommended torque levels as stated in 4.6.2.","Specify"]
["3.7.7","Terminating devices and inter-row connectors",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
[null,"Terminating devices and Inter-row connectors supplied","Yes"]
[{"$nulls":4},"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.7.8","EQUIPMENT PERFORMANCE",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
[null,"Full track record ","Indicate figures on Track Record - Offered Sheet"]
[null,"Equipment hours of installed units / model / type","Yes"]
[null,"Number of units in the field / model / type","Yes"]
[null,"Environmental conditions where equipment installed","Yes"]
[null,"Known problems / exceptional perfromance","Yes"]
[{"$nulls":4},"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.7.9","TECHNICAL MANUALS & OTHER DOCUMENTATION",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.7.9.1","Table with technical information","Provide detail on 2V AGM Cell Worksheets"]
[null,null,"Provide detail on 12V AGM Cell Worksheets"]
[null,null,"Provide detail on 2V Gel Cell Worksheets"]
[null,null,"Provide detail on 12V Gel Cell Worksheets"]
["3.7.9.2","Installation manual","Yes"]
[null,"Commissioning manual","Yes"]
[null,"Maintenance manual","Yes"]
[null,"Safety instructions","Yes"]
[null,"Commissioning test results traceable to unique cells","Yes"]
[null,"Material Safety Data Sheets available per consignment","Yes"]
[null,"Clear storage and freshening charge instructions","Yes"]
[{"$nulls":4},"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.7.10","TOOLS",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
[null,"Special tools or keys required","Specify"]
[{"$nulls":4},"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.7.11","SPARES","As specified"]
[{"$nulls":4},"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.7.12","TRAINING",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
[null,"Recommended course structure included","Yes"]
[null,"Who will present the training","Specify"]
[null,"Train-the-trainer type course","Yes"]
[{"$nulls":4},"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.7.13","WARRANTY REQUIREMENTS",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["1)","Guarantee",1,"yr"]
["2)","Warranty","Yes - Specify"]
["3)","OEM endorsed warranty","Yes"]
[{"$nulls":4},"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.7.14","LOCAL SUPPORT",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["a)","Supplier response during commissioning","As specified"]
["b)","Regional support","As specified"]
[{"$nulls":4},"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.7.15","DISPOSAL",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["a)","Disposal certificates confirming approved process","As specified"]
["b)","Disposal procedure","As specified"]
["c)","Disposal services","As specified"]
["d) 1)","First right of refusal","As specified"]
["d) 2)","Transportation in lieu of Credit for scrap lead","As specified"]
[{"$nulls":4},"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.7.16","EQUIPMENT LIMITATIONS","Specify"]
[{"$nulls":4},"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
[3.8,"ANCILLARY EQUIPMENT"]
["3.8.1","Maintenance equipment: When called for by the purchaser, the following maintenance equipment, as per 240-56356452, shall be made available:","Yes"]
["a)","Anti-corrosion lubricant.","Yes"]
["b)","Touch-up paint","Yes"]
["c)","Paint brush","Yes"]
["d)","Paper towels","Yes"]
["e)","Thermometer – the thermometer shall be of the infrared type.","Yes - as specified"]
["f)","Battery logbooks","Yes"]
["3.8.2","Personal protective equipment: When called for by the purchaser, the following personal protective equipment  shall be made available; all offered personal protective equipment shall comply with the requirements of 240-44175132:","Yes"]
["1)","Apron","Yes"]
["2)","Face shield","Yes"]
["3)","Gloves","Yes"]
["3.8.3","PPE rack / cabinet / box","Yes - Specify"]
["3.8.4","Battery cabinets"]
["a)","Comply with 240-60725641","Yes"]
["b)","Cabinet type","Fixed Frame"]
["c)","Cabinet doors","With doors"]
["d)","Cabinet side panels","As required"]
["e)","Sufficiently strengthened for weight","Yes"]
["3.8.5","Battery stands: When called for by the purchaser, battery stands shall be offered","Yes"]
["3.8.6","Safety signs: When called for by the purchaser, the tenderer shall make safety signs available that comply with the requirements of 240-53114264.","Yes"]
[{"$nulls":4},"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
[3.9,"TESTS","Information",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.9.1","General"]
["a) - c)","Compliance required","Yes"]
["3.9.3","Type Tests","Covered above",null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.9.4","Type Test Certificates provided - SANS 60896-21","Yes"]
["3.9.5","Clearance for dispatch","Yes - as specified"]
["3.9.6","Commissioning tests","Yes"]
[{"$nulls":4},"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
[{"v":3.1,"d":"3.10"},"PACKAGING, LABELLING AND TRANSPORT",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["3.10.1","Packaging","As specified"]
["3.10.2","Labelling","As specified"]
["3.10.3","Transport",null,null,"XXXXXXXXXXXXXXXXXXXXXX","XXXXXXXXXXXXXXXXXXXXXX"]
["a)","Legal compliance with National Road Traffic Act ","Yes"]
["b)","Third party compliance","As specified"]
["c) & d) & e)","Offloading and placement during delivery","As specified"]
["f)","Communication between Eskom and Supplier","As specified"]

{"sheet":"Safe Operation","index":4,"n_rows":26,"n_cols":12,"rows_kept":26,"merged":[[0,4,0,7],[0,8,0,11],[4,0,7,0],[4,2,7,2],[8,0,9,0],[11,2,12,2]],"flags":["formulas_cached_only"]}
[null,"DD = Dropdown",null,null,"Flat Plate",{"$nulls":3},"Tubular Plate"]
[null,"FC = Full Compliance, PC = Partial Compliance, NC = Not Compliant",null,null,"2V AGM","12V AGM","2V Gel","12V Gel","2V AGM","12V AGM","2V Gel","12V Gel"]
[3.3,"SAFE OPERATION REQUIREMENTS"]
["3.3.1","Test in accordance with standard","SANS 60896-21","XX"]
["3.3.2","Gas emission (at float voltage and at 2,40 Vpc)","Specify","XX"]
[null,"Gas volume in millilitres",null,"ml"]
[null,"Time duration in hours",null,"h"]
[null,"Capacity in ampere-hours",null,"Ah"]
["3.3.3","High current tolerance","Pass","DD"]
[null,"Value of the measured current ","Specify","A"]
["3.3.4","Short-circuit current and DC internal resistance",null,"XX"]
["a)","Value of the short-circuit current, Isc [A]","Yes - specify on provided sheets or tables","DD"]
["b)","Value of the internal resistance, Ri, at the reference temperature of 20°C at recommended SG and fully charged float voltage [mW]",null,"DD"]
["3.3.5","Internal ignition from external spark sources","Pass","DD"]
["3.3.6","Protection against ground short propensity","Pass","DD"]
["3.3.7","Content and durability of required markings",null,"XX"]
["b)","Information shall remain readable and remain in place","Pass","DD"]
["c)","Approved cleaning agent ","Specify"]
["d)","Minimum technical information","As specified","DD"]
["e)","ISO warning symbols ","As specified","DD"]
["f)","Environmental protection and recycling symbols ","As specified","DD"]
["g)","ISO 1043-1 material symbol ","As specified","DD"]
["h)","ISO symbol durability","As specified","DD"]
["3.3.8","Valve operation","Pass","DD"]
["3.3.9","Flammability rating of materials","Specify","DD"]
["3.3.10","Intercell connector performance","Specify"]

{"sheet":"Performance","index":5,"n_rows":15,"n_cols":12,"rows_kept":15,"merged":[[0,4,0,7],[0,8,0,11]],"flags":["formulas_cached_only"]}
[null,"DD = Dropdown",null,null,"Flat Plate",{"$nulls":3},"Tubular Plate"]
[null,"FC = Full Compliance, PC = Partial Compliance, NC = Not Compliant",null,null,"2V AGM","12V AGM","2V Gel","12V Gel","2V AGM","12V AGM","2V Gel","12V Gel"]
[3.4,"PERFORMANCE REQUIREMENTS",null,"XX"]
["3.4.1","Test conditions and methods of test","As specified in SANS 60896-21","XX"]
["3.4.2","Discharge capacity performance",null,"XX"]
["b)","The sample cells shall have at least delivered an actual capacity (Ca) of ≥ 0,95 Crt.","Pass","DD"]
["3.4.3","Charge retention during storage",null,"XX"]
["b)","Each individual test unit shall have a retained capacity of at least ≥ 0,7 Crt after six months of storage.","Pass","DD"]
["3.4.4","Float service with daily discharges",null,"XX"]
["b)","The tenderer shall report the capacity available and total number of cycles achieved under float voltage settings (Caf) and boost voltage settings (Cab) for reliable mains power, unreliable mains power and very unreliable mains power.","Specify"]
["3.4.5","Recharge behaviour",null,"XX"]
["b)","The effective available capacity, as a percentage of the original capacity after a recharge for 24 h and 168 h using only the recommended float voltage setting shall be at least 90% and 98%, respectively.","Pass","DD"]
["3.4.6","Critical depth of discharge",null,"XX"]
["b)","The tenderer shall state the maximum depth of discharge in both ampere-hours and V/cell at which the load disconnection device shall be activated.","Specify","Ah"]
["b)","The tenderer shall state the maximum depth of discharge in both ampere-hours and V/cell at which the load disconnection device shall be activated.","Specify","V/cell"]

{"sheet":"Durability","index":6,"n_rows":22,"n_cols":12,"rows_kept":22,"merged":[[0,4,0,7],[0,8,0,11]],"flags":["formulas_cached_only"]}
[null,"DD = Dropdown",null,null,"Flat Plate",{"$nulls":3},"Tubular Plate"]
[null,"FC = Full Compliance, PC = Partial Compliance, NC = Not Compliant",null,null,"2V AGM","12V AGM","2V Gel","12V Gel","2V AGM","12V AGM","2V Gel","12V Gel"]
[3.5,"DURABILITY REQUIREMENTS",null,"XX"]
["3.5.1","Test conditions and methods of test","As specified in SANS 60896-21","XX"]
["3.5.2","Service life at reference temperature",null,"XX"]
["b)","The tenderer shall state the days at the reference temperature, on float charge, of the units to a residual capacity of 0,8 Crt after a 3 h rate discharge test.","Specify","days"]
["3.5.3","Service life at elevated operating temperature",null,"XX"]
["b)","The tenderer shall state the days at 40 °C, on float charge, of the units to a residual capacity of 0,8 Crt after a 3 h rate discharge test.","Specify","days"]
["3.5.4","Impact of stress temperature",null,"XX"]
["b)","The tenderer shall report the days at elevated temperature, on float charge, of the units to a residual capacity of 0,8 Crt after both 3 h rate and 0,25 h rate discharge tests.","Specify","days"]
["3.5.5","Impact of abusive over-discharge",null,"XX"]
["b)","The unbalanced string over-discharge capacity (Caod) shall be ≥ 0,80 Crt for the string.","Pass","DD"]
["c)","The cyclic over-discharge capacity (Caoc) shall be ≥ 0,90 Crt for the string.","Pass","DD"]
["3.5.6","Thermal runaway sensitivity",null,"XX"]
["b)","The units shall achieve at least one week below 60 °C at 2,45 V/cell and at least 24 h below 60 °C at 2,60 V/cell.","Pass","DD"]
["c)","The tenderer shall state the ultimate time to 60 °C or ultimate temperature after 168 h at 2,45 V/cell and 2,60 V/cell.","Specify","h or °C"]
["3.5.7","Capacity impact of low temperature service",null,"XX"]
["b)","The available capacity shall be > 0,95 Crt with no bulging, fractures and other induced mechanical damages.","Pass","DD"]
["3.5.8","Dimensional stability at elevated internal pressures and temperatures",null,"XX"]
["b)","The tenderer shall state dimensional changes in percentage and in millimetres.","Specify"]
["3.5.9","Stability against mechanical abuse",null,"XX"]
["b)","No leakage shall be detectable after two times two drops.","Pass","DD"]

{"sheet":"Track Record - Offered","index":7,"n_rows":68,"n_cols":7,"rows_kept":68,"merged":[[3,2,3,5],[3,6,3,9],[4,2,4,5],[4,6,4,9],[6,2,6,9],[7,0,8,0],[9,0,10,0],[17,2,17,5],[17,6,17,9],[19,2,19,5],[19,6,19,9],[20,2,20,5],[20,6,20,9],[22,2,22,9],[23,0,24,0],[25,0,26,0],[33,2,33,5],[33,6,33,9],[35,2,35,5],[35,6,35,9],[36,2,36,5],[36,6,36,9],[38,2,38,9],[39,0,40,0],[41,0,42,0],[49,2,49,5],[49,6,49,9],[51,2,51,5],[51,6,51,9],[52,2,52,5],[52,6,52,9],[54,2,54,9],[55,0,56,0],[57,0,58,0],[65,2,65,5],[65,6,65,9]],"flags":["formulas_cached_only"]}
[null,"Note: The track record provided shall be exclusively for the equipment offered."]
[]
[null,"Track Record of the Equipment on Offer"]
[null,"Reference - FileName or Document Title"]
[null,null,"Absorbed Glass Mat (AGM)",{"$nulls":3},"Gel"]
[null,"Model number"]
["A","Country 1:","SOUTH AFRICA"]
[1,"Oldest installation (Insert Customer/Site Name)"]
[null,"Date of installation"]
[2,"Most recent installation (Insert Customer/Site Name)"]
[null,"Date of installation"]
[3,"Number of units installed in a controlled environment"]
[4,"Number of units installed in an uncontrolled environment"]
[5,"Number of failures in a controlled environment"]
[6,"Number of failures in an uncontrolled environment"]
[7,"Number of units installed in electricity utility industry"]
[8,"Number of units installed in other industries"]
[9,"List your major customers in this country:"]
[]
[null,"Reference - FileName or Document Title"]
[null,null,"Absorbed Glass Mat (AGM)",{"$nulls":3},"Gel"]
[null,"Model number"]
["B","Country 2:"]
[1,"Oldest installation (Insert Customer/Site Name)"]
[null,"Date of installation"]
[2,"Most recent installation (Insert Customer/Site Name)"]
[null,"Date of installation"]
[3,"Number of units installed in a controlled environment"]
[4,"Number of units installed in an uncontrolled environment"]
[5,"Number of failures in a controlled environment"]
[6,"Number of failures in an uncontrolled environment"]
[7,"Number of units installed in electricity utility industry"]
[8,"Number of units installed in other industries"]
[9,"List your major customers in this country:"]
[]
[null,"Reference - FileName or Document Title"]
[null,null,"Absorbed Glass Mat (AGM)",{"$nulls":3},"Gel"]
[null,"Model number"]
["C","Country 3:"]
[1,"Oldest installation (Insert Customer/Site Name)"]
[null,"Date of installation"]
[2,"Most recent installation (Insert Customer/Site Name)"]
[null,"Date of installation"]
[3,"Number of units installed in a controlled environment"]
[4,"Number of units installed in an uncontrolled environment"]
[5,"Number of failures in a controlled environment"]
[6,"Number of failures in an uncontrolled environment"]
[7,"Number of units installed in electricity utility industry"]
[8,"Number of units installed in other industries"]
[9,"List your major customers in this country:"]
[]
[null,"Reference - FileName or Document Title"]
[null,null,"Absorbed Glass Mat (AGM)",{"$nulls":3},"Gel"]
[null,"Model number"]
["D","Country 4:"]
[1,"Oldest installation (Insert Customer/Site Name)"]
[null,"Date of installation"]
[2,"Most recent installation (Insert Customer/Site Name)"]
[null,"Date of installation"]
[3,"Number of units installed in a controlled environment"]
[4,"Number of units installed in an uncontrolled environment"]
[5,"Number of failures in a controlled environment"]
[6,"Number of failures in an uncontrolled environment"]
[7,"Number of units installed in electricity utility industry"]
[8,"Number of units installed in other industries"]
[9,"List your major customers in this country:"]
[]
["E","Other References"]

{"sheet":"2V AGM Cells","index":8,"n_rows":45,"n_cols":19,"rows_kept":45,"merged":[[1,0,2,0],[1,1,1,9],[1,10,1,18]],"flags":["formulas_cached_only"]}
["C10 Capacity @ 20°C to Veod = 1.80V/cell"]
["Required Capacity [Ah]","2V Absorbed Glass Mat (AGM) - FLAT PLATE",{"$nulls":8},"2V Absorbed Glass Mat (AGM) - TUBULAR PLATE"]
[null,"Offered Capacity [Ah]","Cell Model No.","Short Circuit Current [A]","Internal Resistance [W]","Recommended Torque Levels for Connections [N.m]","Terminals location (Front/Top)","Cell Dimensions  - LxWxH [mm]","Wet Cell Weight [kg]","Lead Content [kg]","Offered Capacity [Ah]","Cell Model No.","Short Circuit Current [A]","Internal Resistance [mW]","Recommended Torque Levels for Connections [N.m]","Terminals location (Front/Top)","Cell Dimensions  - LxWxH [mm]","Wet Cell Weight [kg]","Lead Content [kg]"]
[7.5]
[12]
[26]
[50]
[100]
[150]
[200]
[250]
[300]
[350]
[400]
[450]
[500]
[550]
[600]
[650]
[700]
[800]
[900]
[1000]
[1100]
[1200]
[1300]
[1400]
[1500]
[1600]
[1700]
[1800]
[1900]
[2000]
[2100]
[2200]
[2300]
[2400]
[2500]
[2600]
[2700]
[2800]
[2900]
[3000]
[]
["Notes:"]

{"sheet":"12V AGM Cells","index":9,"n_rows":45,"n_cols":19,"rows_kept":45,"merged":[[1,0,2,0],[1,1,1,9],[1,10,1,18]],"flags":["formulas_cached_only"]}
["C10 Capacity @ 20°C to Veod = 1.80V/cell"]
["Required Capacity [Ah]","12V Absorbed Glass Mat (AGM) - FLAT PLATE",{"$nulls":8},"12V Absorbed Glass Mat (AGM) - TUBULAR PLATE"]
[null,"Offered Capacity [Ah]","Cell Model No.","Short Circuit Current [A]","Internal Resistance [W]","Recommended Torque Levels for Connections [N.m]","Terminals location (Front/Top)","Cell Dimensions  - LxWxH [mm]","Wet Cell Weight [kg]","Lead Content [kg]","Offered Capacity [Ah]","Cell Model No.","Short Circuit Current [A]","Internal Resistance [mW]","Recommended Torque Levels for Connections [N.m]","Terminals location (Front/Top)","Cell Dimensions  - LxWxH [mm]","Wet Cell Weight [kg]","Lead Content [kg]"]
[7.5]
[12]
[26]
[50]
[100]
[150]
[200]
[250]
[300]
[350]
[400]
[450]
[500]
[550]
[600]
[650]
[700]
[800]
[900]
[1000]
[1100]
[1200]
[1300]
[1400]
[1500]
[1600]
[1700]
[1800]
[1900]
[2000]
[2100]
[2200]
[2300]
[2400]
[2500]
[2600]
[2700]
[2800]
[2900]
[3000]
[]
["Notes:"]

{"sheet":"2V Gel Cells","index":10,"n_rows":45,"n_cols":19,"rows_kept":45,"merged":[[1,0,2,0],[1,1,1,9],[1,10,1,18]],"flags":["formulas_cached_only"]}
["C10 Capacity @ 20°C to Veod = 1.80V/cell"]
["Required Capacity [Ah]","2V Gel - FLAT PLATE",{"$nulls":8},"2V Gel - TUBULAR PLATE"]
[null,"Offered Capacity [Ah]","Cell Model No.","Short Circuit Current [A]","Internal Resistance [mW]","Recommended Torque Levels for Connections [N.m]","Terminals location (Front/Top)","Cell Dimensions  - LxWxH [mm]","Wet Cell Weight [kg]","Lead Content [kg]","Offered Capacity [Ah]","Cell Model No.","Short Circuit Current [A]","Internal Resistance [W]","Recommended Torque Levels for Connections [N.m]","Terminals location (Front/Top)","Cell Dimensions  - LxWxH [mm]","Wet Cell Weight [kg]","Lead Content [kg]"]
[7.5]
[12]
[26]
[50]
[100]
[150]
[200]
[250]
[300]
[350]
[400]
[450]
[500]
[550]
[600]
[650]
[700]
[800]
[900]
[1000]
[1100]
[1200]
[1300]
[1400]
[1500]
[1600]
[1700]
[1800]
[1900]
[2000]
[2100]
[2200]
[2300]
[2400]
[2500]
[2600]
[2700]
[2800]
[2900]
[3000]
[]
["Notes:"]

{"sheet":"12V Gel Cells","index":11,"n_rows":45,"n_cols":19,"rows_kept":45,"merged":[[1,0,2,0],[1,1,1,9],[1,10,1,18]],"flags":["formulas_cached_only"]}
["C10 Capacity @ 20°C to Veod = 1.80V/cell"]
["Required Capacity [Ah]","12V Gel - FLAT PLATE",{"$nulls":8},"12V Gel - TUBULAR PLATE"]
[null,"Offered Capacity [Ah]","Cell Model No.","Short Circuit Current [A]","Internal Resistance [mW]","Recommended Torque Levels for Connections [N.m]","Terminals location (Front/Top)","Cell Dimensions  - LxWxH [mm]","Wet Cell Weight [kg]","Lead Content [kg]","Offered Capacity [Ah]","Cell Model No.","Short Circuit Current [A]","Internal Resistance [W]","Recommended Torque Levels for Connections [N.m]","Terminals location (Front/Top)","Cell Dimensions  - LxWxH [mm]","Wet Cell Weight [kg]","Lead Content [kg]"]
[7.5]
[12]
[26]
[50]
[100]
[150]
[200]
[250]
[300]
[350]
[400]
[450]
[500]
[550]
[600]
[650]
[700]
[800]
[900]
[1000]
[1100]
[1200]
[1300]
[1400]
[1500]
[1600]
[1700]
[1800]
[1900]
[2000]
[2100]
[2200]
[2300]
[2400]
[2500]
[2600]
[2700]
[2800]
[2900]
[3000]
[]
["Notes:"]

{"sheet":"Temp Derating Factors","index":12,"n_rows":23,"n_cols":13,"rows_kept":23,"merged":[[2,1,2,6],[2,7,2,12],[3,0,5,0],[3,1,3,3],[3,4,3,6],[3,7,3,9],[3,10,3,12],[19,0,19,1],[19,2,19,6],[20,0,20,1],[20,2,20,6],[21,0,21,1],[21,2,21,6],[22,0,22,1],[22,2,22,6]],"flags":["formulas_cached_only"]}
["Temperature Derating Factors"]
[]
[null,"FLAT PLATE",{"$nulls":5},"TUBULAR PLATE"]
["Temperature [°C]","AGM",null,null,"Gel",null,null,"AGM",null,null,"Gel"]
[null,"Slow rate","Med rate","High rate","Slow rate","Med rate","High rate","Slow rate","Med rate","High rate","Slow rate","Med rate","High rate"]
[null,"10-12 h",{"$nulls":5},"10-12 h"]
[-5]
[0]
[5]
[10]
[15]
[20]
[25]
[30]
[35]
[40]
[45]
[]
["Note: The discharge rate time period (e.g. 10 - 12 hrs for slow rate) shall be indicate in the space provided"]
["Company Name"]
["Representative  Name"]
["Date"]
["Signature"]

{"sheet":"Customer Details","index":13,"n_rows":33,"n_cols":7,"rows_kept":33,"merged":[[0,1,0,6]],"flags":["formulas_cached_only"]}
[null,"CUSTOMER DETAILS - Contactable References"]
[]
[null,"Company Name","Contact Person","Country","Email","Telephone","Mobile"]
[1]
[2]
[3]
[4]
[5]
[6]
[7]
[8]
[9]
[10]
[11]
[12]
[13]
[14]
[15]
[16]
[17]
[18]
[19]
[20]
[21]
[22]
[23]
[24]
[25]
[26]
[27]
[28]
[29]
[30]

{"sheet":"Deviation Schedule","index":14,"n_rows":58,"n_cols":3,"rows_kept":58,"merged":[[0,0,0,2],[53,0,53,2],[54,0,54,1],[55,0,55,1],[56,0,56,1],[57,0,57,1]],"flags":["formulas_cached_only"]}
["Any deviations from this specification shall be listed below with reasons for deviation.  In addition, evidence shall be provided that the proposed deviation will at least be more cost effective than that specified by Eskom."]
[]
["Item","Clause","Proposed Deviation"]
{"$rows_empty":50}
["I confirm that the deviations submitted in this excel sheet are the only deviations for the proposed system to Eskom "]
["Company Name"]
["Representative  Name"]
["Date"]
["Signature"]

{"sheet":"Lists","index":15,"n_rows":4,"n_cols":6,"rows_kept":4,"hidden":true,"merged":[[0,3,0,5]],"flags":["formulas_cached_only"]}
["Yes_No",null,"Pass_Fail","Score"]
["Yes",3,"Pass","Fully compliant","FC",3]
["No",-4,"Fail","Partially compliant (minor deviation)","PC",1]
[{"$nulls":3},"Non-compliant (major deviation)","NC",-4]