| To whom it may concern | Date | 05 November 2025 |
| --- | --- | --- |
|  | Enquiries | Jeanette Makume |
|  | E-mail address | makumej@eskom.co.za |

Dear Sir/Madam

| Request for Enquiry Number | E1284CTRTD-R |
| --- | --- |
| Description / Project Title | FOR THE DESIGN, SUPPLY, DELIVERY, INSTALLATION AND COMMISSIONING OF A HYBRID WIND AND SOLAR PV MICROGRID RESEARCH FACILITY AT ESKOM RESEARCH, TESTING AND DEVELOPMENT (RT&D) FOR A PERIOD OF THREE (3) YEARS |
| Tender Questions Closing Date | 30 November 2025 |

| Item | Questions | Answers | Clarity Published Dates |
| --- | --- | --- | --- |
|  | Please mark the specific PV panel layout area on the map and provide corresponding size. | Please refer to 1.2 of the technical scope document, on the accessible area that is marked, it has included the solar PV array. |  |
|  | Please provide site pictures as a reference. | Please refer to 1.2 of the technical scope document. |  |
|  | Is there any preliminary geological report to be provided? Are there any previous geological reports available for reference? The bid document mentions a report done in 2013 but it is not part of the bidding documents | Please refer to Geotechnical Investigation Report Uploaded on Tender Bulletin |  |
|  | Is there any preliminary feasibility Study Report to be provided? | There is no preliminary feasibility report from Eskom. The tenderer is expected to provide a preliminary design to demonstrate how they are going to approach this project. |  |
|  | What equipment powers the tracking photovoltaic support structure? Is there any available power supply on site? | The tracking system must be powered by the solar PV, but the net PV output must be no less than 30kWac (after powering auxiliaries and losses). |  |
|  | Could you provide the drawings or other materials of the existing distribution room system? Do you need to connect to the main grid or just use it off-grid? | This is a new project – no existing distribution system. The microgrid is powered from both wind and solar, with BESS to ensure continuous supply. The control room will be powered from the 230V mains supply. |  |
|  | Can the cables be laid underground on-site? Can the existing underground system drawings be provided? | Yes. And the cable route is shown in the .kmz maps. There are no underground services in the area. |  |
|  | Does the client require FAT before shipment of goods and products? | NO. |  |
|  | What is the applicable trade method for this project? CIF, FOB, CIP... | Please refer to Z13 clauses of the NEC (Insurance Cover 84) |  |
|  | 10.1. The payment terms in the contract are insufficiently clear. Please clarify the specific payment schedules for each stage, including advance payment, supply, delivery, installation, and commissioning. 10.2. Please clarify whether the client accepts payment in US dollars." | The payment terms will comply with the NEC ECC. When the activity is completed, the assessment will be done and payment will be made. Clause 50 of the NEC data book deals with Payment. |  |
|  | Please clarify whether the client accepts tender quotations denominated in US dollars. Is there a stipulated reference exchange rate? | Please refer to Secondary clause X3 and also read Instructions specified in the exchange rate tab on the Typical Activity Schedule spreadsheet |  |
|  | Is CIDB registration mandatory for the bidder or the sub contractor registration will be valid for evaluation and qualification? | Please refer to the Invitation to Tender Document CIDB requirements are stated in this document |  |