PART C2:

PRICING DATA

TABLE OF CONTENTS

C2	PRICING DATA	C2 - 2

C2.1	PRICING ASSUMPTIONS / INSTRUCTIONS	C2 - 2

C2.1.1	Bill 1 - Civils	C2 - 2

C2.1.2	Bill 2 - Building	C2 - 5

C2.1.3	Bill 3 - Mechanical	C2 - 53

C2.1.4	Bill 4 - Electrical	C2 - 56

C2.1.5	Bill 5 – Control and Instrumentation	C2 - 61

C2.2	BILL OF QUANTITIES	C2 - 64

C2.2.1	PACKAGE A	C2 - 64

C2.2.2	PACKAGE B	C2 - 360

PRICING DATA

PRICING ASSUMPTIONS / INSTRUCTIONS

Bill 1 - Civils

General

The Bill of Quantities forms part of the Contract Documents and must be read and priced in conjunction with all the other documents comprising the Contract Documents (refer to F.1.2 of the Tender Data).

Pricing Instructions and Description of Items in the Schedule

Measurement and payment shall be in accordance with the relevant provisions of Clause 8 of each of the Standard Engineering Specifications referred to in the Scope of Work.  The Preliminary and General items shall be measured in accordance with the provisions of C2.1.8.

The descriptions of the items in the Bill of Quantities are for identification purposes only and comply generally with those in the Standard Engineering Specification.

Clause 8 of each Standard Engineering Specification, read together with the relevant clauses of the Scope of the works, set out what ancillary or associated work and activities are included in the rates for the operations specified. Should any requirements of the measurement and payment clause of the applicable Standard Engineering Specification, or the Scope of the works, conflict with the Bill of Quantities, the requirements of the Standard Engineering Specification or Scope of the work, as applicable, shall prevail.

Quantities Reflected in the Schedule

The quantities given in the Bill of Quantities are estimates only, and subject to re-measuring during the execution of the work. The Contractor shall obtain the Engineer’s detailed instructions for all work before ordering any materials or executing work or making arrangements for it.

The Works as finally completed in accordance with the Contract shall be measured and paid for as specified in the Bill of Quantities and in accordance with the General and Special Conditions of Contract, the Specifications and Project Specifications and the Drawings. Unless otherwise stated, items are measured net in accordance with the Drawings, and no allowance has been made for waste.

The validity of the contract will in no way be affected by differences between the quantities in the Bill of Quantities and the quantities finally certified for payment.

Monthly Payments

Unless otherwise specified in the Specifications and Project Specifications, progress payments in Interim Certificates, referred to in Clause 14.3 and 14.6 of the  Conditions of Contract, in respect of "sum" items in the Bill of Quantities shall be by means of interim progress instalments assessed by the Engineer and based on the measure in which the work actually carried out relates to the extent of the work to be done by the Contractor.

Provisional Sums / Prime Cost Sums

Where Provisional Sums or Prime Cost sums (PC Sum) are provided for items in the Bill of Quantities, payment for the work done under such items will be made in accordance with Clause 13.4 of the Conditions of Contract. The Employer reserves the right, during the execution of the works, to adjust the stated amounts upwards or downwards according to the work actually done under the item, or the item may be omitted altogether, without affecting the validity of the Contract.

The Tenderer shall not under any circumstances whatsoever delete or amend any of the sums inserted in the "Amount" column of the Bill of Quantities and in the Summary of the Bill of Quantities unless ordered or authorized in writing by the Employer before closure of tenders.  Any unauthorized changes made by the Tenderer to provisional items in the schedule, or to the provisional percentages and sums in the Summary of the Bill of Quantities, will be treated as arithmetical errors.

Pricing of the Bill of Quantities

The prices and rates to be inserted by the Tenderer in the Bill of Quantities shall be the full inclusive prices to be paid by the Employer for the work described under the several items, and shall include full compensation for all costs and expenses that may be required in and for the completion and maintenance during the defects liability period of all the work described and as shown on the drawings as well as all overheads, profits, incidentals and the cost of all general risks, liabilities and obligations set forth or implied in the documents on which the Tender is based.

Each item shall be priced and extended to the "Total" column by the Tenderer, with the exception of the items for which only rates are required (Rate Only), or items which already have Prime Cost or Provisional Sums affixed thereto.  If the Contractor omits to price any items in the Bill of Quantities, then these items will be considered to have a nil rate or price.

All items for which terminology such as "inclusive" or "not applicable" have been added by the Tenderer will be regarded as having a nil rate which shall be valid irrespective of any change in quantities during the execution of the Contract.

All rates and amounts quoted in the Bill of Quantities shall be in Rands and Cents and shall include all levies and taxes (other than VAT). VAT will be added in the Summary of the Bill of Quantities.

“Rate Only” Items

The Tenderer shall fill in rates for all items where the words "Rate Only" appear in the "Total" column. "Rate Only" items have been included where:

an alternative item or material is contemplated;

variations of specified components in the make-up of a pay item may be expected; and

no work under the item is foreseen at tender stage but the possibility that such work may be required is not excluded.

For “Rate Only” items no quantities are given in the "Quantity" column but the quoted rate shall apply in the event of work under this item being required. The Tenderer shall however note that in terms of the Tender Data the Tenderer may be asked to reconsider any such rates which the Employer may regard as unbalanced.

Preliminary and General

The following clause is applicable to all Preliminary & General items across all bills of quantities 
(Bill 1, 2 3 &4).

The Preliminary and General Section is provided to cover the Contractor’s expenses incurred in complying with the requirements of the tender documents and consists of the following parts:

- Part AA: Preliminaries

- Part AB: General Specifications

- Part AH: Occupational Health and Safety

Fixed Charge Items: Each item should be priced separately and, subject to the Engineer certifying in terms of Clause 14 of the General Conditions of Contract as well as the PSA Section of the Particular Specification that the work has been done, payment will be made as follows:

(i)	the total amount due when the certified value fixed charge items in this section is less than 5 	% of the net contract price;

(ii)	when the certified value of fixed charge items in this section is greater than 5 % of the net 	contract price, payment will be limited to 5 % of the net contract price. The remainder will be 	paid when the value of the work done under the contract, excluding the value of fixed charge 	items in this section, is greater than 50% of the net contract price, excluding the value of fixed 	charge items in this section.

Time Related Items: Any Time Related items not priced shall be deemed to be covered by the prices of other items in the section.

Payment of Time Related items in this section will be made throughout the contract period, the amount per month being the value of the item divided by the completion in months or, if specified in weeks, the equivalent number of months, in terms of Clause 8 of the General Conditions of Contract. The final monthly increment will only be paid upon the issue of a completion certificate.

Package A and Package B

Both Package A and Package B of the Bill of Quantities shall be priced in its entirety. Package A is for the full scope of works, whereas Package B is a reduced scope, both of which are defined in the Scope of Work. Depending on the available budget, the Employer may choose to award the contract on the basis of the full scope of works (Package A) or the reduced scope of works (Package B). Thus, each package should be priced independently and the rates tendered in Package A and Package B shall be applicable for that particular package and shall cover all costs (including overheads and Preliminary and General items) for the full scope of works or reduced scope of works respectively. If the employer awards the contract on the basis of the Package B (Reduced Scope), no claim will be entertained for additional costs as it is deemed that the rates tendered for Package B are suitable for that particular scope of works.

Bill 2 - Building

Additional notes in the use of these Model Preambles.

- Concrete, Formwork and Reinforcement

The Project Specification embodied in these preambles was compiled in collaboration with the Authors of SANS 1200G, which forms the basis for the Concrete, Formwork and Reinforcement model preambles.

Users of these preambles are advised to submit a copy of the Model Preambles to the Engineers involved in a project for their scrutiny. Any amplifications, amendments, etc required by individual Engineers would then be incorporated in the Supplementary Preambles referred to in item 1.3.

- Roof Coverings

The roof coverings included in these Model Preambles are limited in their content and therefore any roofing material not included in these Preambles will need to have its full preamble included in the Supplementary Preambles.

- Structural Steelwork

The comments made under item 3.1 apply equally to Structural Steelwork.

Note that the protective treatment of the structural steel covers only the treatment up to and including the primer (and patching after erection). The finishing coats of paint must be fully described and included either in the “Structural Steelwork” or in the “Paintwork” trade, as the practitioner wishes.

      - A – General

- Application Of Clauses

These Model Preambles for Trades, and any Supplementary Preambles, shall be read in conjunction with and shall form part of the descriptions of items in the bills of quantities.

Where descriptions or Supplementary Preambles in the bills of quantities differ from these Model Preambles for Trades, the descriptions or Supplementary Preambles in the bills of quantities shall take precedence. Where supplementary preambles differ from descriptions in the bills of quantities, the descriptions in the bills of quantities shall take precedence.

Except where otherwise stated, all preambles contained in any individual Trade Preamble shall apply equally to any work of a similar nature in all other trades.

- Abbreviations

The following abbreviations shall apply:

AASHTO	–	American Association of State Highway and Transportation Officials

AISI		–	American Institute of Steel Industries

BS		–	British Standard

CKS		–	Coordinating Specifications issued by the Central Coordinating Committee 	under the auspices of the South African Bureau of Standards

CSIR		–	Council for Scientific and Industrial Research

SANS		–	South African National Standards and the number following shall refer to the 			relevant specification or code of practice as the case may be

- Materials And Workmanship

Materials and workmanship shall be the best of their respective kinds. Only new and undamaged materials shall be used in the Works. Materials to be permanently installed into the works shall not be used for any temporary purposes on site. Work shall be to the approval of the Principal Agent and shall be executed in accordance with the relevant manufacturer’s written recommendations and instructions where applicable.

- Proprietary Products

For the purposes of submission of tenders, rates for items described in the bills of quantities by trade names, catalogue references, etc shall be for the particular type and manufacture specified.

The approval of the Principal Agent shall be obtained prior to any substitution and where products or materials etc other than those specified are used, adjustments in the rates will be made if necessary.

- Assembling

Rates for manufactured items shall include assembling complete and handing over in proper working order.

- References In Descriptions

Any references given in brackets at the end of certain descriptions shall refer to the relevant references on the drawings or schedules.

- Water

Water shall be clean and free from injurious amounts of acids, alkalis, organic matter and other substances and shall be suitable for its intended use.

- Application Of The National Building Regulations

All work shall be executed in accordance with the requirements of SANS 10400.

- Accuracy In Buildings

The dimensional and positional accuracy of the buildings and their component parts shall comply with Grade II requirements of SANS 10155 unless otherwise stated.

- References To Other Documents

References in these “Model Preambles for Trades” to other documents, including SANS, CKS and BS, shall pertain to the latest edition thereof including all amendments thereto at the date for submission of the tender.

      - B – Alterations

- Alterations

In taking down and removing existing work the utmost care shall be observed to prevent any structural or other damage to remaining portions of the building. The Contractor shall ensure the stability of all structures during alteration work.

Special care shall be exercised during the progress of the work to ensure that any electrical installations, water supply pipes, telephone and other services which may be encountered are not interfered with and notice shall be given to the Principal Agent if any disconnection or alterations become necessary. The Contractor shall take all precautions necessary to prevent any nuisance from dust whilst carrying out the work.

- Materials from the Alterations, Credit, etc

Materials recovered from the alterations (except where described as to be re-used or to be handed over to the Employer) will become the property of the Contractor, who may allow credit in respect thereof where provided for in the bills of quantities. Such materials shall not be re-used in new work without written permission from the Principal Agent.

Materials described as “removed” shall be removed from the site immediately.

Materials described as “handed over to the Employer” shall be carefully dismantled where necessary, neatly stored under cover on the site where directed and protected from damage, until required.

Materials described as “set aside for re-use” shall be carefully dismantled where necessary, cleaned, neatly stored under cover and protected from damage until required for re-use. Any damage caused to such materials during removal, storage or refixing shall be made good at the Contractor’s expense.

- Disposal of Debris etc

The Contractor shall be responsible for the removal from the site of all materials, debris and rubbish resulting from the alterations.

- Making Good Damaged Work

The Contractor shall make good in all trades to existing work where damaged or disturbed through the alterations with all necessary new materials to match the existing.

- Forming New Openings Or Altering Openings In Existing Walls

Where new openings are formed or openings altered in existing walls, the wall above the opening shall be broken out and a new brick, in situ concrete or prestressed concrete lintel inserted, complete with all necessary reinforcement, formwork, turning piece, etc, the jambs and portions of openings as described shall be built up with new brickwork or blockwork properly toothed and bonded to existing, cavities of hollow walls shall be closed where necessary and finishes shall be made good all round and into reveals.

- Building Up Openings

Where existing openings are given in number as built up, the existing surfaces all round shall be prepared as necessary, brickwork or blockwork properly toothed and bonded to existing, wedged up to underside of existing lintel and finishes shall be made good on both sides.

      - C – Earthworks

- Demolitions

- Nature and extent

Descriptions of demolitions give a rough guide only as to the scope of the work. Tenderers are therefore advised to visit the site before submitting a tender and to acquaint themselves with the nature and extent of the work to be done and the value of recoverable materials which are not to be re-used or handed over to the Employer. Unless otherwise stated, loose furniture, kitchen and other equipment, apparatus, machinery, etc shall remain the property of the Employer and the removal thereof does not fall within the scope of this Contract

The Contractor shall completely demolish the buildings etc in a careful, skilful, practical and safe manner down to 150mm below ground level

Demolitions shall include breaking up and removing:

      - all floors and surface beds;

      - all external screen walls, steps, ramps, aprons, surface water channels, rainwater sumps, gulleys, etc attached to the building to be demolished;

      - all services, manholes, etc in ground to a point not less than 1m beyond the perimeter of the building including plugging off ends of all remaining pipes, drains, etc, filling in holes where necessary and ramming and levelling to ground level.

Where only a portion of a building is to be demolished, it shall be done without damage to the remaining portion of the building. Any such damage shall be made good by the Contractor at his own expense.

- Notices etc

The Contractor shall, before commencing work, obtain all necessary authorisation for carrying out the work, by whatever means including the use of pneumatic equipment or blasting, give all necessary notices and pay all charges and fees in connection therewith. He shall also comply with all regulations pertaining to rodent extermination and he shall obtain the requisite Rodent Extermination Clearance Certificate and pay all necessary fees. All receipts and certificates shall be left in the safekeeping of the Principal Agent. All the abovementioned charges and fees shall be paid by the Contractor and included in his prices.

The Contractor shall give ample notice to the Principal Agent and Local Authorities regarding any disconnections necessary prior to the removal or interruption of electrical or telephone cables, water and sanitary services etc.

- Loss

After the handing over of the site to the Contractor, the full risk of any loss or damage to buildings to be demolished shall be the responsibility of the Contractor and he shall take such precautions as he deems necessary against such loss or damage.

- C.1.4	Materials from the demolitions, credit, etc

Materials recovered from the demolitions will become the property of the Contractor, who may allow credit in respect thereof where provided for in the bills of quantities. Such materials shall not be reused in any new work without written permission from the Principal Agent.

- C.1.5 Disposal of debris etc

The Contractor shall be responsible for the removal from the site of all materials, rubble, debris and rubbish resulting from the demolitions.

- Soil Insecticides

The application of soil insecticides shall be carried out in accordance with “The application of soil insecticides for the protection of buildings” - SANS 10124.

- Filling etc

- Filling generally

Filling over site shall be spread, levelled, watered and consolidated in layers not exceeding 300mm.

Filling under floors and backfilling to excavations shall be suitable inert material, free from clay, vegetable matter, large stones, etc, having a maximum plasticity index of 10, spread, levelled and compacted to a density of at least 90% Mod. AASHTO

- Hardcore

Hardcore shall be broken stone or other approved hard material graded from 25mm to 75mm with the finer material on top and shall be spread, levelled and consolidated

- Excavations

- Classification of excavated material

“Hard rock” shall mean granite, quartzitic sandstone or other rock of similar hardness, the removal of which requires drilling, wedging and splitting or the use of explosives.

“Soft rock” shall mean hard material the removal of which warrants the use of pneumatic tools and includes hard shale, ferricite, compact ouklip and material of similar hardness.

“Earth” shall mean all ground other than that classified as “hard rock” or “soft rock” and shall include made-up ground and any loose stones or pieces of concrete not exceeding 0,03m in volume.

      - D – Concrete, Framework and Reinforcement

- Specification For Concrete Work Generally

All in situ concrete work (plain and reinforced) shall comply with SANS 1200G supplemented by the following Project Specification. Where SANS 1200G and the Project Specification are in conflict, the Project Specification shall take precedence

Wherever the term “Engineer” appears in SANS 1200G or in the following Project Specification this shall be deemed to mean the Principal Agent’s representative responsible for this section of the Works

# PROJECT SPECIFICATION

The following amplifications, additions and amendments to SANS 1200G shall constitute the Project Specification. Clause numbers refer to either the existing clauses in SANS 1200G or to new clauses, which are related to the existing clauses

- SCOPE

This clause is amended to include:

1.1	This specification does not cover the methods by which the finished structure is to be measured for the purpose of payment and the “Standard System of Measuring Building Work” shall apply

- INTERPRETATIONS

2.1	SUPPORTING SPECIFICATIONS

Clause 2.1(b) shall not apply

2.2	APPLICATION

This clause shall not apply

- PLANT

4.5		FORMWORK

4.5.2	Finish

Unless otherwise stated the quality of all formwork shall be such that the finished

surface of the concrete is “Rough” in terms of clause 5.2.1(a)

- CONSTRUCTON

5.2		FORMWORK

5.2.1	Classification of Finishes

- Rough. No treatment of the surface of the concrete will be required after the striking of the formwork. The finish of the concrete need not be more accurate than Degree of Accuracy III

- Smooth. Imperfections such as small fins, bulges, irregularities, surface honeycombing and surface discolorations shall be made good and repaired by approved methods. The finish of the concrete shall be accurate to Degree of Accuracy II

- Special

- Smooth and fair

This class of finish requires the highest standard of concrete work, formwork, accuracy and technique

Concrete placed in any one structure to give this finish shall be made from cement and aggregates from the same source. The grading of the aggregate shall be kept constant

Formwork shall be metal, wrot timber or other approved material in new condition designed and constructed to suit the particular job in hand and with shutter bolts and joints between panels in a regular pattern approved by the Principal Agent. Joints between panels shall be watertight, but the use of sealing tape which will mark the concrete shall not be permitted

Designated joints shall be in the position and of the details shown upon the working drawings. Should the Contractor wish to incorporate further construction joints or amend the position of those shown to suit his own requirements or technique, this may be allowed provided that all design considerations are met, that the prior approval of the Engineer is obtained and that any extra costs are borne by the Contractor

In the case of horizontal construction joints, the top edge of the concrete on the smooth and fair finished side shall be struck true and level with a trowel

Special care shall be taken to ensure that forms are clean and free of all pieces of tying wire, nails and other debris at the time of concreting

The standard of finish shall be such that upon removal of the formwork, no further treatment, other than treatment of bolt holes if required, shall be found necessary to provide a straight, smooth and uniform finish of good quality and consistent colour and texture, free of all honeycombing etc. Any defect shall be made good by either removing and replacing the defective concrete or, in certain instances only, by patching

5.5 	CONCRETE

5.5.1.6	Prescribed mix concrete

Where prescribed mix concrete is specified the proportions of constituents, the maximum size of coarse aggregate and the estimated minimum compressive strength shall be as specified in the following table:

| Class of Concrete | Estimated minimum compressive strength in MPa at 28 days | Maximum nominal size of coarse aggregate in mm | Proportions of Constituents |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | Cement (Parts) | Fine aggregate (Parts) | Coarse aggregate (Parts) |
| A | 7 | 37,5 | 1 | 4 | 8 |
| B | 15 | 19 | 1 | 3 | 5 |
| C | 20 | 19 | 1 | 2,5 | 3,5 |

Cement shall comply with SANS 50917-1 of strength 32,5N or higher

Should cement and aggregates be mixed by volume, the contents of a 50kg³ sack of cement shall be taken to be 0,033m

Notwithstanding the requirements contained in SANS 1200G, the Principal Agent may permit certain items of non-structural concrete to be mixed by hand

If the concrete is mixed by hand, it shall first be mixed in a dry state on a clean non-absorbent surface until it is of uniform colour and consistency. Just enough water shall then be added to permit mixing and working, at which stage the concrete shall continue to be mixed until it is of uniform colour and consistency

5.5.1.7	Strength concrete

Where strength concrete is specified it shall be designated by its specified strength followed by the size of stone used in its manufacture, eg 30 MPa/19mm

The water/cement ratio shall be as Table 5 of clause 5.5.1.5 for moderate exposure conditions

5.5.1.8	“No-Fines” concrete

“No-fines” concrete shall consist of one part cement to eight parts aggregate graded from minimum 6mm to maximum 13mm size

The quantity of water used shall be just sufficient to form a smooth grout which shall completely coat every particle of aggregate and also to ensure that the grout is just wet enough to form a small fillet at each point of contact between the stones. “No-fines” concrete mixed with excessive water, which results in a thin grout, which drops off the aggregate, will be rejected

“No-fines” concrete shall be placed in its final position within 20 minutes of mixing and shall be placed in continuous horizontal layers. Concrete shall be spade worked sufficiently to ensure that it fills the forms but vibrating, tamping or ramming will not be permitted

5.5.3.2	Ready-mixed concrete

The use of ready-mixed concrete and the acceptability of test results from a central concrete production facility shall be subject to the written approval of the Engineer.

- TOLERANCES

Degree of Accuracy II shall apply for all work unless otherwise stated.

- TESTS

7.1		FACILITIES AND FREQUENCY OF SAMPLING

7.1.2	Frequency of sampling

7.1.2.5 The frequency of sampling shall be as directed by the Engineer, but not less than one set of cubes from every 50m3 cast

- MEASUREMENT AND PAYMENT

This clause shall not apply

- Aggregates of Low Density

Aggregates of low density shall comply with SANS 794

- Hollow Blocks, Prefabricated Block Beams and Planks, etc

Blocks, block beams, planks, etc shall be fixed and supported in such a manner that no movement can take place before or during the casting of concrete. No broken components shall be used

- Supervision

A competent and experienced foreman shall superintend personally the whole of the concrete construction and pay special attention to:

- The quality, testing and mixing of materials,

- The placing and compaction of concrete,

- The construction and removal of formwork and

- The sizes and position of reinforcement

- The Contractor shall obtain the permission of the Principal Agent before commencing concreting of foundations or reinforced structure

No inspection, approval, authorisation to proceed, comment or instructions following from such an inspection, or failure of the Principal Agent to comment on any particular aspect of the work, shall be deemed to relieve the Contractor in any way from his obligation to ensure through his own supervision that the work is constructed in every way in accordance with the Drawings, Specification and Conditions of Contract, nor relieve him from his obligations to make good any fault or defect, nor shall it be deemed that there is any obligation on the Principal Agent to inspect all or any part of the Works or that such inspection is necessarily complete in every respect

- General

Concrete

Rates for concrete work shall include all “construction joints” other than “designated joints” as defined in SANS 1200G clause 2.4.3 which are measured separately, and for the design of strength concrete mixes and all testing of concrete and materials other than compressive strength testing of concrete samples taken from concrete being placed in the Works. The Contractor shall only be entitled to payment for those samples and compressive strength tests called for by the Engineer and which pass the test requirements

Surface beds cast in panels shall be cast in panels approximately 9m²

Formwork

Formwork to slabs and beams shall be cambered where required

Rates for formwork to soffits shall include propping not exceeding 3,5m high unless otherwise described.

Formwork to walls and columns is not exceeding 3,5m high above bearing level unless otherwise described

Reinforcement

Standard welded steel fabric reinforcement shall be as included in Table 1 of SANS 1024 and shall have 300mm wide laps.

The mass of binding wire is not included in the mass of the reinforcement and the cost thereof shall be included in the rates for the reinforcement.

      - E – Precast Concrete

- Materials And Workmanship

Materials and workmanship shall comply with the following standards:

Precast concrete paving slabs								SANS 541

Cement, water, aggregates and reinforcement shall be as described under D. CONCRETE, FORMWORK AND REINFORCEMENT

- Concrete

Concrete shall be as described under D. CONCRETE, FORMWORK AND REINFORCEMENT and unless

otherwise stated shall be prescribed mix concrete Class C but with coarse aggregate of an appropriate size

- Moulds

Before each casting, moulds shall be coated with a suitable release agent which will not in any way discolour the surface of the finished product or impair its strength. Where items are described as “finished smooth from the mould” or as “precast terrazzo”, moulds shall be made to a high degree of accuracy and shall be such as to leave even and smooth surfaces

- Finishes To Blocks

Where described as “precast terrazzo”, such surfaces shall have a facing of terrazzo described under O. PLASTERING. The facing shall be poured into the moulds in a wet state (not dry pressed) and thoroughly worked up against finished faces to ensure that it finishes smooth from the mould

Projections shall be rubbed off and faces shall be of even colour and free from blemishes, cracks and other imperfections. Salient angles shall be arris rounded

- Casting Etc

Items shall be suitably cured, shall not be handled whilst still green and shall not be built in within 21 days of casting

- Reinforcement

Unspecified reinforcement required for manufacturing, handling and erection purposes and for reinforcing projecting and other unwieldy portions of blocks shall be provided by the Contractor at his discretion

- Bedding, Jointing And Pointing

Blocks shall be bedded and jointed solidly in Class I mortar as described under F. MASONRY and shall be pointed with slightly keyed joints

Blocks finished with “precast terrazzo” shall have joints raked out and pointed with slightly keyed joints in tinted waterproofed mortar composed of one part cement and three parts sand to match terrazzo facing

- General

Precast concrete work shall include reinforcement required for manufacturing, handling and erection purposes, steel rod or wire hooks and/or mortices for lewis bolts required for handling and transporting, any necessary temporary propping and strutting and bedding, jointing and pointing

      - F – Masonry

- Materials And Workmanship

Materials and workmanship shall comply with the following standards:

Burnt clay masonry units	SANS 227

Limes for use in building	SANS 523 {Slaked (hydrated) limes}

Aggregates from natural sources –

fine aggregates for plaster and mortar	SANS 1090

Concrete masonry units	SANS 1215

Prestressed concrete lintels	SANS 1504

Burnt clay paving units	SANS 1575

Metal ties for cavity walls	SANS 28

Common cement	SANS 50197-1 (Class 32,5N)

Masonry cement	SANS 50413-1 (Class 22,5X)

Concrete masonry construction	SANS 10145

The structural use of masonry	SANS 10164-1

Masonry walling	SANS 10249

Concrete floors	SANS 10109-1&2

- Sand

Sand shall be washed where necessary and screened through a 2,4mm mesh sieve

- Burnt Clay Bricks

Burnt clay bricks shall be of nominal size 222 x 106 x 73mm unless otherwise stated

Common bricks shall be General Purpose bricks

Extra hard burnt bricks shall be General Purpose (Special) bricks

Facing bricks shall exhibit a liability to efflorescence not in excess of “Slight” and water absorption when tested in conformity with the requirements of SANS 227 shall not exceed 14%

Particular care shall be taken to preserve arrisses and faces of facing and paving bricks during transit and handling

- Concrete Bricks

Concrete bricks shall have a nominal compressive strength of 8 MPa

- Quarry Tiles etc

Quarry, cement and similar tiles shall be of approved manufacture, even in shape and size, free from cracks, twists or blemishes and uniform in colour

- Wire Ties

Wire ties shall be of galvanized steel of the single wire type for solid walls and either the “Butterfly” or Modified PWD type for hollow walls. Ties shall be of sufficient length to allow not less than 75mm of each end to be built into brickwork or embedded in concrete

- Brickwork Reinforcement

Brickwork reinforcement shall be manufactured from hard drawn steel wire conforming to BS 785 and shall consist of two 2,8mm diameter main wires with 2,5mm diameter cross wires at 300mm centres welded at intersections

Brickwork reinforcement shall be lapped not less than 300mm at end joints and for a length equal to the width of the widest reinforcement at intersections

- Mortar

Mortar shall comply with the following table:

| 1 | 2 | 3 | 4 |
| --- | --- | --- | --- |
| Mortar Class | Minimum compresive strength MPa | Cement:sand (common cement) | Cement:sand (masonry cement) |
| I | 10 | 1:4 or 50kg to 130 litres | 1:3 or 50kg to 100 litres |
| II | 5 | 1:6 or 50kg to 200 litres | 1:5 or 50kg to 170 litres |
| III | 1,5 | 1:9 or 50kg to 300 litres | 1:6 or 50kg to 200 litres |

Mortar shall be Class II unless otherwise specified

Mortar plasticizers may only be used with the approval of the Principal Agent

The materials shall be mixed dry until of uniform colour, water added and the mixture turned over until the ingredients are thoroughly incorporated

Mortar shall be produced in such quantities as can be used before commencement of set and no mortar that has set shall be used

- Compo Mortar

Compo mortar shall be Class III mortar in accordance with clause F.8 but with a lime content of 80 litres

The lime and sand shall be mixed dry until of uniform colour, water added and the mixture turned over until the ingredients are thoroughly incorporated. Immediately before use, the cement shall be mixed in and the requisite amount of water added. Compo mortar shall be produced in such quantities as can be used before commencement of set and no compo mortar that has set shall be used

- Brickwork

Wherever practicable, brickwork shall be built in stretcher bond. Unless legitimately required to form bond, no false headers shall be used. English bond shall only be used where specifically so indicated or where stretcher bond is not practicable

Brickwork, unless otherwise described, shall be built in Class II mortar

Bricks shall be laid on a solid bed of mortar and all joints shall be grouted up solid

The brickwork shall be carried up in a uniform manner, no part being raised more than 1,2m above adjoining work

Where necessary, bricks shall be wetted before being laid and the course of bricks last laid shall be well wetted before laying a fresh course upon it

Walls in thicknesses of more than one skin shall have at least five wire ties per square metre. Linings to concrete, unless otherwise specified, shall be tied to the concrete with at least five wire ties per square metre

Hollow walls, unless otherwise specified, shall be built of two half brick skins with cavity between, tied together with at least five wire ties per square metre. The cavities shall be kept free of all rubbish, mortar droppings and projecting mortar. Mortar joints to brickwork shall be not less than 8mm or more than 12mm thick

- Blockwork

Unless otherwise described, all blockwork shall be built in stretcher bond. Whole blocks shall be used except where bats or closers are required to form bond. Blockwork, unless otherwise described, shall be built in Class II mortar

Solid blocks shall be laid on a solid bed of mortar and all joints shall be grouted up solid

Hollow blocks shall be laid in shell bedding, ie only the inner and outer shells of the blocks shall be covered with mortar. Vertical joints shall be similarly formed

The blockwork shall be carried up in a uniform manner, no part being raised more than 1,2m above adjoining work

Clay blocks shall be wetted before being laid and the course of blocks last laid shall be well wetted before laying a fresh course upon it

- Centres and Turning Pieces

Centres and turning pieces to soffits of arches and lintels shall be left in position for not less than 14 days

- Face Brickwork

Face brickwork shall be built in stretcher bond, unless otherwise specified, to a true and fair face. Perpends shall be vertically aligned

Facing bricks shall be mixed to ensure that the proper blending of bricks within the colour range of each facing brick being used is obtained

- Pavings, Sills, Copings, Etc

Clay bricks and tiles shall be wetted before fixing and shall be solidly bedded and jointed in Class I mortar and pointed with slightly keyed joints

      - G – Waterproofing

- Materials And Workmanship

Materials and workmanship shall comply with the following standards:

Bituminous damp-proof courses	SANS 248 (Type FV)

Polyolefin film for damp- and waterproofing in buildings (walls, sills, etc)	SANS 952 (Type B)

Polyolefin film for damp- and waterproofing in buildings (floors and

basements)	SANS 952 (Type C)

Mastic asphalt for roofing	SANS 297

Mastic asphalt for damp-proof courses and tanking	SANS 298

Bituminous roofing felt	SANS 92 (Type 60)

Polyolefin film for damp- and waterproofing in buildings (flat roofs)	SANS 952 (Type A)

Chloroprene rubber sheet (for waterproofing)	SANS 580

Sealing compounds for the building industry,  two-component,

polysulphide base	SANS110 (Type 2 - Gun Grade)

Sealing compounds for the building and construction

industry, two- component, polyurethane base	SANS 1077

The waterproofing of buildings (including damp-

proofing and vapour barrier installation)	SANS 10021

- Waterproofing to Roofs, Basements, etc

Waterproofing to roofs, basements, etc shall be carried out by workmen who are experienced in this type of work

- Damp-Proof Course to Walls

All joints in damp-proof course to walls shall be lapped a minimum of 150mm except at junctions and corners where the lap shall equal the full thickness of the wall

      - H – Roof Coverings etc

- Materials And Workmanship

Materials and workmanship shall comply with the following standards:

Concrete roofing tiles	SANS 542

Clay roofing tiles	SANS 632

Sawn softwood timber battens	SANS 1783-4

Fibre-cement sheets (flat and profiled)	SANS 685

Aluminium alloy corrugated and troughed sheets	SANS 903

Continuous hot-dip zinc-coated carbon steel sheet

of commercial, lock-forming and drawing qualities	SANS 3575

Continuous hot-dip zinc-coated carbon steel sheet of structural quality	SANS 4998

Polyolefin film for damp- and waterproofing in buildings	SANS 952

Metal roofing tiles	SANS 1022

Glass-reinforced polyester (GRP) laminated sheets (profiled or flat)	SANS 1150

Fasteners for roof and wall coverings in the form of sheeting	SANS 1273

Materials for thermal insulation of buildings	SANS 1381-1&4

Expanded polystyrene thermal insulation boards	SANS 1508

Fixing of concrete interlocking roofing tiles	SANS 10062

Roof and side cladding	SANS 10237

Sheet zinc	BS 849

Sheet lead	BS 1178

Sheet aluminium	BS 1470

Sheet copper	BS 2870

- Galvanized Steel Profiled Sheets Etc

Galvanized steel profiled sheets, ridge and hip coverings, etc shall be coated with a minimum of 275 g zinc per m2 and shall be free of white rust

- Galvanized Sheet Iron

Galvanized sheet iron shall be rolled steel sheet coated on both sides with a minimum of 275 g of zinc per m2 and shall be free from white rust

- Nailing And Screwing

Where nailing and screwing is required:

- Laps galvanized iron nails and screws shall be used for galvanized sheet iron and sheet zinc

- copper or copper alloy nails and screws for sheet copper and sheet lead

- aluminium alloy or stainless steel nails and screws for sheet aluminium

- Laps

Sheet metal flashings shall have minimum 100mm laps and linings to valleys, secret gutters, etc minimum 225mm laps

- General

Rates for profiled sheet roofing and rolled edges, ridge and hip coverings, flashing pieces, etc of metal, fibre-cement, plastic, etc shall include fixing accessories

      - I – Carpentry and Joinery

- Materials and Workmanship

Materials and workmanship shall comply with the following standards:

Sawn softwood timber : General requirements	SANS 1783-1

Sawn softwood timber : Stress-graded structural

timber and timber for frame wall construction	SANS 1783-2

Sawn softwood timber : Brandering and battens	SANS 1783-4

Softwood flooring boards	SANS 629

Hardwood furniture timber	SANS 1099

Hardwood block and strip flooring	SANS 281

Wooden ceiling and panelling boards	SANS 1039

Laminated timber (glulam)	SANS 1460

Gypsum plasterboard	SANS 266

Fibreboard products	SANS 540

Wood-wool panels (cement bonded)	SANS 637

Fibre-cement sheets (flat and profiled)	SANS 685

Fibre-cement boards	SANS 803

Plywood and composite board	SANS 929

Wooden ceiling and panelling boards	SANS 1039

Particle boards	SANS 50312-1to7

Decorative laminates	SANS 4586

Wooden doors	SANS 545

Fire doors	SANS 1253

Materials for thermal insulation of buildings	SANS 1381-1,2,4&6

Expanded polystyrene thermal insulation boards	SANS 1508

Mild steel nails	SANS 820

Metal screws for wood	SANS 1171

Wood-preserving creosote	SANS 539

Softwood shall bear the relevant SABS mark and shall be ordered in the sizes in which it will be used as no scantlings of marked timber will be allowed. Should SABS marked timber be unavailable, the Principal Agent’s prior permission shall be obtained before using unmarked timber

- Hardwoods

All hardwoods shall be specially selected, well seasoned, free from sapwood and well kiln dried. Meranti shall be Red or Medium Brown Meranti, even in grain and colour, selected from “Standard and Better” quality from Malaysia

- Infection And Pre-Treatment Of Timber

All timber used on the site, whether for permanent or temporary work, shall be free of borer or other beetle and termite infection. If the work under this contract falls within an area designated under Government Notice R2577 of 197812-29, permanent softwood fixed in the building shall be treated against borer etc in accordance with Government Notice R451 of 1969-03-28 using Class B or C preservative

When treated timbers are cut, the cut surfaces shall be effectively brushed with at least two coats of preservative solution

- Construction In General

Where applicable, construction methods shall comply with SANS 10082. Wood and laminate flooring shall be installed in accordance with SANS 10043. Roof trusses shall be manufactured, erected and braced in accordance with SANS 10243

- Structural Timber

Timbers generally shall be in single lengths and jointing of timbers will only be permitted when the required length is unobtainable. Only the absolute minimum of joints to obtain a particular length will be permitted and such joints are to be evenly spaced along the length of the timber

Finger-jointing of structural timber will be permitted, in which case it shall be manufactured in accordance with SANS 10096

- Plate Nailed Timber Roof Trusses

Plate nailed timber roof trusses shall be of approved design and manufacture and constructed with softwood structural timber by a truss Fabricator holding a current Certificate of Competence awarded by the Institute of Timber Construction

Each roof truss shall have all its members accurately cut and closely butted together and rigidly fixed by CSIR approved patented galvanized metal spiked connectors, precision pressed on both sides of each intersection by an approved method, all in accordance with the manufacturer’s instructions

The design, manufacture and transportation of the roof trusses, bracing, etc shall be under the control of a registered Structural Engineer in accordance with SANS 1900, SANS 10160 and SANS 10163, who shall, after erection, provide a certificate confirming that the design, manufacture, transportation, erection and bracing has been carried out in accordance with this specification

The design shall include for all live loads, wind loads and for dead loads imposed by roof covering, purlins, ceilings, etc

Fully detailed shop drawings of all trusses etc, indicating sizes, bracing, loading, etc, shall be submitted to the Principal Agent for approval prior to fabrication

Unless specific erection instructions are given, erection shall be carried out in accordance with the procedures and recommendations of the manual “The Erection and Bracing of Timber Roof Trusses” published by the Institute for Timber Construction and the Council for Scientific and Industrial Research or as detailed by the designer

Roof trusses and bracing shall include design and preparation of shop drawings

- Tongued And Grooved Boarding

Tongued and grooved boards for floors, panelling, etc shall be in long varying lengths with joints tightly cramped up and secret nailed. Flooring boarding shall be flush jointed with staggered heading joints and machine sanded after fixing

- Joinery

Skirtings, cornices, rails, etc shall be in single lengths wherever practicable and shall have splayed heading joints where necessary. Skirtings shall be trenched at back

All horns of door frames shall be checked and splayed back where frames are fixed projecting or flush with surface and built in

Heads of screws in exposed faces of hardwood joinery shall be sunk and match pelleted Joinery shall have arris rounded angles and shall be blocked and planted on

- Veneers

All face veneers shall be of kiln dried timber, free from knots, cracks, patchwork, sapwood and other defects, selected and glued, dried and machine-sanded to a smooth finish. All veneers shall be applied under hydraulic pressure

- Doors

Flush doors shall have solid timber edge strips with concealed edges. Where doors are to be finished with a transparent finish, the veneer and the edge strips shall be timber of the same species and as far as possible of matching colour. Unless otherwise described all flush doors shall be of interior quality, but where exterior quality doors are specified the glue used shall be of the WBP type

Framed and ledged batten doors described as filled in with V-jointed boarding shall be filled in flush on one side with tongued and grooved vertical boarding, V-jointed on one or both sides and of the thickness stated. The boarding shall be in narrow widths, closely cramped up, rebated or tongued on outer edges and housed to grooves in stiles and rails and twice countersunk brass screwed at each intersection with ledges and braces and the inner edges of the abutting stiles and rails shall be chamfered to form a V-joint at junction with the board. Unless otherwise described double doors shall have rebated meeting stiles

- Fixing

All nails and screws shall be of the size, length and type appropriate to their respective uses. All screws for hardwood joinery work shall be brass

Items described as “plugged” shall be screwed to fibre, plastic or metal plugs at not exceeding 600mm centres. Where items are described as “bolted”, the bolts have been given separately

- Adhesives

Adhesives shall comply with BS 1204 and 4071 where applicable. Adhesives used in the manufacture of external joinery exposed to excessive moisture (eg kitchen and laboratory worktops) shall be of the WBP type.

      - J – Ceilings, Partitions and Access Flooring

- Materials And Workmanship

Materials and workmanship shall comply with the following standards:

Gypsum plasterboard	SANS 266

Fibreboard products	SANS 540

Gypsum cove cornice	SANS 622

Wood-wool panels (cement-bonded)	SANS 637

Sawn softwood timber : Brandering and battens	SANS 1783-4

Sawn softwood timber : Timber for frame wall Construction	SANS 1783-2

Fibre-cement boards	SANS 803

Plywood and composite board	SANS 929

Wooden ceiling and panelling boards	SANS 1039

Materials for thermal insulation of buildings	SANS 1381-1&4

Expanded polystyrene thermal insulation boards	SANS 1508

Raised access flooring	SANS 1549

- Tongued And Grooved Boarding

Tongued and grooved boarding for ceilings shall be in long varying lengths, V-jointed one side and with joints tightly cramped up and secret nailed

- Ceilings Etc

- J.3.1	Brandering

Brandering for ceilings and eaves soffit coverings shall be symmetrically arranged with necessary smaller panels. Main branders shall be at right angles to roof timbers, with cross branders cut in between and branders shall be fixed with galvanized wire nails driven in on skew alternately in opposite directions

- J.3.2	Ceiling boards

Ceiling boards shall be in long lengths symmetrically arranged with necessary smaller panels, closely butted and secured at 150mm centres to brandering with galvanized or cadmium-plated clout-headed nails

- Gypsum Skim Plaster

Gypsum skim plaster shall be pure gypsum plaster finished with a steel trowel

- Exposed Tee-System Suspended Ceilings

The ceiling panels shall be as described in the items and the panels shall be stiffened at back as recommended by the manufacturer to prevent bowing or sagging

The exposed surfaces of all ceiling panels and supporting members shall be uniform in colour and free from surface blemishes

The suspension grid system shall be an approved patent suspension system comprising 38mm galvanized steel main and cross tee bearers spaced in both directions at centres to suit sizes of ceiling panels used, with the cross bearers fitted between and notched to form flush fit with main bearers. The exposed flange of the tees shall be 25mm wide, covered with a rolled aluminium cap painted a low sheen satin white. Cornices etc shall be as described in the items and shall be finished to match the exposed tees

The main tee bearers shall have holes for cross tees at 300mm centres and holes for hangers at 50mm centres. In addition, main and cross tee bearers shall be holed as necessary for and provided with timber wedges or steel clips where recommended by the manufacturer to prevent ceiling panels from lifting

The web of the exposed cross tee bearers shall extend to form a positive interlock with the main tee bearers and the lower flange shall be cut back to provide a joint free appearance

All hangers shall be galvanized and shall be at centres to meet the requirements of the specification with one end fixed to the suspension grid main bearers and the other end fitted with suitable galvanized fixing cleat securely fixed to the structure. Fixing points shall be agreed to by the Principal Agent before any power shot fixings are made. Hangers shall not be suspended from air-conditioning ducts. Where recommended by the manufacturer, hangers shall be of the rigid type

Component parts and fixings shall be non-corrosive and able to withstand atmospheric pollution. Surfaces of aluminium which are in contact with other materials when fixed, particularly metals, shall be suitably insulated to prevent electrolytic corrosion

Ceilings shall comprise hangers, suspension grid system and ceiling panels, shall be constructed in a manner suitable for carrying air-conditioning diffusers and light fittings in the positions required, shall be set out to layouts approved by the Principal Agent and shall have the standard suspension systems modified as necessary to work around any pipes or light fittings

- Flush Plastered Suspended Ceilings

Gypsum plasterboard panels of the specified thickness generally in 1200mm widths and in long lengths shall be fixed grey side down with self-tapping screws to the suspension system with the joints between boards loosely butt jointed and covered with 50mm wide strips of self-adhesive fibre tape

The plasterboard panels shall be finished with gypsum skim plaster trowelled to a smooth polished surface to the thickness etc recommended by the manufacturer

The suspension system shall be an approved patent concealed suspension system consisting of galvanized mild steel bearers suspended on approved non-rusting metal hangers spaced generally at 1200mm centres or to suit layout of air-conditioning ducts and other services etc above ceiling with one end bolted to the bearer and the other end fitted with a galvanized fixing cleat securely fixed to the structure as required

Fixing points shall be agreed to by the Principal Agent before any power shot fixings are made. Hangers shall not be suspended from air-conditioning ducting

Ceilings shall comprise hangers, suspension system, ceiling panels and plaster finish, shall be constructed in a manner suitable for carrying air-conditioning diffusers and light fittings in the positions required, shall be set out to layouts approved by the Principal Agent and shall have the standard suspension system modified as necessary to work around any pipes or light fittings.

      - K – Floor Coverings, Wall Linings, etc.

- Materials and Workmanship

Materials and workmanship shall comply with the following standards:

Semi-flexible vinyl floor tiles	SANS 581

Resin modified vinyl floor tiles	SANS 586

Flexible vinyl flooring	SANS 786

Hardwood block and strip flooring	SANS 281

Wood mosaic flooring	SANS 978

Textile floor coverings (pile construction)	SANS 1375

Textile floor coverings (needle-punchedconstruction)	SANS 141

Carpet underlays	SANS 1419

The installation of wood and laminate flooring	SANS 10043

The installation of resilient thermoplastic

and similar flexible floor covering materials	SANS 10070

The installation of textile floor coverings	SANS 10186

Sheet linoleum (calendered types), cork, carpet and linoleum tiles	BS 810

Solid rubber flooring	BS 1711

Felt backed linoleum	BS 1863

- Laying of Material

Floor tiles shall be laid with continuous joints in both directions

Patterned floor coverings shall be matched at joints

- General

Floor coverings, wall linings, skirtings, nosings, etc shall include all preparatory work to screeded or plastered surfaces etc, priming coats and adhesives

Floor coverings and wall linings shall be dressed around and into corners. Wood block and wood mosaic

flooring shall be sanded with a sanding machine and sealed with a coat of approved penetrating sealer

Plastic handrails shall have welded and polished butt joints

      - L- Ironmongery

- Materials and Workmanship

Materials and workmanship shall comply with the following standards:

Locks, latches and associated furniture for doors. (Domestic type)	SANS 4

Kitchen cupboards: Built-in and free-standing	SANS 1385

Single action closers	SANS 1510

Padlocks	SANS 1533

Fasteners	SANS 1700

Chalk writing boards for schools	CKS 36

- Keys

Locks shall have the minimum possible number of interchangeable keys. Cylinder locks and locks described as “en suite” shall be clearly marked with consecutive numbers and each key shall be punched with the corresponding number of the relative lock.

- Fixing

Unless otherwise described, ironmongery is to be fixed to wood.

Items described as “plugged” shall be screwed to fibre, plastic or metal plugs.

Screws, bolts, etc for fixing of ironmongery shall be of matching metal and finish, except for aluminium ironmongery or ironmongery fixed to aluminium in which cases stainless steel screws may be used.

All necessary preparation of pressed steel door frames for the fixing of ironmongery to the frames has been included with the pressed steel door frames.

- Kitchen Cupboards

Steel cupboards shall be finished with baked enamel. Tops of floor cupboards shall have laminated plastic covering.

Cupboards shall be fitted with all necessary hinges, handles, catches, etc. Cupboards shall be securely fixed with all necessary screws and fibre, plastic or metal plugs.

Where cupboards are described as a “series”, tops shall be continuous and cupboards shall be bolted or screwed together, including bolts, screws, holes, etc.

      - M – Structural Steelwork

- Specification

All structural steelwork shall comply with SANS 1200H or 1200HA as applicable. Structural fasteners shall comply with SANS 1700

Whenever the term “Engineer” appears in SANS 1200H or 1200HA or in the following Project Specification this shall be deemed to mean the Principal Agent’s representative responsible for this section of the Works

- Project Specification Incorporating Amplifications, Additions and Amendments to SANS 1200H and 1200HA

The following amplifications, additions and amendments to SANS 1200H and SANS 1200HA shall apply and clause numbers refer to either the existing clauses in the relevant SANS or to new clauses which are related to the clauses therein

SANS 1200H

3.1.1	Weldable structural steel

Weldable structural steel shall comply with SANS 1431

5.1.2	Contractor provides shop details

The Contractor shall be responsible for the preparation of all shop detail drawings

5.1.3	Engineer provides shop details

This clause shall not apply

5.3.9	Protective treatment

Structural steelwork shall be cleaned and prepared by wire brushing in accordance with SANS 10064 and all surfaces shall be primed as specified to a minimum dry film thickness of 30 micrometres before leaving the workshop. Upon delivery to the site and again after erection all bared surfaces shall be made good with similar primer

8.	Measurement and payment

This clause shall not apply

SANS 1200HA

5.2.10 Protective treatment

Structural steelwork shall be cleaned and prepared by wire brushing in accordance with SANS 10064 and all surfaces shall be primed as specified to a minimum dry film thickness of 30 micrometres before leaving the workshop. Upon delivery to the site and again after erection all bared surfaces shall be made good with similar primer

5.3.7	Repairs to paint and site painting

This clause shall not apply

8.	Measurement and payment

This clause shall not apply

      - N – Metalwork

- Materials and Workmanship

Materials and workmanship shall comply with the following standards:

Fasteners	SANS 1700

Expanded metal	SANS 190-1&2

Windows and doors made of rolled mild steel sections	SANS 727

Hot-dip galvanized zinc coatings on fabricated iron and steel articles	SANS 121

Strongroom and vault doors	SANS 949

Anodized coatings on aluminium (for architectural applications)	SANS 999

Steel door frames	SANS 1129

Mushroom- and countersunk-head bolts and nuts	SANS 1143

Welding of metalwork	SANS 1044

Adjustable glass-louvred windows	CKS 413

Aluminium sheet and strips	BS 1470

Aluminium extruded tube and hollow sections	BS 1474

Aluminium bars and sections	BS 1476

- Steel

Steel shall be mild steel of approved commercial quality. Steelwork shall be cleaned and prepared by wire brushing in accordance with SANS 10064 and given one coat of primer as specified before leaving the workshop.

- Galvanizing of steel

Steelwork described as “galvanized” shall be galvanized by means of the hot-dip process after fabrication. Where welding on site is unavoidable, such welded joints shall be cleaned down and cold galvanized to approval.

- Stainless Steel

Stainless steel shall be AISI Type 304 stainless steel and shall be buffed to an even satin finish. Stainless steel screws shall be used for fixing stainless steel.

- Aluminium

Aluminium extrusions shall be of 6063-T6 alloy and temper. Aluminium sheet and strips shall be of 1200-H4 alloy and temper.

Joints in all aluminium members shall be formed in an approved manner so that the joints are practically invisible. Screw heads, pins, rivets, etc shall be concealed as far as possible. 300 Series stainless steel screws and bolts shall be used for jointing and fixing aluminium work.

The surfaces of all aluminium which are in contact with other materials when fixed shall be suitably insulated with a non-absorbent insulating material to prevent corrosion. All aluminium work shall be suitably protected against damage, deterioration or discolouration caused by mortar droppings, paint, etc by taping with removable tape, covering with temporary casings or by covering with motor oil.

- Anodizing of aluminium

Aluminium described as “anodized” shall be treated with Grade 25 coating thickness for exterior use or Grade 15 for interior use as specified, to the required finish. All alloys to be anodized shall be suited to anodizing.

- Bolts and Nuts

Nuts shall be of at least the strength grade appropriate to the grade of bolt or other threaded element with which they are used.

- Screwing of Metalwork to Steel, Wood, Concrete, etc

Metalwork described as “screwed” to steel, wood, etc or “plugged” to brickwork, concrete, etc shall be fixed at not exceeding 500mm centres, with necessary holes, countersinking, threading, screws, set screws, self-tapping screws and fibre, plastic or metal plugs.

- Bolting of Metalwork

Where metalwork is described as “bolted” to steel, wood, brickwork, concrete, etc the bolts are measured elsewhere.

- Welding of Metalwork

All welds shall be cleaned and filed or ground off smooth to approval. All welded joints shall be continuous.

- Metalwork Generally

Metalwork shall have all sharp edges ground smooth. Tubular and pipe work shall include running joints. Rails etc described as “continuous” shall be in long lengths with welded joints.

- Pressed Steel Doors, Frames, etc

- N.10.1 Door frames

Frames shall project not less than 20mm into floor finish. Except where described as galvanized, frames shall be primed as specified before leaving the factory. Frames are to jambs and heads of openings. Frames for single doors shall be provided with two 100mm steel butt hinges and an adjustable striking plate for a mortice lock and frames for double doors shall be provided with four 100mm steel butt hinges. Butt hinges shall be steel butts with loose pins, welded to frames. Where necessary mortar caps shall be welded to frames and back plates shall be welded on behind tappings for screws.

- N.10.2 Cupboard door frames

Cupboard door frames shall be as described in N.10.1, but with thresholds of unequal channel section, two 100mm steel butt hinges to hanging stiles, two 75mm steel butt hinges to hanging stiles above transoms, necessary striking plates for mortice locks and keeps for barrel bolts.

- N.10.3 Combination doors and frames

Combination doors and frames shall be manufactured of 1,6mm thick steel plate. Frames shall be as described in N.10.1. Doors shall be standard design and required profile, with a 44mm wide edge all round, vertical reinforcing ribs pressed in and with two reinforcing rails welded on. The door shall be provided with two lever mortice lock with lock box welded to inside. Doors shall be welded to steel butts.

- N.10.4 Transformer room doors and frames

Transformer room doors and frames shall be manufactured of 1,6mm thick steel plate. Frames shall be as described in N.10.1. Doors shall be of standard design with a 44mm wide edge all round, vertical reinforcing ribs pressed in and with three reinforcing rails welded on. Single doors shall be fitted with a padlock cleat and two 100mm brass pintle hinges and double doors shall be fitted with a padlock cleat, two 150mm bolts and four 100mm brass pintle hinges. Each leaf shall be fitted with a louvered ventilation panel of standard design backed with 6mm mesh galvanized wire vermin proof screen.

- N.10.5 Sizes

The frame widths given refer to unfinished wall thicknesses.

- N.10.6 Glazing beads

Where specified, glazing beads shall be 12 x 12mm standard metal glazing beads mitred at angles and countersunk screwed on at not exceeding 300mm centres with self-tapping screws.

- Steel Windows, Doors, etc

- N.11.1 Windows, doors, etc

All fittings to windows, doors, etc shall be chromium plated. Fixed lights and opening sashes shall be in single squares. Windows etc of single unit construction shall have weather bars at transoms above opening sashes.

Composite windows not of single piece construction shall be coupled with standard coupling mullions and transoms that correspond with the window section used.

Kicking plates and panels shall be 1,6mm metal plate fixed with standard metal glazing beads mitred at angles and countersunk screwed on at not exceeding 300mm centres with self-tapping screws.

Except where described as galvanized, windows, doors, burglar bars, etc shall be primed as specified before leaving the factory.

- N.11.2 Burglar bars and flyscreens

Where windows are described as fitted with burglar bars or flyscreens, these shall be standard type fitted over opening sashes.

- N.12 Adjustable Louvre Units

Adjustable louvre units shall be suitable for hand or longarm operation.

Louvre units shall include glass louvres with polished edges and installation, including holes, screws, rivets, preparation of openings, etc.

- Aluminium Windows and Doors

The foregoing preambles “N.4 – ALUMINIUM” shall apply to aluminium windows, doors, etc in all respects in so far as they are applicable. Aluminium windows and doors shall be manufactured from extruded aluminium members of 6063T6, 6261-T6 or 6082-T6 alloy and temper.

Ancillary members such as sills, flashings, infill panels and the like formed from flat sheet material shall be of an appropriate alloy selected from 1200, 3004 or 5251 complying with BS 1470 of a temper suitable for the method of forming and a composition suitable for anodizing or painting as required.

Windows, doors, etc shall be of an approved standard system, manufactured by an approved firm experienced in this type of work, and shall meet with the minimum recommended performance requirements as set out by the Association of Architectural Aluminium Manufacturers of South Africa (AAAMSA) in the latest edition of the Selection Guide.

The fittings for all opening sashes shall be substantial and, unless otherwise described, shall be of high quality aluminium alloy finished to match the windows, doors, etc on which they occur. Samples of all fittings shall be supplied to the Principal Agent for approval.

Top, side and bottom hung opening sashes shall be hung on two aluminium hinges with 300 Series stainless steel pins, nylon bushes and stainless steel washers. Side hung sashes shall have fasteners and sliding stays, top hung sashes shall have peg stays and bottom hung sashes shall have spring catches and concealed arms.

Projected out sashes shall have aluminium fasteners and concealed arms of a non-corrosive material compatible with aluminium.

The frames which are to be built into openings in brickwork shall be fitted with the manufacturer’s standard type fixing lugs, not less than 20 x 3 x 150mm long, screwed to frame and placed one near each corner and intermediately not more than 450mm apart to sides, top and bottom and where fixed to concrete reveals, wood sub-frames or to preformed openings in brickwork shall have countersunk holes for screws, one near each corner and intermediately not more than 450mm apart to sides, top and bottom.

- N.13.1 Glazing beads

Where so described, openings and sashes of windows and doors shall be fitted with approved channel section aluminium glazing beads sufficient in size and profile to suit the method of glazing employed, finished to match the windows, doors, etc and neatly mitred. Screws where necessary shall be of aluminium or 300 Series stainless steel and have pan or raised heads finished to match the beads

- N.13.2 Finishes

Windows, doors, etc described as “anodized” shall be treated with Grade 25 coating thickness. Windows, doors, etc described as “factory painted” shall have an electrostatically applied oven baked polyester paint coating not less than 25 micrometres thick

- N.13.3 General

Aluminium windows, doors, etc shall include glass as described, fixing in position, sealing and protection against damage, deterioration or discolouration by taping with removable tape or covering with temporary casings or motor oil and removing same on completion

- Strongroom And Record Room Doors

Strongroom and record room doors shall not be built in as the work proceeds, but shall be fixed later in the openings provided. The Contractor shall ensure that the lock or other important parts of the door are not tampered with. Should any such tampering occur, the Contractor will be held responsible and at the Principal Agent’s discretion shall provide a new door or lock and keys at his own expense. The keys shall not be delivered together with the doors to the building site. The Contractor shall arrange for the manufacturer to send the keys direct to the Principal Agent per registered post. If these instructions are not complied with, a new lock and keys shall be provided by the Contractor at his own expense.

- Steel Roller Shutters

Roller shutters shall be of approved manufacture comprising curtain, vertical channel guides and top mechanism. The curtain shall be constructed of 1mm thick machine-rolled galvanized interlocking slats with mild steel end locks spot welded to alternate strips. The bottom shall be provided with a galvanized rail riveted on and vertical edges shall slide in galvanized channel guides formed of steel not less than 2,5mm thick bolted to sides of openings.

The mechanism shall be covered in a galvanized sheet iron box. The ungalvanized sections shall be primed as specified before leaving the factory.

      - O – Plastering

- Materials And Workmanship

Materials and workmanship shall comply with the following standards:

Common cement	SANS 50197-1(Class 32,5N)

Masonry cement	SANS 50413-1(Class 225X)

Limes for use in building	SANS 523 {Slaked (hydrated) limes}

Aggregates from natural sources – Fine

aggregates for plaster and mortar	SANS 1090

- Preparatory Work

Surfaces shall be clean and free of oil and thoroughly wetted directly before any plastering or other in situ finishes are commenced. Concrete surfaces shall be slushed with a mixture of one part cement and one part coarse sand or otherwise treated to form a proper key. Preparatory coats shall be thoroughly scored and roughened to form a proper key.

- Finish

All coats of paving and plastering shall be executed in one operation without any blemishes.

- Screeds

Screeds shall be composed of one part cement and four parts sand.

- Cement Render

Cement render shall be composed of one part cement and three parts sand finished with a steel trowel to a smooth polished surface and cured for at least seven days after laying.

Cement render finish shall be divided into panels not exceeding 6m2 with V-joints and deep trowel cuts.

- Granolithic

Granolithic shall be composed of one part cement, one part fine sand, two parts coarse sand and one part granite or other approved stone aggregate that will pass through a 5mm sieve, finished with a steel trowel to a smooth polished surface and cured for at least seven days after laying.

Coloured granolithic shall be carried out in two coats in one operation and shall be tinted to the required colour with approved colouring pigment mixed into the finishing coat. Under no circumstances is the pigment to be sprinkled on and trowelled in after the granolithic is laid.

Granolithic shall be divided into panels not exceeding 6m2 with V-joints and deep trowel cuts.

- Terrazzo

Terrazzo shall be applied in two coats. The undercoat shall be composed of one part cement and three parts sand and shall be finished with a wooden float. The finishing coat shall be composed of one part cement and two parts marble or stone aggregate of a colour and size to obtain the required colour and texture and shall be at least 12mm thick, and applied before the undercoat has dried out. The finishing coat shall be compacted by tamping or rolling until superfluous water has been expelled, finished with a steel trowel and cured for at least seven days after laying. The finished surface shall show at least 80% of the aggregate.

Surfaces described as “polished” shall be polished by machine using various grades of abrasive and grouting with tinted cement as necessary between polishings.

Surfaces described as “polished” shall be polished by machine using various grades of abrasive and grouting with tinted cement as necessary between polishings.

Surfaces described as “brushed” shall be brushed with a steel wire brush on the day the terrazzo has been laid to expose the aggregate as required

Where required, brass or other dividing strips shall be embedded in the undercoat to finish flush with the finished surface.

Three sample blocks, each size 300 x 300mm, as separately measured shall be prepared for approval by the Principal Agent and kept in an accessible place on the site until the completion of the contract.

- Skirtings

Skirtings shall not exceed 25mm thick and shall have a fair edge with arris or rounded external angle at top edge or V-joint to finish flush with plaster and coved or square junction with floor finish.

- Thickness Of Plaster

All plaster, other than skim plaster, shall be not less than 10mm and not more than 20mm thick.

- Cement Plaster

Cement plaster shall comply with the following table:

| 1 | 2 | 3 |
| --- | --- | --- |
| Plaster Class | Cement:sand (common cement) | Cement:sand (masonry cement) |
| I | 1:4 or 50kg to 130 litres | 1:3 or 50kg to 100 litres |
| II | 1:6 or 50kg to 200 litres | 1:5 or 50kg to 170 litres |
| III | 1:9 or 50kg to 300 litres | 1:6 or 50kg to 200 litres |

- Compo Plaster

Compo plaster shall be composed of one part cement, two parts lime and nine parts sand.

- Gypsum Skim Plaster

Gypsum skim plaster shall be pure gypsum plaster finished with a steel trowel.

- Two Coat Plaster With Gypsum Finish

Two coat plaster with gypsum finish shall comprise an undercoat of Class II cement plaster finished with a wooden float and a finishing coat of gypsum skim plaster.

- Rough-Cast Plaster

Rough-cast plaster shall be applied in two coats. The undercoat shall be composed of one part cement and five parts sand finished with a wooden float. The finishing coat shall be composed of one part cement and three parts stone aggregate that will pass through a 4mm sieve. The finishing coat shall be flicked on with a machine before the undercoat has set to obtain an even texture.

- Fine Rough-Cast Plaster

Fine rough-cast plaster shall be as for rough-cast plaster but the finishing coat shall be composed of one part cement and three parts coarse sand.

- General

Rates for plastering described as being on vertical surfaces of brickwork or blockwork shall include concrete columns, beams and lintels flush with the face of the wall.

      - P – Tiling

- Materials And Workmanship

Materials and workmanship shall comply with the following standards:

Glazed ceramic wall tiles and fittings	SANS 22

Ceramic wall and floor tiles	SANS 1449

Common cement	SANS 50197-1(Class 32,5N)

Masonry cement	SANS 50413-1(Class 22,5X)

Aggregates from natural sources – Fine

aggregates for plaster and mortar	SANS 1090

The design and installation of ceramic tiling	SANS 10107

- Tiles, Mosaics, Etc

Tiles, mosaics, etc shall be even in shape and size, free from cracks, twists or blemishes and uniform in colour.

- Preparatory Work

Surfaces shall be clean and free of oil and thoroughly wetted directly before any tiling is commenced. Concrete surfaces shall be slushed with a mixture of one part cement and one part coarse sand or otherwise treated to form a proper key.

- Ceramic Wall And Floor Tiling

Where tiles are fixed to plaster or screeds with an adhesive, the adhesive shall be as recommended by the manufacturer of the tiles. Joints shall be straight, continuous and flush pointed with an approved grouting compound.

- General

Tiling described as “on walls” is on brick walls or block walls unless otherwise stated and shall include concrete columns, beams and lintels flush with the face of the wall.

      - Q – Plumbing and Drainage

- Materials And Workmanship

Materials and workmanship shall comply with the following standards:

Sheet metal

Sheet zinc	BS 849

Sheet aluminium	BS 1470

Sheet copper								BS 2870 
Rainwater systems

Unplasticized poly(vinyl chloride) (PVC-U)

components for external rainwater systems	SANS 11

Pipes and fittings

Steel pipes : Pipes suitable for threading and of

nominal size not exceeding 150mm	SANS 62

Plain-ended solid drawn copper tubes for Potable water	SANS 460

Malleable cast iron fittings threaded to ISO 7-1	SANS 4

Polyethylene (PE) pipes for water supply – Specifications	SANS 4427

Cast iron fittings for asbestos cement pressure pipes 	SANS 546

Vitrified clay sewer pipes and fittings	SANS 559

Reinforced concrete pressure pipes	SANS 676

Concrete non-pressure pipes	SANS 677

Cast iron pipes and pipe fittings for use above ground in drainage installations	SANS 746

Unplasticized poly(vinyl chloride) (PVC-U) sewer

and drain pipes and pipe fittings	SANS 791

Fibre-cement pipes, couplings and fittings for

sewerage, drainage and low-pressure irrigation	SANS 819

Pitch-impregnated fibre pipes and fittings and jointing 	SANS 921

Unplasticized poly (vinyl chloride) (PVC-U) pressure pipe systems	SANS 966-1

Unplasticized poly(vinyl chloride) (PVC-U) soil,

waste and vent pipes and pipe fittings	SANS 967

Rubber joint rings (non-cellular)	SANS 974-1

Copper-based fittings for copper tubes	SANS 1067-1&2

Fibre-cement pressure pipes and couplings	SANS 1223

Polypropylene pressure pipes	SANS 1315

Non-metallic waste traps	SANS 1321-1&2

Vent valves for drainage installations	SANS 1532

Heavy duty cast iron pipe fittings for drainage and gas and water supplies	BS 78

Lead pipes	BS 602

Cast iron pressure pipes for use in drainage and gas and water supplies	BS 1211

Stainless steel pipes for use with compression fittings	BS 4127

Sanitary fittings etc

Stainless steel sinks with draining boards (for domestic use)	SANS 242

Stainless steel wash-hand basins and wash troughs 	SANS 906

Stainless steel sinks for institutional use	SANS 907

Stainless steel stall urinals	SANS 924

Acrylic sanitary ware : Baths	SANS 1402-1

Glazed ceramic sanitary ware	SANS 497

WC flushing cisterns	SANS 821

Flush valves for WC flushing cisterns	SANS 1509

Taps, valves etc

Water taps (metallic bodies)	SANS 226

Water taps (plastic bodies)	SANS 1021

Single control mixer taps	SANS 1480

Float valves	SANS 752

Plastic floats for ball valves	SANS 1006

Functional control valves and safety valves for

Domestic hot and cold water supply systems	SANS 198

Cast iron gate valves for waterworks	SANS 664

Automatic shut-off flush valves for water closets and urinals	SANS 1240

Check valves (flanged and wafer types)	SANS 1551-1&2

Fire extinguishers

Portable refillable fire extinguishers	SANS 1910

Portable rechargeble fire extinguishers :

Halogenated hydrocarbon type extinguishers	SANS 1151

Water heaters and fire hose reels

Fixed electric storage water heaters	SANS 151

Fire hose reels (with semi-rigid hose)	SANS 543

Drainage covers, gratings, etc

Cast iron surface boxes and manhole and inspection covers and frames	SANS 558

Cast iron gratings for gullies and stormwater drains 	SANS 1115

The installation of polyethylene and poly

(vinyl chloride) (PVC-U and PVC-M) pipes	SANS 10112

Water supply and drainage for buildings	SANS 10252-1&2

Cast iron step irons	BS 1247

- General

- Excavations

Excavations shall be deemed to be in “earth”. Backfilling to excavations shall be executed in 300mm thick layers, watered and compacted. Surplus excavated material shall be spread and levelled over site as directed

- Q.2.2 Concrete

Unreinforced concrete shall be Class B prescribed mix concrete and reinforced and precast concrete shall be Class C prescribed mix concrete

- Q.2.3 Brickwork

Brickwork shall be of extra hard burnt bricks built in Class I mortar

- Q.2.4 Plaster

Plaster shall be 1:3 cement plaster finished smooth with a steel trowel. All angles shall be rounded

- Q.2.5 Diameters of pipes etc

Diameters stated for pipes, traps, valves, etc are internal diameters except PVC, polyethylene, stainless steel and copper pipes and traps for which external diameters are stated

- Sheet Metal Work

- Galvanized sheet iron

Galvanized sheet iron shall be rolled steel sheet coated on both sides with Class Z275, unless otherwise specified, zinc coating complying with SANS 3575/4998. Sheets shall be free from white rust

- Eaves Gutters

- Galvanized sheet iron gutters

Galvanized sheet iron gutters shall have beaded edges and all joints shall be riveted and soldered. Angles shall be strengthened with 50 x 0,6mm galvanized sheet iron strips soldered on over the internal faces of mitres

Gutters shall be fixed with falls to outlets on 30 x 3mm galvanized mild steel brackets, bent to the shape of gutters, with front ends taken up to the underside of beaded edge of gutter and each screwed to roof timbers or bolted to fibre-cement fascias with 6mm galvanized gutter bolts. Gutters shall be bolted to brackets at front with 6mm galvanized gutter bolts, one to each bracket

Brackets shall be positioned at joints of gutters and intermediately at not exceeding 1,25m centres

- Fibre-cement gutters

Fibre-cement gutters shall have spigot and socket joints. Gutters shall be fixed with falls to outlets on standard aluminium alloy brackets, screwed or bolted to roof timbers or fascias

- Unplasticized polyvinyl chloride (UPVC) gutters

Gutters shall be fixed with falls to outlets on brackets as supplied by the manufacturer, screwed or bolted to roof timbers or fascias

- Aluminium gutters

Aluminium gutters shall be roll formed on site to required lengths and profiles from 3003H14-3SH4 alloy strip not less than 0,7mm thick factory coated on both sides with baked enamel and two coats of silicone modified polyester to a total minimum thickness of 20 micrometres. Angles, stopped ends, etc shall be prefabricated units pop riveted to gutters with joints sealed with mastic. The guttering shall be in continuous lengths between angles, stopped ends, etc

- Rainwater Pipes

- Galvanized sheet iron pipes

Galvanized sheet iron pipes shall have seams at the back and shall be jointed with soldered slip joints. Pipes shall be fixed to walls etc with galvanized mild steel holderbats spaced at not exceeding 2m centres with tails driven in or cut and pinned in 1:3 cement mortar

- Fibre-cement pipes

Fibre-cement pipes shall have spigot and socket joints. Pipes shall be fixed to walls etc with standard

aluminium alloy holderbats with tails driven in or cut and pinned in 1:3 cement mortar

- Unplasticized polyvinyl chloride (UPVC) pipes

Pipes shall be fixed to walls etc with patented UPVC or aluminium clips and holderbats as supplied by the manufacturer of the pipe

- Aluminium pipes

Aluminium pipes and fixing straps shall be formed from 3003H14-3SH4 alloy strip not less than 0,7mm thick factory coated on both sides as described for aluminium gutters. Pipes shall be in continuous lengths with formed angles, offsets, shoes, etc. Pipes shall be fixed to walls etc with 20 x 0,6mm straps at not exceeding 1,5m centres screwed to 25 x 75 x 100mm hardwood chamfered and oiled blocks plugged to walls

- Stormwater Channels

In-situ concrete stormwater channels shall be constructed of unreinforced concrete with segmental channel formed in top. Channels shall be laid to falls on a well rammed earth bottom and finished smooth on exposed surfaces

Precast concrete channels shall be of 25 MPa concrete, generally in 1m lengths, finished smooth from the mould on exposed surfaces, laid to falls on a well rammed earth bottom, jointed in 1:3 cement mortar and pointed with keyed joints

- Joints

Joints of pipes not covered by SANS shall be as follows:

| Pipes | Joints |
| --- | --- |
| Fibre-cement, concrete, pitch-impregnated fibre and vitrified clay pipes for use under ground in non-pressure pipe lines | Flexible joints in accordance with the manufacturer’s instructions |
| Cast iron for use above ground | Spigot and socket joints with tarred rope yarn and caulking compound or Plain ended joints with stainless steel couplings with neoprene rubber sleeves |
| Cast iron for use below ground | Spigot and socket joints with tarred rope yarn and caulking compound |
| Galvanized mild steel | Joints of screwed galvanized steel sockets or bolted galvanized iron flanges Screwed joints with plastic jointing tape or hemp Flanged joints which shall be bolted and provided with rubber gaskets and with flanges screwed to pipes |
| Joints between pipes of different materials shall be as follows: |  |
| Between cast iron and mild steel | Spigot and socket joints with tarred rope yarn and caulking compound |
| Between cast iron and clay | Spigot and socket joint with semi-dry cement caulking and 1:2 cement mortar fillet |
| Between mild steel or copper and clay | Spigot and socket joint with either bitumen or semi-dry cement caulking and 1:2 cement mortar fillet |

- Fixing Of Pipes

Pipes shall be fixed as follows:

| Q.8.1 Galvanized mild steel (except those stated in Q.8.3) | To walls with galvanized mild steel brackets for pipes not exceeding 80mm diameter and with galvanized cast iron hinged holderbats with brass pins or bolts for pipes exceeding 80mm diameter; both types with tails cut and pinned in 1:3 cement mortar To woodwork with screw-on type galvanized mild steel holderbats |
| --- | --- |
| Q.8.2 Copper and stainless steel | To walls with brass holderbats or screw-on type two- piece spacing clips for pipes not exceeding 75mm diameter and with purpose made holderbats for pipes exceeding 75mm diameter; both types with tails cut and pinned in 1:3 cement mortar To woodwork with screw-on type brass holderbats |
| Q.8.3 Cast iron and galvanized mild steel for soil, waste and vent pipes | To walls with hinged cast iron holderbats with brass bolts and with tails cut and pinned in 1:3 cement mortar To woodwork with screw-on type galvanized mild steel holderbats |
| Q.8.4 Polyethylene, polypropylene and patented UPVC or unplasticized polyvinyl chloride | To walls, woodwork, etc with aluminium clips and holderbats as supplied by the manufacturer of the pipes |
| Q.8.5 Fibre-cement | To walls with aluminium alloy holderbats with tails cut and pinned in 1:3 cement mortar |
| Q.8.6 Pipes fixed to ceilings | Fixed with holderbats and standard or purpose made hangers, with extended hangers for pipes to falls |

- Pipes Laid in Ground

- Water pipes etc

Water pipes, gas pipes, etc laid in ground shall be at least 400mm deep from the crown of the pipe to the finished surface

- Drain pipes

Excavations taken out too deep shall be filled in with selected soil and compacted. Backfilling to sides and up to 300mm above plastic pipes shall be free from stone or hard substances which will not pass a 10mm mesh

- Cleaning Eye Lids

Cleaning eye lids for drain pipe fittings shall be fixed and sealed as follows:

| Pipe fittings | Method of sealing and fixing |
| --- | --- |
| Fibre-cement | Sealed with synthetic rubber or bituminous mastic packing and fixed with screws |
| Vitrified clay | Polypropylene lid sealed with synthetic rubber packing and pressed into position |
| Polypropylene and unplasticized polyvinyl chloride | Sealed with synthetic rubber packing and screwed on or pressed into position |
| Cast iron | Sealed with tallow or putty and fixed with non-ferrous metal screws |
| Galvanized malleable cast iron and cast brass | Sealed with synthetic rubber packing and screwed in |

- Cleaning Eyes

Cleaning eyes shall consist of cast iron frames and lids with letters “CE” (or “SO”) cast in lids. The lids shall be secured with non-ferrous metal screws. Frames shall be jointed to vertical drain pipes. Cleaning eyes shall be encased in unreinforced concrete taken up to ground level and plastered on exposed surfaces

- Inspection Eye Marker Slabs

Inspection eye marker slabs shall be 350 x 350 x 50mm thick precast concrete finished smooth from the mould, with letters “IE” (or “IO”) formed in top and placed flush in ground or paving

- Gulleys

Gulleys shall be built up of traps, vertical piping and gulley heads with loose gratings, all encased in unreinforced concrete to finish flush with gulley head top and taken up to at least 50mm above surrounding finished surfaces. The outer top edge of the concrete encasing shall be splayed and the exposed surfaces plastered

- Dished Gulleys

Dished gulleys shall be built up of traps, vertical piping and gulley heads with loose gratings, all encased in unreinforced concrete and with dished unreinforced concrete hopper size 450 x 450mm overall around gulley head with rounded kerb 50mm wide to front and sides and 25mm wide at back, 100mm high above top of dishing and the hopper plastered on exposed surfaces. Top of hopper shall be taken up to at least 50mm above surrounding finished surfaces

- Sumps, Catchpits, Inspection Chambers, Etc

- Rainwater sumps

Rainwater sumps shall be built with half-brick sides on 100mm thick unreinforced concrete bottom, plastered internally on walls and with 80mm high unreinforced concrete kerb at top rebated for grating or cover and plastered on exposed surfaces

- Stormwater catchpits and inspection chambers

Brick catchpits and inspection chambers shall be built with one-brick sides on 150mm thick unreinforced concrete bottom projecting 100mm beyond walls all round, plastered internally on walls and with 100mm thick reinforced concrete cover slab with opening rebated for frame of grating or cover and plastered on exposed surfaces

Precast concrete catchpits and inspection chambers shall be constructed in accordance with the applicable details shown on Drawing LE-1 of SANS 1200LE. Precast concrete manhole sections and slabs shall comply with SANS 1294 and pipes shall be SC type and in accordance with SANS 677

- Sewer inspection chambers

Brick inspection chambers shall be built as for brick stormwater inspection chambers and with the bottom of the chamber well benched around half round channels, bends, junctions, etc up to sides of chamber in unreinforced concrete finished smooth

Precast concrete inspection chambers shall be constructed in accordance with the applicable details shown on Drawing LD-5 of SANS 1200LD. Precast concrete manhole sections and slabs shall comply with SANS 1294 and the pipes shall be SC type in accordance with SANS 677

- Stormwater drain junction boxes

Junction boxes shall be formed of 150mm thick unreinforced concrete bottom and sides to suit the various sizes of the drain pipes and built after the pipes have been laid, with the sides taken up slightly higher than the highest pipe and finished level on top for and covered with a 75mm thick loose precast concrete slab

- Step irons

Where inspection chambers exceed 1,2m deep, cast iron step irons shall be provided, built into the wall at 300mm centres and staggered regularly in vertical rows spaced at 200mm centres horizontally

- Stopcock And Meter Boxes

Stopcock and meter boxes shall be built with half-brick sides with a cast iron box and lid complying with SANS 558 set in 75mm wide unreinforced concrete kerb for the full depth of the cast iron box and plastered on exposed surfaces

- Valve Chambers

Valve chambers shall be built with half-brick sides with 100mm thick unreinforced concrete kerb to top with rebate for cover and frame to finish flush with adjacent paving or finished ground level and plastered on exposed surfaces

- Cast Iron Covers, Gratings, Etc

All cast iron covers, gratings, frames and surface boxes shall be coated with preservative solution. Frames shall be cast into concrete. Covers, except covers to stormwater drainage or electrical cable inspection chambers, shall be set in grease

- Concrete Encasing

Concrete encasing for pipes, bends, traps, gulleys, grease traps, etc shall be unreinforced concrete not less than 100mm thick all round

- Sanitary Fittings

- General

Glazed ceramic, acrylic and porcelain enamelled sanitary fittings and component parts shall be white. Accessories for sanitary fittings shall be chromium plated brass

Waste outlets for baths, basins, etc shall comprise chromium plated brass waste union with grating, rubber washers and locknut, fitted with rubber or vulcanite plug on a chromium plated brass chain and stay

- Stainless steel sanitary fittings

Stainless steel sinks and draining boards, basins, wash troughs and urinals shall be AISI Type 304 satin finished stainless steel. All stainless steel fittings shall be treated on the back with a vermin proof sound deadening coating. Sinks, basins and wash troughs shall be provided with 40mm diameter screwed waste outlets

- Precast concrete wash troughs

Reinforced precast concrete wash troughs shall have a sloping front with ribbed rubbing surface and shall be finished smooth on exposed faces with top edges and inner angles rounded. Each compartment shall be fitted with a 40mm diameter waste outlet. Wash troughs shall each be supported on two reinforced precast concrete pedestals finished smooth on exposed faces

- Steel baths

Steel baths shall be porcelain enamelled internally and painted externally and fitted with waste outlet and overflow grating with coupling

- Acrylic resinous baths

Acrylic resinous baths shall be fitted with waste outlet and overflow grating with coupling

- Acrylic resinous wash hand basins

Acrylic resinous wash hand basins and vanity units shall have a smooth high gloss finish, with outlet openings, soap recesses, tap-holes and integral overflow and shall be fitted with waste outlet and overflow grating with coupling

- Glazed ceramic sanitary fittings

Sinks shall be provided with integral weir overflows

Washdown closet pans shall have washdown action and be provided with smooth finished injection moulded polypropylene heavy duty double flap seats fixed with non-ferrous bolts. Urinal channels shall be provided with outlet gratings fitted in bitumen

- Flush and sparge pipes

Flush pipes for high level cisterns shall be of plastic or drawn galvanized steel

Flushpipes for low level cisterns shall be of plastic

Flush and sparge pipes for urinals with high level cisterns shall be of chromium plated copper piping and of the sizes recommended by the manufacturer of the urinal.

- Installation of Sanitary

Fittings - Sanitary fittings shall be installed as follows:

- Precast concrete wash troughs

Precast concrete wash troughs shall be bedded on top of pedestals which shall be bedded on floors in 1:3 cement mortar

- Stainless steel wash troughs and wash hand basins

Stainless steel wash troughs and wash hand basins shall be fixed to walls on a pair of galvanized mild steel gallows brackets bolted to wall with 6mm diameter expanding bolts

- Acrylic resinous wash hand basins

Acrylic resinous wash hand basins shall be fixed to walls on a pair of standard painted cast iron brackets screwed to underside of basin and bolted to wall with 6mm diameter expanding bolts

- Ceramic wash hand basins

Ceramic wash hand basins shall be fixed to walls on a pair of standard painted steel or cast iron brackets bolted to wall with 6mm diameter expanding bolts

- Acrylic resinous baths

Acrylic resinous baths shall be bedded in 1:5 cement mortar on three cross rows of bricks or bedded solid on a layer of dry river sand and fixed to wall with galvanized steel brackets under edges (in the middle of the sides against walls) bolted to wall with 6mm diameter expanding bolts and sealed along top against wall finishes with patent mildew resistant silicone rubber

- Washdown closet pans and cisterns

Washdown closet pans shall be bedded on floors in 1:3 cement mortar. Cisterns shall be fixed to walls with 6mm diameter expanding bolts

- Ceramic urinals

Ceramic stall and slab urinals shall be bedded on floors and against walls in 1:3 cement mortar. Slabs, channels, treads, etc shall be jointed in 1:3 cement mortar and pointed in white cement

Ceramic bowl urinals shall be fixed to walls on standard steel brackets bolted to wall with 6mm diameter expanding bolts. Cisterns shall be fixed to walls on standard brackets bolted to wall with 6mm diameter expanding bolts

- Stainless steel urinals

Stainless steel stall and slab urinals shall be bedded on floors in 1:3 cement mortar and with backs and sides against walls filled in with fine unreinforced concrete. Cisterns shall be fixed as cisterns for ceramic urinals

- Fire Hose Reels

Fire hose reels shall each be fitted with a 30m long hose of internal diameter not less than 19mm with a 4,8mm internal diameter chromium plated brass nozzle

- Fire Extinguishers

All fire extinguishers shall be fully charged.

- Tests

Sewerage pipe lines, sanitary plumbing including fittings and hot and cold water supply and fire service shall be tested to the approval of the Principal Agent and Local Authority.

The Contractor shall provide all testing apparatus, material and labour required for the tests and inspections.

      - R – Glazing

- Materials and Workmanship

Materials and workmanship shall comply with the following standards:

Glass in building	SANS 50572-1 to 5

Glazing putty for wooden and metal window frames 	SANS 680

Silvered glass mirrors for general use	SANS 1236

Safety and security glazing materials for buildings	SANS 1263-1 to 3

Sealing compounds for the building industry, one

Component, silicone-rubber based	SANS 1305

The installation of glazing materials in buildings	SANS 10137

Work on glass for glazing	SANS 1817

- Putty etc

Glazing putty shall be Type I for wooden sashes and Type II for steel sashes. Putty for glazing to unpainted hardwood shall be tinted to match the colour of the wood.

Back putty shall not exceed 3mm thick. Putty shall not be painted until it has formed a surface crust, and if the putty does not form a surface crust it shall be replaced.

Butyl putty shall be used where glass is to be fixed in aluminium sashes with glazing beads Non-setting compounds shall be used where laminated glass is fixed in sashes with glazing beads.

      - S – Paintwork

- Materials and Workmanship

Materials and workmanship shall comply with the following standards:

Decorative paint for interior use	SANS 515

Decorative high gloss enamel paints	SANS 630

Primers for wood (for external work)	SANS 678

Primers for wood (for internal work)	SANS 678

Zinc phosphate primer for steel	SANS 1319

Undercoats for paints (except emulsion paint)	SANS 681

Aluminium paint	SANS 682

Varnish for interior use	SANS 887

Emulsion paints	SANS 1586

Materials for paintwork shall be delivered to the site in unopened containers and applied in accordance with the manufacturer’s instructions. Materials shall be suitable for application to the surfaces concerned. Undercoats shall be as recommended by the manufacturer of the finishing coats.

- Preparatory Work

- Plastered surfaces etc

Plastered surfaces shall be thoroughly inspected and, if necessary, washed down and brushed in order to remove any traces of efflorescence and allowed to dry completely before any paint finish is applied. Before any paint is applied, holes, cracks and irregularities in plaster and other surfaces shall be filled with a suitable filler and finished smooth. Unfinished concrete surfaces shall have all projections rubbed off and shall be thoroughly cleaned with a spirits-of-salts solution (1 part concentrated spirits-of-salts to 4 parts water)

- Metal surfaces

Metal surfaces shall be sanded, where necessary, washed with a suitable cleaning agent and left smooth

Protective coatings applied by manufacturers to galvanized metal surfaces shall be removed with a suitable agent and the surfaces washed down

Rust, grease and defective factory primers on metal surfaces, as well as pitch on cast iron pipes, shall be removed

- Wood surfaces

Knots in woodwork shall be treated with knotting. Minor blemishes shall be filled with a suitable filler. Wood surfaces shall be sanded smooth

- Application of Paint

Primers to wood surfaces shall be applied by brush. Primers to other surfaces may be applied by roller with the approval of the Principal Agent. Undercoats and finishing coats may be applied by brush or roller

Paint shall not be sprayed on except in the case of cellulose and other special paints where spray painting is the accepted method of application

Before subsequent coats of paint are applied the previous coat shall be properly dry and shall be sanded down where necessary

- Colour Scheme

A colour scheme comprising colours and the blending of colours approved by the Principal Agent shall be used for the paintwork. The tints of the undercoats shall closely match the finishing coat but nevertheless differ sufficiently to indicate the number of undercoats. Colour samples of the finishing coats shall be provided in all cases

- General

Paintwork shall include the preparation of surfaces, filling, stopping, sanding and priming of nail heads and screws. Where windows, sashes, etc are to be painted, the rebates of the openings to be glazed shall be primed

      - T – Paperhanging

- Preparatory Work

Plaster surfaces to be papered shall be dry, thoroughly cleaned down, filled with a suitable filler as necessary to obtain a smooth surface and painted thereafter with a single coat of emulsion paint.

Wood surfaces to be papered shall be knotted, stopped and sanded.

- Paperhanging

Wallpaper shall be hung in vertical long lengths. Vertical joints shall be close-fitted and plumb and the paper shall be tightly fitted to skirtings, ceilings, door frames, windows, etc. Horizontal joints will not be allowed.

      - U – External Works

- General

- Excavations

Excavations shall be deemed to be in “earth”

- Landscaping

- Topsoil

Topsoil shall vary between sandy loamy soil and sandy clayey soil with an ideal composition of 15% to 25% clay, 10% silt/sludge and 65% to 75% sand, with a minimum ratio of organic material of 2%. All material shall be free of harmful deposits as well as unwanted seeds

- Compost

Compost shall be composed of properly decayed organic material, free from harmful deposits, salts, seeds and other waste material and shall have a pH of more than 4 and less than 7

- Mulch

Mulch shall be approved organic material free from small particles of bark residue, fungus, disease, etc

- Lime

Lime shall be agricultural lime of an approved manufacture

- Fertilizer

Fertilizer shall be of the type specified, mixed thoroughly into the soil as prescribed. No fertilizer shall be added more than two weeks prior to planting

- Backfilling

Backfilling in plant and tree holes shall be composed of two parts topsoil to one part compost mixed thoroughly together and compacted by foot in 100mm layers. Fertilizer shall only be added if prescribed

- Pebbles

Pebbles shall be smooth with a uniform colour and form and ranging in size from 50mm to 75mm diameter. Removal of pebbles from river beds shall be done selectively to avoid any major disruption to the ecology of the river and environment

- Plant material

- General

All plant material (plants, shrubs, trees, etc) shall be obtained from a registered nursery and shall be free from damaged parts, parasites, fungus, other plant diseases or insects. No container-bound plants will be acceptable

- Trees

The height of trees described in the bills of quantities shall be measured from the top of the root ball to the top of the tree. Where trees are pruned, such prune wounds shall not be more than 25mm in diameter and be sealed with an approved sealing compound

- Shrubs and small plants

Shrubs and small plants shall meet the requirements for height and spread as specified. Thin or sparsely branched plants shall not be accepted. Branches shall be well spread with ample young branches and the plant as a whole shall be growing well

- Groundcover

Groundcover shall be dense and healthy and shall comply with the minimum requirements for leaf density as specified

Formal grass shall be planted as runners in 50mm deep drills at 150mm centres unless otherwise described

- Cultivation and preparation of planting areas etc

All surface rocks and stones larger than 50mm shall be removed before commencing cultivation and preparation. The entire area shall be ripped and rotavated using approved machinery by breaking up the earth to a depth of 300mm at 600mm centres in both directions, unless otherwise described, and then levelled. Where fertilizer or compost is specified, it shall be worked into the topsoil after ripping and rotavation to a depth of 300mm and finished to final levels

All fertilizer to areas to be grassed shall be strewn on the final layer before final finishing is commenced and worked mechanically into the top 150mm soil

- Planting procedure

Holes for shrubs and groundcover shall be as follows:

- Shrubs – 500 x 500 x 500mm deep

- Groundcover – 300 x 300 x 300mm deep (if not planted in drills)

- Holes for trees shall be square, of adequate size to accommodate the root system and suitable for the height of the tree

All plant material shall be watered thoroughly before careful removal from the container and planted in the prescribed planting medium with the top of the soil in the container finishing level with the surrounding area. Water dams size 800mm diameter x 150mm deep and 500mm diameter x 150mm deep shall be formed around trees and shrubs respectively and all planting material shall be watered immediately after planting. Trees, shrubs, etc shall be properly staked or stayed, depending on their size, on the prevailing windy side with patent tree ties

- Maintenance

All planted areas shall be maintained for a period of three months after practical completion as defined in the contract with the exception of hydroseeded areas which shall be maintained for 12 months after an acceptable cover has been obtained

This maintenance shall consist of keeping clear of weeds and litter, loosening soil where necessary every two weeks, replacing damaged, diseased or dead plants, pruning, cutting and mowing as necessary and watering so as to keep the plant material in a healthy growing condition

- Roadwork

- Filling

Filling under roads etc shall be of inert material having a maximum plasticity index of 10, free from large stones etc spread, levelled, watered and compacted in layers not exceeding 200mm thick to a density of 98% Mod AASHTO

- Preparation of sub-grade

The sub-grade shall be prepared by scarifying for a depth of 150mm and compacting to a density of 98% Mod. AASHTO, including trimming to the correct levels and grades

- Base course

The base course shall consist of crusher run stone compacted to a density of 98% Mod. AASHTO and finished to the correct levels and grades

- Weed killer

The completed sub-grade shall be treated with an approved total weed killer

- Bituminous premix road surfacing

Before spreading the premix material, the base course shall be swept clean and free from all dust, dirt and loose particles, lightly wetted and sprayed with a prime coat of cutback bitumen complying with SANS 308 at the rate of 1 litre/m2

The material shall consist of semi-gap graded crushed stone aggregate having the following grading:

| Sieve size mm) |  | % By mass passing sieve |  |
| --- | --- | --- | --- |
| 13,2 | 100 |  |
| 4,75 | 45-60 |  |
| 2,36 | 42-55 |  |
| 1,18 | 40-52 |  |
| 0,3 | 25-45 |  |
| 0,075 | 5-12 |  |

The aggregate shall be mixed with bituminous road tar binder complying with SANS 748 at the rate of 1m3 of stone to 120 litre of emulsion at atmospheric temperature

The binder shall be added to the stone and mixed until the stone is uniformly coated. Thereafter 5% of clean, dry quartzitic sand shall be added and mixed until evenly distributed through the mixture

The premix shall be applied only after the primer has dried out completely and shall be spread immediately after mixing and rolled on the same day

Spreading shall be done evenly over the prepared base course to a loose depth sufficient to ensure the consolidated thickness specified

Rolling shall commence as soon as the binder has set sufficiently, followed after three days by a final rolling

- Precast concrete block road surfacing

Paving blocks shall be precast concrete blocks complying with SANS 1058

Blocks shall be laid to true levels and grades on and including a 25mm thick layer of river sand with joints exceeding 2mm and not exceeding 6mm wide

After laying, the paving shall be compacted by means of a vibrating plate compactor, with joints between the blocks filled in, after compaction, by sweeping in fine sand

Infill areas at edges of paving constituting less than 25% of a full block unit and of 25mm minimum dimension shall be filled with Class C prescribed mix unreinforced concrete with top surface trowelled smooth to match blocks. Smaller areas shall be filled with 1:4 cement mortar

- Precast concrete kerbs and channels

Precast concrete kerbs and channels shall comply with SANS 927, generally in 1m lengths and finished smooth from the mould on exposed surfaces. Kerbs and channels shall be bedded on and jointed in 1:3 cement mortar and pointed with keyed joints. Bases to kerbs shall be Class B prescribed mix unreinforced concrete

- Process control tests

The Contractor shall be responsible for carrying out all necessary process control tests on the density and moisture content of the compacted sub-grade, base course, etc to ensure that the required compaction is being attained

- Fencing Etc

- Materials

Materials and workmanship shall comply with the following specifications and requirements :

Wooden poles, droppers, guardrail posts and spacer blocks	SANS 457-2&3

Zinc-coated fencing wire	SANS 675

Prefabricated concrete components for fencing	SANS 1372

Chain-link fencing and its wire accessories 	SANS 1373

Fasteners	SANS 1700

Anti-intruder fences	CKS 451

Metal droppers and standards	CKS 451

- Galvanized wire

All galvanized wire shall be zinc coated wire with Class B zinc coating. Straining wire shall be 4mm diameter galvanized mild steel wire. Tie wire shall be 1,6mm diameter galvanized mild steel wire

- Plastic coated wire

Plastic coated straining wire shall be 3,15mm diameter Class C galvanized mild steel wire plastic coated to an overall diameter of 3,95mm.

Plastic coated tie wire shall be 1,8mm diameter Class C galvanized mild steel wire plastic coated to an overall diameter of 2,5mm.

- Galvanized barbed wire

Galvanized barbed wire shall be 2,5mm diameter mild steel double strand reverse twist zinc coated barbed wire with Class A zinc coating.

- Galvanized wire mesh

Galvanized wire mesh shall be 50mm mesh chain link netting of 2,5mm diameter Class C galvanized mild steel wire.

- Plastic coated wire mesh

Plastic coated wire mesh shall be 50mm mesh chain link netting of 2,5mm diameter Class C galvanized mild steel wire plastic coated to an overall diameter of 3,25mm.

- Galvanized welded wire mesh

Galvanized welded wire mesh shall be fabricated from pre-galvanized wires to rectangular pattern welded together at each intersection using a welding method which forms a zinc oxide protective coating at each intersection.

- Razor wire

Razor wire shall be fabricated from 2,5mm diameter galvanized high tensile steel wire fitted with razor barbs formed of 0,5mm galvanized steel strip clipped on at 37,5mm centres.

- Metal droppers and standards

Droppers shall be of ridged T-section mild steel with a mass of not less than 0,55kg/m. Standards shall be of I- section mild steel with a mass of not less than 3kg/m or of ridged edge Y-section mild steel with a mass of not less than 2,5kg/m, and shall be driven 600mm deep into the ground.

Droppers and standards shall have either galvanized, sprayed metal or painted finish as described in the items and in accordance with CKS 451. In addition, those surfaces of standards embedded in the ground shall be coated with bitumen.

- Metal posts and stays

Posts and stays shall comply with CKS 451 and shall be of black galvanized mild steel tubing as specified.

Straining posts shall be of 108mm outside diameter x 3mm wall thickness tubing, each with a 300 x 300 x 5mm thick mild steel sole plate and a steel cap welded on.

Intermediate posts shall be of 50mm outside diameter x 2,5mm wall thickness tubing, each with a 230 x 230 x 5mm thick mild steel sole plate and a steel cap welded on.

Stays for straining posts shall be of 50mm outside diameter x 2,5mm wall thickness tubing, each with a 230 x 230 x 5mm thick mild steel sole plate welded on and fixed raking with top end flattened, bent, holed and bolted to straining post with and including a 5mm diameter galvanized mild steel bolt with nut and washer.

Posts and stays shall have either galvanized or painted finish as described in the items and in accordance with CKS 451. In addition, sole plates and portions of posts and stays embedded in ground shall be coated with bitumen.

- Timber posts, stays and droppers

Timber posts shall be 125mm diameter, timber stays shall be 100mm diameter and timber droppers shall be 30mm diameter.

- Prestressed concrete posts and stays

Prestressed concrete posts and stays shall be finished smooth from the mould and uniformly stressed by means of high tensile longitudinal prestressing wires with concrete cover to wires of not less than 20mm.

Corner and straining posts shall be 100 x 100mm and intermediate posts and stays shall be 75 x 75mm. Stays shall be fixed raking with top end splayed and glued to posts with a suitable epoxy compound.

- Bolts, nuts and washers

Straining eye bolts, hinge bolts, bolts, nuts and washers shall be galvanized.

- Precast concrete fencing

Precast concrete fencing over sloping terrain shall be stepped to suit terrain, including the use of increased lengths of posts as necessary, excavation, etc.

- Concrete bases

Bases in ground for posts, stays, etc shall be of Class B prescribed mix concrete with tops 100mm below surface of ground.

Sizes of concrete bases for posts, stays, etc shall be as follows:

Straining and gate posts	–	450 x 450 x 700mm deep

Intermediate posts	–	300 x 300 x 600mm deep

Stays			–	600 x 300 x 500mm deep

- Security overhangs

Where fencing is described as having a security overhang, the posts and standards shall have angular (single arm) extension arms.

Extension arms shall be attached to the posts and standards by welding in the case of steel and by spiking in the case of timber.

Concrete extension arms shall be cast integrally with the post or standard.

Barbed wire to security overhangs shall be tightly strained and wired at each intersection with extension arms and shall have barbed wire braces at 450mm centres between standards, posts, etc wired onto the barbed wire and the top straining wire.

- Gates

Gates shall be formed of 40mm outside diameter x 2,5mm wall thickness mild steel tubular framework with welded joints, strongly braced as necessary and filled in with wire mesh as described above.

Bill 3 - Mechanical

Preamble

Pricing Assumptions mean the criteria as set out below, read together with all Parts of this contract document, which it will be assumed in the contract, that the tenderer has taken into account when developing his prices.

- The method of measurement published by the South African Bureau of Standards in clause 8 of the Standardised Specifications for Civil Engineering Construction is applicable, subject to the variations and amendments contained in the section “Applicable SANS 1200 standardised specifications”.

Descriptions in the Schedules of Quantities are abbreviated and comply generally with those in the Standardised Specifications.  The applicable clause of each Standardised Specification, read together with the relevant clauses of the Scope of Work, set out what ancillary or associated activities are included in the rates for the operations specified. Should any requirements of the measurement and payment clause of the applicable Standardised Specification, or the Scope of Work, conflict with the terms of the Schedule, the requirements of the Standardised Specification or Scope of Work, as applicable, shall prevail.

The measurement and payment clauses in a specification in which further information regarding the scheduled items is given, are referenced under “Item” (pay items) in the Schedules of Quantities. The referenced clauses are not necessarily the only sources of information in respect of scheduled items. Further information and specifications may be found elsewhere in the contract documents. Standardised Specifications are identified by the digits which follow SANS in the SANS 1200 series of specifications, e.g. G for SANS 1200 G.

Unless otherwise stated, items are measured net in accordance with the drawings, and no allowance is made for waste.

The quantities set out in the Schedules of Quantities are the estimated quantities of the Contract Works, but the Contractor will be required to undertake whatever quantities may be directed by the Employer’s Agent from time to time. The Contract Price for the completed contract shall be computed from the actual quantities of work done, valued at the relevant unit rates and prices.

The prices and rates to be inserted in the Schedule of Quantities are to be the full inclusive prices for the work described under the several items. Such prices and rates shall cover all costs and expenses that may be required in and for the execution of the work described, and shall cover the cost of all general risks, liabilities, and obligations set forth or implied in the documents on which the tender is based, as well as overhead charges and profit. Reasonable prices shall be inserted as these will be used as a basis for assessment of payment for additional work that may have to be carried out.

A price or rate should be entered against each item in the Schedules of Quantities, whether the quantities are stated or not. An item against which no rate is/are entered, or if anything other than a rate or a nil rate (for example, a zero, a dash or the word “included” or abbreviations thereof) is entered against an item, it will also be regarded as a nil rate having been entered against that item, i.e. that there is no charge for that item. The Tenderer may be requested to clarify nil rates, or items regarded as having nil rates; and the Employer may also perform a risk analysis with regard to the reasonableness of such rates.

Except where rates only are required, insert all amounts to be included in the total tendered price in the "Amount" column and show the corresponding total tendered price.

Items have been provided where any further items considered necessary by the Tenderer can be priced. The Tenderer must provide full details of what has been allowed for with his Tender under these items.

The units of measurement described in the Schedule of Quantities are metric units. Abbreviations which may be used in these Schedule of Quantities are as follows:

- Sum/item		=	lump sum

- No.		=	number

Where fractions of a cent occur in calculations of prices and amounts, they shall be rounded up/down to the nearest whole cent.

Where the tenderer cannot tender in all respects in accordance with the provisions contained in the tender documents, all deviations therefrom shall be clearly and separately listed in the Schedule of Deviations, or in a tenderer’s covering letter expressly referenced in this schedule.

The tenderer accept that the Employer will examine such deviations and shall not be bound to accept any such deviations or qualifications.

It must be clearly stated by the tenderer whether the sum tendered in the Tender Offer includes for all such deviations or qualifications listed or referred to in the schedule titled Proposed Deviations and Qualifications by Tenderer or not.

Should the submission of Schedules of Quantities which have been priced electronically, and which the Tenderer wishes to submit as a printed version with his/her tender in the place of handwritten priced Schedule of Quantities, the following shall apply.

If there is found to be any variance between the printed version and the original issued document, the original shall stand.  However, where Addenda have been issued which amend the Schedules of Quantities, then the printed Schedules of Quantities shall take these into account.

The pages of the issued Schedules of Quantities should not be removed from the tender document.

All descriptions or clauses where trade names or proprietary products are specified, are deemed to include the phrase “or equal approved”

Tenderers are referred to Sub-Clause 13.7 in the regarding contract price adjustment.

The following schedules in Mechanical Schedules of Quantities (Bill 3) are deemed applicable to the following categories for the purposes of Contract Price Adjustment:

| Bill 3 | CPA CATEGORY |
| --- | --- |
| BoQ 1 : Preliminary and General | Site Installation and General Items |
| BoQ 2 : Coarse and Fine Screening | To be proportioned between Mechanical Plant and Materials / Site Installation and General Items |
| BoQ 3: Degritting | To be proportioned between Mechanical Plant and Materials / Site Installation and General Items |
| BoQ 4: Pump Station | To be proportioned between Mechanical Plant and Materials / Site Installation and General Items |
| BoQ 5: Dewatering Facility | To be proportioned between Mechanical Plant and Materials / Site Installation and General Items |
| BoQ 6: Cake Transfer and Storage | To be proportioned between Mechanical Plant and Materials / Site Installation and General Items |
| BoQ 7: Biological Reactors | To be proportioned between Mechanical Plant and Materials / Site Installation and General Items |
| BoQ 8: Utilities | To be proportioned between Mechanical Plant and Materials / Site Installation and General Items |
| BoQ 9: Mechanical Sundries | To be proportioned between Mechanical Plant and Materials / Site Installation and General Items |
| BoQ 10: Second Class Water | To be proportioned between Mechanical Plant and Materials / Site Installation and General Items |
| BoQ 11: Ultrafine Screens | To be proportioned between Mechanical Plant and Materials / Site Installation and General Items |

Design of the Works, Contractor’s Documents (including “as built” drawings and Manual), and design for the manufacture of materials and equipment, must be priced and will be paid for as follows:

- An item is provided in the Schedules of Quantities (BoQ No. 1, Preliminary and General) for Design of the Works and submission of Contractor’s Documents – this item includes inter alia the Contractor’s obligations under Clause 2 in Part C3.2 Engineering,

- Items are provided in the Schedules of Quantities (BoQ 9: Mechanical Sundries) for Providing “as built” drawings, and draft and final copies of the Installation, Operation and Maintenance Manuals – these items cover the Contractor’s obligations in Part C3.2 Engineering

- Items of materials and equipment are provided in the Schedules of Quantities under headings containing the words “design, manufacture, painting, testing, supply, delivery, offloading and storage” – “design” in these items will usually only be paid upon supply of the materials and equipment, but may be paid for separately at the discretion of the Engineer.

Items are provided in the Schedules of Quantities (BoQ 9: Mechanical Sundries) for costs associated with witnessing various testing. Tenderers should take note of the method used for costing in the detailed mechanical specification.

A provisional sum has been allowed in the Schedule of Quantities (BoQ 9: Mechanical Sundries) to extend the Contractor’s obligation to include operation and maintenance of the works during the defects period. Refer to the detailed mechanical specification for more details.

Items are provided in the Schedules of Quantities (BoQ 9: Mechanical Sundries) for costs associated with The Contractor training the Employer’s staff. Tenderers should take note of the training requirements in the detailed mechanical specification.

Bill 4 - Electrical

Measurement and Payment Principles

Scheduled pay items are items to be priced in the bill of quantities. Contractors are to familiarise details and components indicated under each item as these are to be allowed for in the pricing. No additional costs or variations will be allowed for items indicated. Contractors to comply with the General and Particular Specification in its entirety when pricing.

The basic principles of measurement and payment for works carried out will be as installed and measured on site. No extra is payable for slack, wastage, supplier minimum length, etc.

Schedules Pay Items (PI)

- Reticulation System

| PI. | 1.1. | Low voltage Cable | Unit: m. |
| --- | --- | --- | --- |
| - The unit of measure shall be the cable length in meters supplied, installed, terminated, and commissioned. - The rate shall include the supply and installation of copper PVC/SWA/PVC/ECC cables laid in ducts, trenches, horizontal racks, or vertical ducts. Rates shall include the supply and fixing of supports with regard to installation of cables. Rates shall include the PVC cable ties as required. All cables are Copper PVC/SWA/PVC/ECC cables per SANS 1507. |  |  |  |
| PI. | 1.2. | Low voltage Cable Joint and Termination. | Unit: No. |
| - The unit of measure shall be the number of joints and terminations supplied and installed. - The rate shall include the termination of copper PVC/SWA/PVC/ECC cables in DB's, Kiosks and metering panel. Rates shall include the supply and installation of glands, shrouds, lugs, nuts, bolts, and washers as required. |  |  |  |

- Building Electrical Works

| PI. | 2.1. |  | Distribution Board |  | Unit: No. |  |
| --- | --- | --- | --- | --- | --- | --- |
| - The unit of measure shall be the number of complete distribution board units supplied and installed. - The rate shall include the supply & installation of distribution boards complete with doors, frames, sub-frames, chassis fixtures, switchgear, terminations, bus-bars and wiring, labelling and line diagrams as specified. Minimum 30% spare space to be allowed in each DB. |  |  |  |  |  |  |
| PI. |  | 2.2. |  | Conduit & Conduit boxes |  | Unit: No. & m |  |
| - The unit of measure shall be length of conduit and number of conduit boxes supplied and installed. - The rate shall include the supply and installation of conduit and boxes as specified for lighting, power, and auxiliary outlets, including couplings, bushes, locknuts, bending, drawboxes and fixing, etc in accordance with metallic conduit and accessories as per SANS 950. |  |  |  |  |  |  |
| PI. | 2.3. |  | Power Skirting |  | Unit: No. & m |  |
| - The unit of measure shall be number, and length of power skirting and ducts installed on surface. - The rate shall include the supply and fixing of surface mounted ducts and power skirting, complete with cover plates. |  |  |  |  |  |  |
| PI. | 2.4. |  | PVC Insulated Copper Conductors |  | Unit: m |  |
| - The unit of measure shall be length of power skirting installed on surface. - The rate shall include the supply and drawn in of copper PVC insulated conductors in conduit or trunking system in floor or in roof space for lights, plugs and power points, including connection to switches and equipment. For Live, Neutral and Earth. |  |  |  |  |  |  |
| PI. | 2.5. |  | Light Switches |  | Unit: No |  |
| - The unit of measure shall be number of light switches installed on surface. - The rate shall include the supply, installation, and connection of 16 Amp light switches in flush 50 x 100 x 50mm boxes, including white coloured cover plates. |  |  |  |  |  |  |
| PI. | 2.6. |  | Switched Socket Outlet |  | Unit: No |  |
| - The unit of measure shall be number of light switches installed on surface. - The rate shall include supply, installation, and connection of 16Amp switched socket outlets in single, two compartment power skirting, and in 100 x 100 x 50mm boxes with white coloured cover plates. |  |  |  |  |  |  |
| PI. | 2.7. |  | Isolator |  | Unit: No |  |
| - The unit of measure shall be number of isolators supplied and installed. - The rate shall include the supply, installation, and connection of isolator in extension box complete with box, mounting screw, labels and cover plate. |  |  |  |  |  |  |

- Lighting

| PI. | 3.1. | Luminaires | Unit: No. |
| --- | --- | --- | --- |
| - The unit of measure shall be the number of luminaires supplied and installed. - The rate shall include the supply, installation and commissioning of Luminaires. Note that all luminaires are subject to approval by the Engineer prior to purchase. - Alternate fittings proposed will only be considered if cost saving, better quality and longer guarantee is provided and subject to approval by the engineer, architect, and client. |  |  |  |
| PI. | 3.2. | Mid-hinged Masts and Poles | Unit: No. |
| - The unit of measure shall be the number of poles supplied and installed. - The rate shall include the supply Installation and Commissioning of light poles. Note that all light poles are subject to approval by the Engineer prior to purchase. |  |  |  |

- Earthing and Lightning Protection

| PI. | 4.1. | Soil Resistivity Tests | Unit: Item |
| --- | --- | --- | --- |
| - The unit of measure shall be the number of tests done. - The rate shall include conduction of a complete soil resistivity survey for the switching station area. Resistivity measurements shall be taken at, at least 5 locations and at the supply points. It shall include a certificate and recommendation regarding the soil conditions. |  |  |  |
| PI. | 4.2. | Earth Conductors | Unit: No. & m |
| - The unit of measure shall be the number of earth test points and the length of earthing conductors. - The rate shall include the conductors installed in trenches, sleeves and in earth trench. - Terminations to include drilling, bolting, connections, sealing and testing. Only cad weld joints will be allowed. |  |  |  |
| PI. | 4.3. | Earth Bars | Unit: No. |
| - The unit of measure shall be the number of earth bars supplied and installed. |  |  |  |
| PI. | 4.4. | Enclosures | Unit: No. |
| - The unit of measure shall be the number of enclosures supplied and installed, as well as the number of labels for test joint box. |  |  |  |
| PI. | 4.5. | Earth Electrodes | Unit: No. |
| - The unit of measure shall be the number of earth electrodes supplied and installed. - The rate shall include the supply and install 'Cadweld' 16 mm diameter copper earth electrodes driven in ground, including 'Cadweld' joining sleeves as required. |  |  |  |
| PI. | 4.6. | Earthing of Indoor Equipment | Unit: No. |
| - The unit of measure shall be the number of points of earthing. - The rate shall include the earth equipment as per drawings and specification to achieve earth resistivity values as per SANS and NRS requirements |  |  |  |
| PI. | 4.7. | Trench Excavations for Earthing and Lightning Protection | Unit: m3 & m |
| - The unit of measure shall be volume of the trench excavation and the length of the cable warning tape. - The rate shall include the excavation for earthing including temporary support of sides, keeping excavation dry, bedding material, backfilling, compacting, and testing as specified. All backfill material to be suitable as per SANS codes and engineer’s approval. Backfill material to be imported if necessary. |  |  |  |

- Standby Generator System

| PI. | 5.1. | Complete 1100kVA Outdoor Standby Generator Set | Unit: No. |
| --- | --- | --- | --- |
| - The unit of measure shall be the number of generator units supplied and installed. *Note: Refer to Generator Schedule B7 and Technical Specifications - The rate shall include the supply, install, testing and commissioning of a fully enclosed, acoustic, outdoor diesel generator complete with smart controller, exhaust, day fuel tank and accessories. - Generator to be included in a new ISO painted container. - To include 12 months maintenance and guarantee. |  |  |  |
| PI. | 5.2. | Bulk Diesel Tank | Unit: No. |
| - The unit of measure shall be the number of units supplied and installed. *Note: Refer to Bulk tank Schedule B8 and Technical Specifications - The rate shall include the supply, install, testing and commissioning of a self bunded, outdoor diesel tank complete with level control and pumped diesel supply to the generator day tanks. - To include 12 months maintenance and guarantee. |  |  |  |

| PI. | 5.3. | Electric bulk filling (for emergency fuel fill) | Unit: No. |
| --- | --- | --- | --- |
| - The unit of measure shall be the number of units supplied and installed. *Note: Refer to Bulk tank Schedule B8 and Technical Specifications - The rate shall include the supply, install, testing and commissioning of a self priming centrifugal pump complete with control panel and loose pipework for manual filling of generator tanks via 200 Litre drums. - To include 12 months maintenance and guarantee. |  |  |  |

- Sleeves and Manholes

| PI. | 6.1. | HDPE Sleeves | Unit: m |
| --- | --- | --- | --- |
| - The unit of measure shall be the length of HDPE sleeves supplied and installed. - The rate shall include the supply and installation of HDPE sleeves buried in ground as specified for Electrical,& data services, including couplings in accordance with non-metallic sleeves and accessories as per SANS 61386-24. Tenderers to note that all sleeves under buildings will be encased in concrete by the building contractor. |  |  |  |
| PI. | 6.2. | Manholes | Unit: No. |
| - The unit of measure shall be the number of manholes supplied and installed. - The rate shall include the construction of watertight manholes in ground as specified for Electrical & data services, including, lockable cover, seals ,bushes, sleeve entries and end caps. Inclusive of cover and frame (Cover and frame - colour: GREY) including engraving on cover to read : "DATA" for data manholes and "ELECTRICAL" for electrical manholes. |  |  |  |
| PI. | 6.3. | Trench Excavations | Unit: m3 & m |
| - The unit of measure shall be volume of the trench excavation and the length of the cable warning tape. - The rate shall include the excavation for earthing including temporary support of sides, keeping excavation dry, bedding material, backfilling, compacting, and testing as specified. All backfill material to be suitable as per SANS codes and engineer’s approval. Backfill material to be imported if necessary. |  |  |  |

- LV Distribution Network

| PI. | 7.1. | LV Kiosks | Unit: No. |
| --- | --- | --- | --- |
| - The unit of measure shall be the number of LV kiosks supplied and installed. - The rate shall include the supply and installation of Low Voltage Kiosks complete with plinth, base, doors, frames, sub-frames, chassis fixtures, switchgear, terminations, bus-bars, wiring, labelling and line diagrams as specified. |  |  |  |
| PI. | 7.2. | Signage and Labelling | Unit: Item |
| - The unit of measure shall be the number of labels supplied and installed. - The rate shall include the supply and installation of all signage as per OHS Act and eThekwini Electricity requirements. |  |  |  |

- Testing, Comissioning and Handover of Electrical Installation

| PI. | 8.1. |  | Testing and Commissioning |  | Unit: Item |  |
| --- | --- | --- | --- | --- | --- | --- |
| - The unit of measure shall be the complete testing, proving and handover of a complete working system. - The rate shall include the testing and commissioning of the complete installation per SANS 10142-1 and as specified. |  |  |  |  |  |
| PI. | 8.2. | Documentation |  | Unit: Item |  |
| - The unit of measure shall be the submission of all relevant handover documents. |  |  |  |  |  |
| PI. | 8.3. | Training |  | Unit: Item |  |
| - The following items to be accounted for: - Provide training to Personnel on systems as per technical schedule B11 – Training Requirements. - Provide Training Manuals for critical operation and maintenance of the complete system. |  |  |  |  |  |
| PI. | 8.4. | General |  | Unit: Item |  |
| - The following items to be accounted for: - Guarantee and full maintenance of the complete electrical system for 12 months after handover to the client. - Full list of material and maintenance plan to be provided. - Guarantee and full maintenance of the complete Generator system for 12 months after handover to the client. To include all spares and replacement items for generator. Based on running time of 20Hrs per month. - Full list of material and maintenance plan to be provided. |  |  |  |  |  |

Bill 5 – Control and Instrumentation

Measurement and Payment Principles

Scheduled pay items are items to be priced in the bill of quantities. Contractors are to familiarise details and components indicated under each item as these are to be allowed for in the pricing. No additional costs or variations will be allowed for items indicated. Contractors to comply with the General and Particular Specification in its entirety when pricing.

The basic principles of measurement and payment for works carried out will be as installed and measured on site. No extra is payable for slack, wastage, supplier minimum length, etc.

Schedules Pay Items (PI)

- Reticulation System

| PI. | 1.1. | Low voltage Cable | Unit: m. |
| --- | --- | --- | --- |
| - The unit of measure shall be the cable length in meters supplied, installed, terminated, and commissioned. - The rate shall include the supply and installation of copper PVC/PVC/SWA/PVC cables laid in ducts, trenches, horizontal racks, or vertical ducts. Rates shall include the supply and fixing of supports with regard to installation of cables. Rates shall include the PVC cable ties as required. All cables are Copper PVC/PVC/SWA/PVC cables per SANS 1507. |  |  |  |
| PI. | 1.2. | Low voltage Cable Joint and Termination. | Unit: No. |
| - The unit of measure shall be the number of joints and terminations supplied and installed. - The rate shall include the termination of copper PVC/PVC/SWA/PVC cables in PLC’s, DB's, junction boxes and instrument junction boxes. Rates shall include the supply and installation of glands, shrouds, lugs, nuts, bolts, and washers as required. |  |  |  |
| PI. | 1.3. | Control and Instrument Cable | Unit: m. |
| - The unit of measure shall be the cable length in meters supplied, installed, terminated, and commissioned. - The rate shall include the supply and installation of copper Dekobon type M855 single pair, M877 multi pairs and M865, M887 triad cables laid in ducts, trenches, horizontal racks, or vertical ducts. Rates shall include the supply and fixing of supports with regard to installation of cables. Rates shall include the PVC cable ties as required. |  |  |  |
| PI. | 1.4. | Control and Instrument Cable Joint and Termination. | Unit: No. |
| - The unit of measure shall be the number of joints and terminations supplied and installed. - The rate shall include the termination of copper Dekobon type M855 single pair, M877 multi pairs and M865, M887 triad cables in PLC’s, DB's, junction boxes and instrument junction boxes. Rates shall include the supply and installation of glands, shrouds, lugs, nuts, bolts, and washers as required. |  |  |  |

- Field Junction Boxes

| PI. | 2.1. | Junction Boxes | Unit: No. |
| --- | --- | --- | --- |
| - The unit of measure shall be the number of complete field junction box units supplied and installed. - The rate shall include the supply & installation of field junction boxes complete with doors, frames, sub-frames, chassis fixtures, circuit breakers, surge protection devices, terminations, terminals, wiring, labelling and line diagrams as specified. |  |  |  |
| PI. | 2.2. | Instrument Junction Boxes | Unit: No. |
| - The unit of measure shall be the number of complete instrument junction box units supplied and installed. - The rate shall include the supply & installation of instrument junction boxes complete with doors, frames, sub-frames, chassis fixtures, circuit breakers, surge protection devices, terminations, terminals, wiring, labelling and line diagrams as specified. |  |  |  |

- Instrumentation

| PI. | 3.1. | Field Instrumentation | Unit: No. |
| --- | --- | --- | --- |
| - The unit of measure shall be the number of instruments supplied and installed. - The rate shall include the supply, installation and commissioning of the instruments and the required fixtures and fittings, including but not limited to isolation valves, mounting brackets and support as required. |  |  |  |

- Cable Racking

| PI. | 4.1. | Cable Racking | Unit: No. & m |
| --- | --- | --- | --- |
| - The unit of measure shall be the number of; internal bends, 90° bends, T-pieces and the length of cable racking installed. - The rate shall include the supply and installation of the required support steel, splice kits and earth bonding and continuity conductors econduction of a complete soil resistivity survey for the switching station area. Resistivity. |  |  |  |

- Sleeves and Manholes

| PI. | 5.1. | HDPE Sleeves | Unit: m |
| --- | --- | --- | --- |
| - The unit of measure shall be the length of HDPE sleeves supplied and installed. - The rate shall include the supply and installation of HDPE sleeves buried in ground as specified for Electrical,& data services, including couplings in accordance with non-metallic sleeves and accessories as per SANS 61386-24. Tenderers to note that all sleeves under buildings will be encased in concrete by the building contractor. |  |  |  |
| PI. | 5.2. | Manholes | Unit: No. |
| - The unit of measure shall be the number of manholes supplied and installed. - The rate shall include the construction of watertight manholes in ground as specified for Electrical & data services, including, lockable cover, seals ,bushes, sleeve entries and end caps. Inclusive of cover and frame (Cover and frame - colour: GREY) including engraving on cover to read : "DATA" for data manholes and "ELECTRICAL" for electrical manholes. |  |  |  |
| PI. | 5.3. | Trench Excavations | Unit: m3 & m |
| - The unit of measure shall be volume of the trench excavation and the length of the cable warning tape. - The rate shall include the excavation for earthing including temporary support of sides, keeping excavation dry, bedding material, backfilling, compacting, and testing as specified. All backfill material to be suitable as per SANS codes and engineer’s approval. Backfill material to be imported if necessary. |  |  |  |

- Testing, Comissioning and Handover of C&I Installation

| PI. | 6.1. | Testing and Commissioning | Unit: Item |
| --- | --- | --- | --- |
| - The unit of measure shall be the complete testing, proving and handover of a complete working system. - The rate shall include the testing and commissioning of the complete installation per SANS 10142-1 and as specified. |  |  |  |
| PI. | 6.2. | Documentation | Unit: Item |
| - The unit of measure shall be the submission of all relevant handover documents. |  |  |  |
| PI. | 6.3. | Training | Unit: Item |
| - The following items to be accounted for: - Provide training to Personnel on systems. Allow for 2 days for 3 people. - Provide Training Manuals for critical operation and maintenance of the complete system. |  |  |  |
| PI. | 6.4. | General | Unit: Item |
| - The following items to be accounted for: - Guarantee and full maintenance of the complete C&I system for 12 months after handover to the client. - Full list of material and maintenance plan to be provided. |  |  |  |

BILL OF QUANTITIES

CONTENTS

PACKAGE A

BILL1: CIVIL AND STRUCTURAL

BoQ 1 : Preliminary and general

BoQ 2: Inlet works, raw sewage pump station and second class water pump station

BoQ 3: Dewatering facility

BoQ 4: Services (Potable water and second class water)

BoQ 5: Reactor and other miscellaneous items

BILL 2: BUILDING WORKS

BoQ 1: Alterations and refurbishment of admin building

BoQ 2: Raw water pump station

BoQ 3: Guardhouses

BoQ 4: Sludge dewatering building

BILL 3: MECHANICAL WORK

BoQ 1 : Preliminary and General

BoQ 2 : Coarse and Fine Screening

BoQ 3: Degritting

BoQ 4: Pump Station

BoQ 5: Dewatering Facility

BoQ 6: Cake Transfer and Storage

BoQ 7: Biological Reactors

BoQ 8: Utilities

BoQ 9: Mechanical Sundries

BoQ 10: Second Class Water

BILL 4: ELECTRICAL WORK

BoQ 1 : Preliminary and general

BoQ 2 : Emergency generator system

BoQ 3: Domestic power & lighting

BoQ 4: Earthing & lightning protection

BoQ 5: MV Works

BoQ 6: Inlet works electrical system

BoQ 7: Dewatering electrical system

BoQ 8: Raw sewage pump station electrical system

BoQ 9: OHS, testing, commissioning, training & general electrical

BILL 5: CONTROL AND INSTRUMENTATION WORKS

BoQ 1 : Preliminary and general

BoQ 2 : Inlet works C&I system

BoQ 3 : Dewatering C&I system

BoQ 4: Raw sewage pump station C&I system

BoQ 5: Network system

BoQ 6: System integration, testing, training & general C&I

SUMMARY OF BILLS FOR PACKAGE A

- CONTENTS

PACKAGE B

BILL1: CIVIL AND STRUCTURAL

BoQ 1 : Preliminary and General

BoQ 3: Dewatering facility

BoQ 4: Services (Potable water and second class water)

BILL 2: BUILDING WORKS

BoQ 1: Admin Building

BoQ 3: Guardhouse

BoQ 4: Dewatering facility

BILL 3: MECHANICAL WORK

BoQ 1 : Preliminary and General

BoQ 5: Dewatering Facility

BoQ 6: Cake Transfer and Storage

BoQ 9: Mechanical Sundries

BoQ 10: Second Class Water

BILL 4: ELECTRICAL WORK

BoQ 1 : Preliminary and general

BoQ 2 : Emergency generator system

BoQ 3: Domestic power & lighting

BoQ 4: Earthing & lightning protection

BoQ 5: MV Works

BoQ 6: Dewatering electrical system

BoQ 7: OHS, testing, commissioning, training & general electrical

BILL 5: CONTROL AND INSTRUMENTATION WORKS

BoQ 1 : Preliminary and general

BoQ 2 : Dewatering C&I system

BoQ 3: Network system

BoQ 4: System integration, testing, training & general C&I

SUMMARY OF BILLS FOR PACKAGE B