ROSHERVILLE BUILDINGS FIRE SAFETY CONCERNS

STAND 14 OIL DEPOT

Brief Description:

The Oil Depot consists of North and South Tank farms

2 x large tanks with an estimated Shell area of 252 sq meter each.

12 x smaller tanks with an estimated shell area of 50 sq meter each

Total surface area for tank farm North - 1104 sq/m (Excluding bund area)

Total surface area for tank farm South – 1104 sq/m (Excluding bund area)

Minimum water required:  1104 sq /m x 10.2 mm/min = 11,260 L/min per tank farm. Refer to regulation – N.F.P.A.15 – Chapter 4.5.2.1 (Fire protection for the exposed vessels), also refer to the EMS By-Laws Chapter 6 (63) (a). Permanent Above Ground Storage Tanks for Flammable liquids

Available water supply for fire protection currently: 4200 L/min@ 600 Kpa

The flow of 4200 L/min being supplied by the existing pumps at TGS Balancing plant will be inadequate for the worst case scenario

Refer to regulation - N.F.P.A.  15,   Chapter 4.1.5.1 (Size of System and Water Demand) - a single system shall not protect more than one fire area.

In view of the above report and the risk demand, the Oil plant needs a comprehensive and standalone Fire detection and suppression system which will cater for Oil plant only.

Regen Plant:

The main purpose of the Regen plant is to regenerate the oil that is not usable, and this is designed to operate 24 hours. Since the oil is classified as Class B, in a fire condition and after the burning oil has reaching the flash point the spillage can result in a pool fires which will be very difficult to control. So the Regen plant is classified as a high risk area and therefore it must be fully fire protected. Also bear in mind that in 2004 there was a massive fire at Oil plant, because the installed fire protection proved inadequate for its designed purpose.  Please Refer to SABS 0400:1990 Part T – Fire Protection T1 (1), (b) and also T2 – (2)

Thanks

Canon Mthethwa