{"text_format":"3","workbook":"xls","n_sheets":6,"sheets":["D20 IDF","D20 Inputs","D20 Controls","D20 Analogues","Revision History","C.T. & V.T."],"not_rendered":{"external_links":19,"defined_names":691},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"D20 IDF","index":0,"n_rows":63,"n_cols":18,"rows_kept":63,"merged":[[3,4,3,8]],"flags":["formulas_cached_only"]}
[]
[]
[]
[{"$nulls":4},"MAKHATINI S/S TELECONTROL IDF"]
[{"$nulls":14},"D20A","D20K","D20S","D20C"]
[{"$nulls":4},"VERTICAL A",{"$nulls":3},"VERTICAL B",{"$nulls":4},"Analogue Inputs",32,null,null,16]
[{"$nulls":4},"PROTECTION ",{"$nulls":3},"PROTECTION ",{"$nulls":4},"Control Outputs (Singles)",null,64,null,16]
[{"$nulls":3},"NO.","ROW","CABLE",null,"NO.","ROW","CABLE",{"$nulls":3},"Digital Inputs",null,null,64,16]
[{"$nulls":3},1,"D20A CARD #1     (ANALOGUES 1 - 32)",null,null,1,"132KV NONDABOYA"]
[{"$nulls":3},2,null,"C01 ",null,2]
[{"$nulls":3},3,null,"40 Pair",null,3]
[{"$nulls":3},4,{"$nulls":3},4]
[{"$nulls":3},5,{"$nulls":3},5]
[{"$nulls":3},6,"D20K CARD #1         (CONTROLS 1 - 64)",null,null,6,"132/22KV TRANSFORMER 1"]
[{"$nulls":3},7,null,"C02",null,7]
[{"$nulls":3},8,null,"40 Pair",null,8]
[{"$nulls":3},9,{"$nulls":3},9]
[{"$nulls":3},10,{"$nulls":3},10]
[{"$nulls":3},11,null,"C03",null,11,"132/22KV TRANSFORMER 1 TAP CHANGER"]
[{"$nulls":3},12,null,"40 Pair",null,12]
[{"$nulls":3},13,{"$nulls":3},13]
[{"$nulls":3},14,"D20S CARD #1           (INPUTS 1 - 64)",null,null,14,"NETWORK BREAKER 23"]
[{"$nulls":3},15,null,"C04",null,15]
[{"$nulls":3},16,null,"40 Pair",null,16]
[{"$nulls":3},17,{"$nulls":3},17,"NETWORK BREAKER 24"]
[{"$nulls":3},18,{"$nulls":3},18]
[{"$nulls":3},19,null,"C05",null,19]
[{"$nulls":3},20,null,"40 Pair",null,20,"NETWORK BREAKER 43"]
[{"$nulls":3},21,{"$nulls":3},21]
[{"$nulls":3},22,"D20S CARD #2       (INPUTS 65 - 128)",null,null,22]
[{"$nulls":3},23,null,"C06",null,23,"NETWORK BREAKER 57"]
[{"$nulls":3},24,null,"40 Pair",null,24]
[{"$nulls":3},25,{"$nulls":3},25]
[{"$nulls":3},26,{"$nulls":3},26,"?"]
[{"$nulls":3},27,null,"C07",null,27]
[{"$nulls":3},28,null,"40 Pair",null,28,"?"]
[{"$nulls":3},29,{"$nulls":3},29]
[{"$nulls":3},30,"D20S CARD #2       (INPUTS 129 - 192)",null,null,30,"?"]
[{"$nulls":3},31,null,"C08",null,31]
[{"$nulls":3},32,null,"40 Pair",null,32,"?"]
[{"$nulls":3},33,{"$nulls":3},33]
[{"$nulls":3},34,{"$nulls":3},34]
[{"$nulls":3},35,null,"C09",null,35]
[{"$nulls":3},36,null,"40 Pair",null,36]
[{"$nulls":3},37,{"$nulls":3},37]
[{"$nulls":3},38,{"$nulls":3},38]
[{"$nulls":3},39,{"$nulls":3},39]
[{"$nulls":3},40,{"$nulls":3},40]
[{"$nulls":3},41,{"$nulls":3},41]
[{"$nulls":3},42,{"$nulls":3},42]
[{"$nulls":3},43,{"$nulls":3},43]
[{"$nulls":3},44,{"$nulls":3},44]
[{"$nulls":3},45,{"$nulls":3},45]
[{"$nulls":3},46,{"$nulls":3},46]
[{"$nulls":3},47,{"$nulls":3},47]
[{"$nulls":3},48,{"$nulls":3},48]
[{"$nulls":3},49,{"$nulls":3},49]
[{"$nulls":3},50,{"$nulls":3},50]
[{"$nulls":3},51,{"$nulls":3},51]
[{"$nulls":3},52,{"$nulls":3},52]
[{"$nulls":3},53,{"$nulls":3},53]
[{"$nulls":3},54,{"$nulls":3},54]
[{"$nulls":3},55,{"$nulls":3},55]

{"sheet":"D20 Inputs","index":1,"n_rows":305,"n_cols":24,"rows_kept":305,"merged":[[4,2,4,3],[5,2,5,3],[6,2,6,9],[6,10,6,14],[6,15,6,17],[6,18,6,19],[7,2,7,5],[7,6,7,9],[168,7,168,9],[169,7,169,9],[213,7,213,9],[214,7,214,9],[254,7,254,9],[255,7,255,9],[280,7,280,9],[281,7,281,9]],"flags":["formulas_cached_only"]}
[]
[]
[{"$nulls":8},"TELECONTROL FUNCTION ALLOCATION AND WIRING RECORDS"]
[{"$nulls":9},"DIGITAL INPUTS"]
[null,null,"STATION :",null,"MAKHATINI"]
[null,null,"ADDRESS :",null,7221]
[null,null,"I . D . F .",{"$nulls":7},"D20 RACK",{"$nulls":4},"MASTER STN",null,null,"D20 CONFIGURATION / MASTER STATION"]
[null,null,"PROTECTION",{"$nulls":3},"TELECONTROL",{"$nulls":15},"TESTED TO","TESTED TO"]
[null,null,"Vert","Block","-","+","Vert","Block","-","+","CARD #","-","+","D/I #","Bit Type ","Seg","Bit","Add","DESCRIPTION "," POINT NAME","STATE '0'","STATE '1'","PROTECTION","SCADA"]
[null,null,"B",3,"5a","5b","A",15,"1a","1b","D20S1",67,1,1,"2 Bit",1,1,0,"132KV NONDABOYA ","132KV BREAKER","OPENED"]
[null,null,"B",3,"6a","6b","A",15,"2a","2b","D20S1",68,2,2,"2 Bit",1,2,1,"132KV NONDABOYA ","132KV BREAKER","CLOSED"]
[null,null,"B",8,"9a","9b","A",15,"3a","3b","D20S1",69,3,3,"2 Bit",1,3,2,"132/22KV TRANSFORMER 1 ","132KV BREAKER","OPENED"]
[null,null,"B",8,"8a","8b","A",15,"4a","4b","D20S1",70,4,4,"2 Bit",1,4,3,"132/22KV TRANSFORMER 1 ","132KV BREAKER","CLOSED"]
[null,null,"B",9,"1a","1b","A",15,"5a","5b","D20S1",71,5,5,"2 Bit",1,5,4,"132/22KV TRANSFORMER 1 ","22KV BREAKER","OPENED"]
[null,null,"B",8,"10a","10b","A",15,"6a","6b","D20S1",72,6,6,"2 Bit",1,6,5,"132/22KV TRANSFORMER 1 ","22KV BREAKER","CLOSED"]
[null,null,"B",15,"1a","1b","A",15,"7a","7b","D20S1",73,7,7,"2 Bit",1,7,6,"22KV NETWORK BREAKER 23","22KV BREAKER","OPENED"]
[null,null,"B",15,"2a","2b","A",15,"8a","8b","D20S1",74,8,8,"2 Bit",1,8,7,"22KV NETWORK BREAKER 23","22KV BREAKER","CLOSED"]
[null,null,"B",18,"1a","1b","A",15,"9a","9b","D20S1",75,9,9,"2 Bit",1,9,8,"22KV NETWORK BREAKER 24","22KV BREAKER","OPENED"]
[null,null,"B",18,"2a","2b","A",15,"10a","10b","D20S1",76,10,10,"2 Bit",1,10,9,"22KV NETWORK BREAKER 24","22KV BREAKER","CLOSED"]
[null,null,"B",21,"1a","1b","A",16,"1a","1b","D20S1",77,11,11,"2 Bit",1,11,10,"22KV NETWORK BREAKER 43","22KV BREAKER","OPENED"]
[null,null,"B",21,"2a","2b","A",16,"2a","2b","D20S1",78,12,12,"2 Bit",1,12,11,"22KV NETWORK BREAKER 43","22KV BREAKER","CLOSED"]
[null,null,"B",24,"1a","1b","A",16,"3a","3b","D20S1",79,13,13,"2 Bit",1,13,12,"22KV NETWORK BREAKER 57","22KV BREAKER","OPENED"]
[null,null,"B",24,"2a","2b","A",16,"4a","4b","D20S1",80,14,14,"2 Bit",1,14,13,"22KV NETWORK BREAKER 57","22KV BREAKER","CLOSED"]
[{"$nulls":6},"A",16,"5a","5b","D20S1",81,15,15,"2 Bit",1,15,14,"SPARE"]
[{"$nulls":6},"A",16,"6a","6b","D20S1",82,16,16,"2 Bit",1,16,15,"SPARE"]
[null,null,"B",2,"5a","5b","A",16,"7a","7b","D20S1",83,17,17,"Status",2,1,16,"132KV NONDABOYA","VT FUSE","NORMAL","FAIL"]
[null,null,"B",2,"6a","6b","A",16,"8a","8b","D20S1",84,18,18,"Status",2,2,17,"132KV NONDABOYA","ZONE 1 TRIP","RESET","OPERATED"]
[null,null,"B",2,"7a","7b","A",16,"9a","9b","D20S1",85,19,19,"Status",2,3,18,"132KV NONDABOYA","RED PHASE TRIP","RESET","OPERATED"]
[null,null,"B",2,"8a","8b","A",16,"10a","10b","D20S1",86,20,20,"Status",2,4,19,"132KV NONDABOYA","WHITE PHASE TRIP","RESET","OPERATED"]
[null,null,"B",2,"9a","9b","A",17,"1a","1b","D20S1",87,21,21,"Status",2,5,20,"132KV NONDABOYA","BLUE PHASE TRIP","RESET","OPERATED"]
[null,null,"B",2,"10a","10b","A",17,"2a","2b","D20S1",88,22,22,"Status",2,6,21,"132KV NONDABOYA","ARC RELAY","ON","OFF"]
[null,null,"B",3,"1a","1b","A",17,"3a","3b","D20S1",89,23,23,"Status",2,7,22,"132KV NONDABOYA","BREAKER","HEALTHY","NOT HEALTHY"]
[null,null,"B",3,"2a","2b","A",17,"4a","4b","D20S1",90,24,24,"Status",2,8,23,"132KV NONDABOYA","MECHANISM","HEALTHY","NOT HEALTHY"]
[null,null,"B",3,"3a","3b","A",17,"5a","5b","D20S1",91,25,25,"Status",2,9,24,"132KV NONDABOYA","ZONE TIME DELAYED TRIP","RESET","OPERATED"]
[null,null,"B",3,"4a","4b","A",17,"6a","6b","D20S1",92,26,26,"Status",2,10,25,"132KV NONDABOYA","BREAKER FAIL","RESET","OPERATED"]
[null,null,"B",3,"8a","8b","A",17,"7a","7b","D20S1",93,27,27,"Status",2,11,26,"132KV NONDABOYA","EXTERNAL TRIP","RESET","OPERATED"]
[null,null,"B",3,"9a","9b","A",17,"8a","8b","D20S1",94,28,28,"Status",2,12,27,"132KV NONDABOYA","SUPERVISORY","ON","OFF"]
[null,null,"B",3,"10a","10b","A",17,"9a","9b","D20S1",95,29,29,"Status",2,13,28,"132KV NONDABOYA","PROTECTION ","HEALTHY","NOT HEALTHY"]
[null,null,"B",4,"1a","1b","A",17,"10a","10b","D20S1",96,30,30,"Status",2,14,29,"132KV NONDABOYA","BACK UP OVERCURRENT TRIP","RESET","OPERATED"]
[null,null,"B",4,"2a","2b","A",18,"1a","1b","D20S1",97,31,31,"Status",2,15,30,"132KV NONDABOYA","BACK UP EARTH FAULT TRIP","RESET","OPERATED"]
[null,null,"B",4,"3a","3b","A",18,"2a","2b","D20S1",98,32,32,"Status",2,16,31,"132KV NONDABOYA","BACK UP VT FUSE ","NORMAL","FAIL"]
[null,null,"B",4,"4a","4b","A",18,"3a","3b","D20S1",99,33,33,"Status",3,1,32,"132KV NONDABOYA","MAIN PROTECTION ON TEST","NORMAL","ON TEST"]
[null,null,"B",4,"5a","5b","A",18,"4a","4b","D20S1",100,34,34,"Status",3,2,33,"132KV NONDABOYA","BACK UP PROTECTION ON TEST","NORMAL","ON TEST"]
[null,null,"B",4,"6a","6b","A",18,"5a","5b","D20S1",101,35,35,"Status",3,3,34,"132KV NONDABOYA","BACK UP PROTECTION  CROSS TRIP","RESET","OPERATED"]
[null,null,"B",8,"6a","6b","A",18,"6a","6b","D20S1",102,36,36,"Status",3,4,35,"132/22KV TRANSFORMER 1","SUPERVISORY","ON","OFF"]
[null,null,"B",8,"7a","7b","A",18,"7a","7b","D20S1",103,37,37,"Status",3,5,36,"132/22KV TRANSFORMER 1","DC","ON","OFF"]
[null,null,"B",9,"2a","2b","A",18,"8a","8b","D20S1",104,38,38,"Status",3,6,37,"132/22KV TRANSFORMER 1","132KV PROTECTION  TRIP","RESET","OPERATED"]
[null,null,"B",9,"3a","3b","A",18,"9a","9b","D20S1",105,39,39,"Status",3,7,38,"132/22KV TRANSFORMER 1","22KV PROTECTION  TRIP","RESET","OPERATED"]
[null,null,"B",9,"4a","4b","A",18,"10a","10b","D20S1",106,40,40,"Status",3,8,39,"132/22KV TRANSFORMER 1","22KV REF OPERATED","RESET","OPERATED"]
[null,null,"B",9,"5a","5b","A",19,"1a","1b","D20S1",107,41,41,"Status",3,9,40,"132/22KV TRANSFORMER 1","132KV BREAKER ","HEALTHY","NOT HEALTHY"]
[null,null,"B",9,"6a","6b","A",19,"2a","2b","D20S1",108,42,42,"Status",3,10,41,"132/22KV TRANSFORMER 1","22KV BREAKER","HEALTHY","NOT HEALTHY"]
[null,null,"B",9,"7a","7b","A",19,"3a","3b","D20S1",109,43,43,"Status",3,11,42,"132/22KV TRANSFORMER 1","PROTECTION NOT HEALTHY","HEALTHY","NOT HEALTHY"]
[null,null,"B",9,"8a","8b","A",19,"4a","4b","D20S1",110,44,44,"Status",3,12,43,"132/22KV TRANSFORMER 1","MASTER TRIP","RESET","OPERATED"]
[null,null,"B",9,"9a","9b","A",19,"5a","5b","D20S1",111,45,45,"Status",3,13,44,"132/22KV TRANSFORMER 1","132KV MAIN TRIP CIRCUIT FAIL","RESET","OPERATED"]
[null,null,"B",9,"10a","10b","A",19,"6a","6b","D20S1",112,46,46,"Status",3,14,45,"132/22KV TRANSFORMER 1","132KV B/U TRIP CIRCUIT FAIL","RESET","OPERATED"]
[null,null,"B",10,"1a","1b","A",19,"7a","7b","D20S1",113,47,47,"Status",3,15,46,"132/22KV TRANSFORMER 1","22KV MAIN TRIP CIRCUIT FAIL","RESET","OPERATED"]
[null,null,"B",7,"1a","1b","A",19,"8a","8b","D20S1",114,48,48,"Status",3,16,47,"132/22KV TRANSFORMER 1","BUCHHOLZ  TRIP","RESET","OPERATED"]
[null,null,"B",7,"2a","2b","A",19,"9a","9b","D20S1",115,49,49,"Status",4,1,48,"132/22KV TRANSFORMER 1","MAIN TANK PRESSURE  RELIEF TRIP","RESET","OPERATED"]
[null,null,"B",7,"3a","3b","A",19,"10a","10b","D20S1",116,50,50,"Status",4,2,49,"132/22KV TRANSFORMER 1","OIL  TEMPERATURE  TRIP","RESET","OPERATED"]
[null,null,"B",7,"4a","4b","A",20,"1a","1b","D20S1",117,51,51,"Status",4,3,50,"132/22KV TRANSFORMER 1","OLTC BUCHHOLZ   TRIP","RESET","OPERATED"]
[null,null,"B",7,"5a","5b","A",20,"2a","2b","D20S1",118,52,52,"Status",4,4,51,"132/22KV TRANSFORMER 1","NEC BUCHHOLZ / OIL TEMPERATURE TRIP","RESET","OPERATED"]
[null,null,"B",7,"6a","6b","A",20,"3a","3b","D20S1",119,53,53,"Status",4,5,52,"132/22KV TRANSFORMER 1","WINDING TEMPERATURE TRIP","RESET","OPERATED"]
[null,null,"B",7,"7a","7b","A",20,"4a","4b","D20S1",120,54,54,"Status",4,6,53,"132/22KV TRANSFORMER 1","BUCHHOLZ  ALARM","RESET","OPERATED"]
[null,null,"B",7,"8a","8b","A",20,"5a","5b","D20S1",121,55,55,"Status",4,7,54,"132/22KV TRANSFORMER 1","WINDING / OIL TEMPERATURE ALARM","RESET","OPERATED"]
[null,null,"B",7,"9a","9b","A",20,"6a","6b","D20S1",122,56,56,"Status",4,8,55,"132/22KV TRANSFORMER 1","OIL LEVEL ","NORMAL","LOW"]
[null,null,"B",7,"10a","10b","A",20,"7a","7b","D20S1",123,57,57,"Status",4,9,56,"132/22KV TRANSFORMER 1","NEC BUCHHOLZ / OIL TEMPERATURE ALARM","RESET","OPERATED"]
[null,null,"B",8,"1a","1b","A",20,"8a","8b","D20S1",124,58,58,"Status",4,10,57,"132/22KV TRANSFORMER 1","SFT OPERATED","RESET","OPERATED"]
[null,null,"B",12,"1a","1b","A",20,"9a","9b","D20S1",125,59,59,"Status",4,11,58,"132/22KV TRANSFORMER 1 TAP CHANGE","DC","NORMAL","FAIL"]
[null,null,"B",12,"2a","2b","A",20,"10a","10b","D20S1",126,60,60,"Status",4,12,59,"132/22KV TRANSFORMER 1 TAP CHANGE","TAP CHANGER ON","AUTO","MANUAL"]
[null,null,"B",12,"3a","3b","A",21,"1a","1b","D20S1",127,61,61,"Status",4,13,60,"132/22KV TRANSFORMER 1 TAP CHANGE","CONDITION","HEALTHY","NOT HEALTHY"]
[null,null,"B",12,"4a","4b","A",21,"2a","2b","D20S1",128,62,62,"Status",4,14,61,"132/22KV TRANSFORMER 1 TAP CHANGE","LOCK OUT","RESET","OPERATED"]
[null,null,"B",12,"5a","5b","A",21,"3a","3b","D20S1",129,63,63,"Status",4,15,62,"132/22KV TRANSFORMER 1 TAP CHANGE","VOLTAGE","NORMAL","ABNORMAL"]
[null,null,"B",12,"6a","6b","A",21,"4a","4b","D20S1",130,64,64,"Status",4,16,63,"132/22KV TRANSFORMER 1 TAP CHANGE","SUPPLY ","ON","OFF"]
[null,null,"B",12,"7a","7b","A",23,"1a","1b","D20S2",67,1,1,"Status",5,1,64,"132/22KV TRANSFORMER 1 TAP CHANGE","MECHANISM","ON","OFF"]
[null,null,"B",12,"8a","8b","A",23,"2a","2b","D20S2",68,2,2,"Status",5,2,65,"132/22KV TRANSFORMER 1 TAP CHANGE","SUPERVISORY","ON","OFF"]
[null,null,"B",15,"3a","3b","A",23,"3a","3b","D20S2",69,3,3,"Status",5,3,66,"22KV NETWORK BREAKER 23","RECLOSE LOCKOUT RELAY","RESET","OPERATED"]
[null,null,"B",15,"4a","4b","A",23,"4a","4b","D20S2",70,4,4,"Status",5,4,67,"22KV NETWORK BREAKER 23","SUPERVISORY","ON","OFF"]
[null,null,"B",15,"5a","5b","A",23,"5a","5b","D20S2",71,5,5,"Status",5,5,68,"22KV NETWORK BREAKER 23","PROTECTION","HEALTHY","NOT HEALTHY"]
[null,null,"B",15,"6a","6b","A",23,"6a","6b","D20S2",72,6,6,"Status",5,6,69,"22KV NETWORK BREAKER 23","SEF RELAY","ON","OFF"]
[null,null,"B",15,"7a","7b","A",23,"7a","7b","D20S2",73,7,7,"Status",5,7,70,"22KV NETWORK BREAKER 23","ARC RELAY","ON","OFF"]
[null,null,"B",15,"8a","8b","A",23,"8a","8b","D20S2",74,8,8,"Status",5,8,71,"22KV NETWORK BREAKER 23","BREAKER","HEALTHY","NOT HEALTHY"]
[null,null,"B",15,"9a","9b","A",23,"9a","9b","D20S2",75,9,9,"Status",5,9,72,"22KV NETWORK BREAKER 23","SEF TRIP","RESET","OPERATED"]
[null,null,"B",15,"10a","10b","A",23,"10a","10b","D20S2",76,10,10,"Status",5,10,73,"22KV NETWORK BREAKER 23","PROTECTION","RESET","OPERATED"]
[null,null,"B",16,"1a","1b","A",24,"1a","1b","D20S2",77,11,11,"Status",5,11,74,"22KV NETWORK BREAKER 23","TRIP CIRCUIT SUPERVISION","HEALTHY","NOT HEALTHY"]
[null,null,"B",16,"2a","2b","A",24,"2a","2b","D20S2",78,12,12,"Status",5,12,75,"22KV NETWORK BREAKER 23","VT FUSE FAIL","HEALTHY","NOT HEALTHY"]
[null,null,"B",18,"3a","3b","A",24,"3a","3b","D20S2",79,13,13,"Status",5,13,76,"22KV NETWORK BREAKER 24","RECLOSE LOCKOUT RELAY","RESET","OPERATED"]
[null,null,"B",18,"4a","4b","A",24,"4a","4b","D20S2",80,14,14,"Status",5,14,77,"22KV NETWORK BREAKER 24","SUPERVISORY","ON","OFF"]
[null,null,"B",18,"5a","5b","A",24,"5a","5b","D20S2",81,15,15,"Status",5,15,78,"22KV NETWORK BREAKER 24","PROTECTION","HEALTHY","NOT HEALTHY"]
[null,null,"B",18,"6a","6b","A",24,"6a","6b","D20S2",82,16,16,"Status",5,16,79,"22KV NETWORK BREAKER 24","SEF RELAY","ON","OFF"]
[null,null,"B",18,"7a","7b","A",24,"7a","7b","D20S2",83,17,17,"Status",6,1,80,"22KV NETWORK BREAKER 24","ARC RELAY","ON","OFF"]
[null,null,"B",18,"8a","8b","A",24,"8a","8b","D20S2",84,18,18,"Status",6,2,81,"22KV NETWORK BREAKER 24","BREAKER","HEALTHY","NOT HEALTHY"]
[null,null,"B",18,"9a","9b","A",24,"9a","9b","D20S2",85,19,19,"Status",6,3,82,"22KV NETWORK BREAKER 24","SEF TRIP","RESET","OPERATED"]
[null,null,"B",18,"10a","10b","A",24,"10a","10b","D20S2",86,20,20,"Status",6,4,83,"22KV NETWORK BREAKER 24","PROTECTION","RESET","OPERATED"]
[null,null,"B",19,"1a","1b","A",25,"1a","1b","D20S2",87,21,21,"Status",6,5,84,"22KV NETWORK BREAKER 24","TRIP CIRCUIT SUPERVISION","HEALTHY","NOT HEALTHY"]
[null,null,"B",19,"2a","2b","A",25,"2a","2b","D20S2",88,22,22,"Status",6,6,85,"22KV NETWORK BREAKER 24","VT FUSE FAIL","HEALTHY","NOT HEALTHY"]
[null,null,"B",21,"3a","3b","A",25,"3a","3b","D20S2",89,23,23,"Status",6,7,86,"22KV NETWORK BREAKER 43","RECLOSE LOCKOUT RELAY","RESET","OPERATED"]
[null,null,"B",21,"4a","4b","A",25,"4a","4b","D20S2",90,24,24,"Status",6,8,87,"22KV NETWORK BREAKER 43","SUPERVISORY","ON","OFF"]
[null,null,"B",21,"5a","5b","A",25,"5a","5b","D20S2",91,25,25,"Status",6,9,88,"22KV NETWORK BREAKER 43","PROTECTION","HEALTHY","NOT HEALTHY"]
[null,null,"B",21,"6a","6b","A",25,"6a","6b","D20S2",92,26,26,"Status",6,10,89,"22KV NETWORK BREAKER 43","SEF RELAY","ON","OFF"]
[null,null,"B",21,"7a","7b","A",25,"7a","7b","D20S2",93,27,27,"Status",6,11,90,"22KV NETWORK BREAKER 43","ARC RELAY","ON","OFF"]
[null,null,"B",21,"8a","8b","A",25,"8a","8b","D20S2",94,28,28,"Status",6,12,91,"22KV NETWORK BREAKER 43","BREAKER","HEALTHY","NOT HEALTHY"]
[null,null,"B",21,"9a","9b","A",25,"9a","9b","D20S2",95,29,29,"Status",6,13,92,"22KV NETWORK BREAKER 43","SEF TRIP","RESET","OPERATED"]
[null,null,"B",21,"10a","10b","A",25,"10a","10b","D20S2",96,30,30,"Status",6,14,93,"22KV NETWORK BREAKER 43","PROTECTION","RESET","OPERATED"]
[null,null,"B",22,"1a","1b","A",26,"1a","1b","D20S2",97,31,31,"Status",6,15,94,"22KV NETWORK BREAKER 43","TRIP CIRCUIT SUPERVISION","HEALTHY","NOT HEALTHY"]
[null,null,"B",22,"2a","2b","A",26,"2a","2b","D20S2",98,32,32,"Status",6,16,95,"22KV NETWORK BREAKER 43","VT FUSE FAIL","HEALTHY","NOT HEALTHY"]
[null,null,"B",24,"3a","3b","A",26,"3a","3b","D20S2",99,33,33,"Status",7,1,96,"22KV NETWORK BREAKER 57","RECLOSE LOCKOUT RELAY","RESET","OPERATED"]
[null,null,"B",24,"4a","4b","A",26,"4a","4b","D20S2",100,34,34,"Status",7,2,97,"22KV NETWORK BREAKER 57","SUPERVISORY","ON","OFF"]
[null,null,"B",24,"5a","5b","A",26,"5a","5b","D20S2",101,35,35,"Status",7,3,98,"22KV NETWORK BREAKER 57","PROTECTION","HEALTHY","NOT HEALTHY"]
[null,null,"B",24,"6a","6b","A",26,"6a","6b","D20S2",102,36,36,"Status",7,4,99,"22KV NETWORK BREAKER 57","SEF RELAY","ON","OFF"]
[null,null,"B",24,"7a","7b","A",26,"7a","7b","D20S2",103,37,37,"Status",7,5,100,"22KV NETWORK BREAKER 57","ARC RELAY","ON","OFF"]
[null,null,"B",24,"8a","8b","A",26,"8a","8b","D20S2",104,38,38,"Status",7,6,101,"22KV NETWORK BREAKER 57","BREAKER","HEALTHY","NOT HEALTHY"]
[null,null,"B",24,"9a","9b","A",26,"9a","9b","D20S2",105,39,39,"Status",7,7,102,"22KV NETWORK BREAKER 57","SEF TRIP","RESET","OPERATED"]
[null,null,"B",24,"10a","10b","A",26,"10a","10b","D20S2",106,40,40,"Status",7,8,103,"22KV NETWORK BREAKER 57","PROTECTION","RESET","OPERATED"]
[null,null,"B",25,"1a","1b","A",27,"1a","1b","D20S2",107,41,41,"Status",7,9,104,"22KV NETWORK BREAKER 57","TRIP CIRCUIT SUPERVISION","HEALTHY","NOT HEALTHY"]
[null,null,"B",25,"2a","2b","A",27,"2a","2b","D20S2",108,42,42,"Status",7,10,105,"22KV NETWORK BREAKER 57","VT FUSE FAIL","HEALTHY","NOT HEALTHY"]
[{"$nulls":6},"A",27,"3a","3b","D20S2",109,43,43,"Status",7,11,106,"132/22KV TRANSFORMER 2","PROTECTION","HEALTHY","NOT HEALTHY"]
[{"$nulls":6},"A",27,"4a","4b","D20S2",110,44,44,"Status",7,12,107,"132/22KV TRANSFORMER 2 TAP CHANGE","PROTECTION","HEALTHY","NOT HEALTHY"]
[null,null,"B",31,"1a","1b","A",27,"5a","5b","D20S2",111,45,45,"Status",7,13,108,"DOOR ","ALARM","CLOSED","OPENED"]
[null,null,"B",33,"1a","1b","A",27,"6a","6b","D20S2",112,46,46,"Status",7,14,109,"UNDER-FREQUENCY LOAD-SHEDDING","PROTECTION","HEALTHY","NOT HEALTHY"]
[null,null,"B",33,"2a","2b","A",27,"7a","7b","D20S2",113,47,47,"Status",7,15,110,"UNDER-FREQUENCY LOAD-SHEDDING","FREQUENCY","RESET","OPERATED"]
[null,null,"B",33,"3a","3b","A",27,"8a","8b","D20S2",114,48,48,"Status",7,16,111,"UNDER-FREQUENCY LOAD-SHEDDING","TNS ON TEST","RESET","OPERATED"]
[null,null,"B",19,"10a","10b","A",27,"9a","9b","D20S2",115,49,49,"Status",8,1,112,"22KV NETWORK BREAKER 24","SF6 GAS","NORMAL","LOW"]
[null,null,"B",16,"10a","10b","A",27,"10a","10b","D20S2",116,50,50,"Status",8,2,113,"22KV NETWORK BREAKER 23","SF6 GAS","NORMAL","LOW"]
[null,null,"B",22,"10a","10b","A",28,"1a","1b","D20S2",117,51,51,"Status",8,3,114,"22KV NETWORK BREAKER 43","SF6 GAS","NORMAL","LOW"]
[null,null,"B",25,"10a","10b","A",28,"2a","2b","D20S2",118,52,52,"Status",8,4,115,"22KV NETWORK BREAKER 57","SF6 GAS","NORMAL","LOW"]
[null,null,"B",29,"5a","5b","A",28,"3a","3b","D20S2",119,53,53,"Status",8,5,116,"110V DC BATTERY CHARGER","BATTERY FAIL","NORMAL","FAIL"]
[null,null,"B",29,"4a","4b","A",28,"4a","4b","D20S2",120,54,54,"Status",8,6,117,"110V DC BATTERY CHARGER","DC SYSTEM FAIL","NORMAL","FAIL"]
[null,null,"B",29,"3a","3b","A",28,"5a","5b","D20S2",121,55,55,"Status",8,7,118,"110V DC BATTERY CHARGER","DC SYSTEM ABNORMA:","NORMAL","ABNORMAL"]
[null,null,"B",29,"2a","2b","A",28,"6a","6b","D20S2",122,56,56,"Status",8,8,119,"110V DC BATTERY CHARGER","CHARGER FAIL","NORMAL","FAIL"]
[null,null,"B",29,"1a","1b","A",28,"7a","7b","D20S2",123,57,57,"Status",8,9,120,"110V DC BATTERY CHARGER","AC FAIL","NORMAL","FAIL"]
[null,null,"B",13,"3a","3b","A",28,"8a","8b","D20S2",124,58,58,"BCD",8,10,121,"132/22KV TRANSFORMER 1 TAP CHANGE","TAP POSITION",1]
[null,null,"B",13,"4a","4b","A",28,"9a","9b","D20S2",125,59,59,"BCD",8,11,122,"132/22KV TRANSFORMER 1 TAP CHANGE","TAP POSITION",2]
[null,null,"B",13,"5a","5b","A",28,"10a","10b","D20S2",126,60,60,"BCD",8,12,123,"132/22KV TRANSFORMER 1 TAP CHANGE","TAP POSITION",4]
[null,null,"B",13,"6a","6b","A",29,"1a","1b","D20S2",127,61,61,"BCD",8,13,124,"132/22KV TRANSFORMER 1 TAP CHANGE","TAP POSITION",8]
[null,null,"B",13,"7a","7b","A",29,"2a","2b","D20S2",128,62,62,"BCD",8,14,125,"132/22KV TRANSFORMER 1 TAP CHANGE","TAP POSITION",10]
[{"$nulls":6},"A",29,"3a","3b","D20S2",129,63,63,"Status",8,15,126,"SPARE"]
[{"$nulls":6},"A",29,"4a","4b","D20S2",130,64,64,"Status",8,16,127,"SPARE"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",9,1,128,"132/22KV TRANSFORMER 2","TRFR OIL LEVEL INDICATOR ALARM","RESET","OPERATED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",9,2,129,"132/22KV TRANSFORMER 2","MASTER TRIP","RESET","OPERATED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",9,3,130,"132/22KV TRANSFORMER 2","TRFR BUCHHOLZ TRIP","RESET","OPERATED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",9,4,131,"132/22KV TRANSFORMER 2","NECRT BUCHHOLZ/OIL TEMP TRIP","RESET","OPERATED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",9,5,132,"132/22KV TRANSFORMER 2","NEC BUCHHOLZ/OIL TEMP ALARM","RESET","OPERATED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",9,6,133,"132/22KV TRANSFORMER 2","TRFR PRESSURE RELIEF VALVE TRIP","RESET","OPERATED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",9,7,134,"132/22KV TRANSFORMER 2","TRFR OIL TEMP TRIP","RESET","OPERATED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",9,8,135,"132/22KV TRANSFORMER 2","TC BUCHHOLZ TRIP","RESET","OPERATED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",9,9,136,"132/22KV TRANSFORMER 2","TRFR OIL TEMP ALARM","RESET","OPERATED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",9,10,137,"132/22KV TRANSFORMER 2","TRFR FAN FAIL","NORMAL","FAIL"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",9,11,138,"132/22KV TRANSFORMER 2","TRFR BUCHHOLZ ALARM","RESET","OPERATED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",9,12,139,"132/22KV TRANSFORMER 2","MIB/CB HEATER FAIL","NORMAL","FAIL"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",9,13,140,"132/22KV TRANSFORMER 2","DIGITAL TEMPERATURE INSTRUMENT FAIL","NORMAL","FAIL"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",9,14,141,"132/22KV TRANSFORMER 2","TRFR OIL SUMP DRAIN VALVE OPEN","CLOSED","OPENED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",9,15,142,"132/22KV TRANSFORMER 2","TRFR WINDING TEMP ALARM","RESET","OPERATED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",9,16,143,"132/22KV TRANSFORMER 2","WINDING TEMP TRIP","RESET","OPERATED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",10,1,144,"SPARE"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",10,2,145,"SPARE"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",10,3,146,"132/22KV TRANSFORMER 2","132KV BB 1 ISOL OPEN","OPEN"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",10,4,147,"132/22KV TRANSFORMER 2","132KV BB 2 ISOL OPEN","OPEN"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",10,5,148,"132/22KV TRANSFORMER 2","132KV CB OPEN","OPEN"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",10,6,149,"132/22KV TRANSFORMER 2","132KV CB CLOSED","CLOSE"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",10,7,150,"SPARE"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",10,8,151,"SPARE"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",10,9,152,"132/22KV TRANSFORMER 2","HV CB NOT HEALTHY","HEALTHY","NOT HEALTHY"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",10,10,153,"132/22KV TRANSFORMER 2","22KV LINE ISOLATOR ","OPEN"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",10,11,154,"132/22KV TRANSFORMER 2","22KV CUSTOMER ISOLATOR ","OPEN"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",10,12,155,"132/22KV TRANSFORMER 2","22KV CB OPEN","OPEN"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",10,13,156,"132/22KV TRANSFORMER 2","22KV CB CLOSED","CLOSE"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",10,14,157,"132/22KV TRANSFORMER 2","SPARE IN320 / MV CB INTEGRAL EARTH APPLIED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",10,15,158,"132/22KV TRANSFORMER 2","SPARE IN321 / MV CB BUSBAR EARTH APPLIED"]
[null,null,"----","----","----","----","----","SERIAL PORT",null,null,"----","----","----","----","----",10,16,159,"132/22KV TRANSFORMER 2","22KV CB NOT HEALTHY","HEALTHY","NOT HEALTHY"]
[null,null,"----","----","----","----","----","SEL-487E",null,null,"----","----","----","----","----",11,1,160,"132/22KV TRANSFORMER 2","SF6 GAS LOW ALARM","NORMAL","LOW"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",11,2,161,"132/22KV TRANSFORMER 2","SPARE EXT TRIP / 132KV BUSBAR PROTECTION ","RESET","OPERATED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",11,3,162,"132/22KV TRANSFORMER 2","EXT TRIP / 22KV BUSBAR PROTECTION","RESET","OPERATED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",11,4,163,"132/22KV TRANSFORMER 2","132KV BREAKER FAIL TRIP","RESET","OPERATED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",11,5,164,"132/22KV TRANSFORMER 2","22KV BREAKER FAIL TRIP","RESET","OPERATED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",11,6,165,"132/22KV TRANSFORMER 2","TRFR DIFF TRIP","RESET","OPERATED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",11,7,166,"132/22KV TRANSFORMER 2","132KV REF TRIP","RESET","OPERATED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",11,8,167,"132/22KV TRANSFORMER 2","22KV REF TRIP","RESET","OPERATED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",11,9,168,"132/22KV TRANSFORMER 2","22KV CUSTOMER CABLE FAULT","RESET","OPERATED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",11,10,169,"132/22KV TRANSFORMER 2","SUSTAINED FAULT TIMER TRIP","RESET","OPERATED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",11,11,170,"132/22KV TRANSFORMER 2","22KV CB INDOOR CABLE CHAMBER ARC SENSOR TRIP","RESET","OPERATED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",11,12,171,"132/22KV TRANSFORMER 2","132KV OC INST TRIP","RESET","OPERATED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",11,13,172,"132/22KV TRANSFORMER 2","132KV OC IDMT TRIP","OPEN","OPEN"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",11,14,173,"132/22KV TRANSFORMER 2","132KV EF INST TRIP","RESET","OPERATED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",11,15,174,"132/22KV TRANSFORMER 2","132KV EF IDMT TRIP","RESET","OPERATED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",11,16,175,"132/22KV TRANSFORMER 2","22KV EF IDMT TRIP","RESET","OPERATED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",12,1,176,"132/22KV TRANSFORMER 2","22KV SUSTAINED EF TRIP","RESET","OPERATED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",12,2,177,"132/22KV TRANSFORMER 2","TIME DELAYED (22KV OR 132KV, OC OR EF) TRIP","RESET","OPERATED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",12,3,178,"132/22KV TRANSFORMER 2","OVERFLUX TRIP / 22KV OVER VOLTAGE TRIP/SFT","RESET","OPERATED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",12,4,179,"132/22KV TRANSFORMER 2","UNDER FREQUENCY TRIP","RESET","OPERATED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",12,5,180,"132/22KV TRANSFORMER 2","132KV VT FAIL","NORMAL","FAIL"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",12,6,181,"132/22KV TRANSFORMER 2","22KV VT FAIL","NORMAL","FAIL"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",12,7,182,"132/22KV TRANSFORMER 2","MAIN IED HARDWARE FAILURE","NORMAL","FAIL"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",12,8,183,"132/22KV TRANSFORMER 2","MAIN IED SOFTWARE FAILURE","NORMAL","FAIL"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",12,9,184,"132/22KV TRANSFORMER 2","DC SUPPLY LOW VOLTAGE ALARM","RESET","OPERATED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",12,10,185,"132/22KV TRANSFORMER 2","DC SUPPLY LOW VOLTAGE TRIP","RESET","OPERATED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",12,11,186,"132/22KV TRANSFORMER 2","132KV CB ANY TRIP CIRCUIT FAULTY","NORMAL","FAULTY"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",12,12,187,"132/22KV TRANSFORMER 2","22KV CB ANY TRIP CIRCUIT FAULTY","NORMAL","FAULTY"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",12,13,188,"132/22KV TRANSFORMER 2","132KV CB CLOSE BLOCKED","NORMAL","BLOCKED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",12,14,189,"132/22KV TRANSFORMER 2","22KV CB CLOSE BLOCKED","NORMAL","BLOCKED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",12,15,190,"132/22KV TRANSFORMER 2","SPARE CUSTOMER MASTER TRIP","RESET","OPERATED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",12,16,191,"132/22KV TRANSFORMER 2","SUPERVISORY SWITCH ISOLATED","NORMAL","ISOLATED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",13,1,192,"132/22KV TRANSFORMER 2","DNP3 IN TEST MODE","NORMAL","TEST"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",13,2,193,"132/22KV TRANSFORMER 2","PROTECTION NOT HEALTHY","HEALTHY","NOT HEALTHY"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",13,3,194,"132/22KV TRANSFORMER 2","BREAKER FAIL SWITCH ISOLATED","NORMAL","ISOLATED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",13,4,195,"132/22KV TRANSFORMER 2","MAIN DC SUPPLY FAIL","NORMAL","FAIL"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",13,5,196,"132/22KV TRANSFORMER 2","132KV / 22KV VT MCB TRIPPED","NORMAL","TRIPPED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",13,6,197,"132/22KV TRANSFORMER 2 TAP CHANGE","REG-DA RELAY","HEALTHY","NOT HEALTHY"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",13,7,198,"132/22KV TRANSFORMER 2 TAP CHANGE","TAP CHANGE SCHEME","HEALTHY","NOT HEALTHY"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",13,8,199,"132/22KV TRANSFORMER 2 TAP CHANGE","OLTC LOCK-OUT","NORMAL","LOCKED-OUT"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",13,9,200,"132/22KV TRANSFORMER 2 TAP CHANGE","VOLTAGE","NORMAL","ABNORMAL"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",13,10,201,"132/22KV TRANSFORMER 2 TAP CHANGE","OLTC DRIVE","NORMAL","TRIPPED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",13,11,202,"132/22KV TRANSFORMER 2 TAP CHANGE","OLTC ON","AUTO","MANUAL"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",13,12,203,"132/22KV TRANSFORMER 2 TAP CHANGE","OLTC MECHANISM ISOLATED","NORMAL","ISOLATED"]
[null,null,"----","----","----","----","----","SERIAL PORT",null,null,"----","----","----","----","----",13,13,204,"132/22KV TRANSFORMER 2 TAP CHANGE","SUPERVISORY","NORMAL","ISOLATED"]
[null,null,"----","----","----","----","----","REG-DA",null,null,"----","----","----","----","----",13,14,205,"132/22KV TRANSFORMER 2 TAP CHANGE","AC FAIL","NORMAL","FAIL"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",13,15,206,"132/22KV TRANSFORMER 2 TAP CHANGE","MASTER","SLAVE","MASTER"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",13,16,207,"132/22KV TRANSFORMER 2 TAP CHANGE","SLAVE","MASTER","SLAVE"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",14,1,208,"132/22KV TRANSFORMER 2 TAP CHANGE","VOLTAGE SETPOINT 1 SELECTED","NORMAL","SELECTED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",14,2,209,"132/22KV TRANSFORMER 2 TAP CHANGE","VOLTAGE SETPOINT 2 SELECTED","NORMAL","SELECTED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",14,3,210,"132/22KV TRANSFORMER 2 TAP CHANGE","VOLTAGE SETPOINT 3 SELECTED","NORMAL","SELECTED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",14,4,211,"132/22KV TRANSFORMER 2 TAP CHANGE","VOLTAGE SETPOINT 4 SELECTED","NORMAL","SELECTED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",14,5,212,"132/22KV TRANSFORMER 2 TAP CHANGE","MINIMUM TAP LIMIT","NORMAL","REACHED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",14,6,213,"132/22KV TRANSFORMER 2 TAP CHANGE","MAXIMUM TAP LIMIT","NORMAL","REACHED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",14,7,214,"22KV CAPACITOR BANK 1","CB_R- CLOSED","CLOSE= 0","OPEN = 1"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",14,8,215,"22KV CAPACITOR BANK 1","CB_W- CLOSED","CLOSE= 0","OPEN = 1"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",14,9,216,"22KV CAPACITOR BANK 1","CB_B- CLOSED","CLOSE= 0","OPEN = 1"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",14,10,217,"22KV CAPACITOR BANK 1"," Any EF_TRIP","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",14,11,218,"22KV CAPACITOR BANK 1","Breaker Fail Trip","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",14,12,219,"22KV CAPACITOR BANK 1","Any Over Voltage Trip","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",14,13,220,"22KV CAPACITOR BANK 1","Thermal Prot Operated","CLEAR","EARTHED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",14,14,221,"22KV CAPACITOR BANK 1","Cap Unbal Trip","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",14,15,222,"22KV CAPACITOR BANK 1","Any Unbalanced Alam","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",14,16,223,"22KV CAPACITOR BANK 1","Pole Disp Trip","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",15,1,224,"22KV CAPACITOR BANK 1","BusZone Trip","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",15,2,225,"22KV CAPACITOR BANK 1","External Trip","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",15,3,226,"22KV CAPACITOR BANK 1","Filter Unbalanced Trip","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",15,4,227,"22KV CAPACITOR BANK 1","Restricted Overload Trip","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",15,5,228,"22KV CAPACITOR BANK 1","Thermal Prot 2 Operated ","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",15,6,229,"22KV CAPACITOR BANK 1","TNS Not Normal","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",15,7,230,"22KV CAPACITOR BANK 1","Point of Wave","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",15,8,231,"22KV CAPACITOR BANK 1","Supervisory Isolated","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",15,9,232,"22KV CAPACITOR BANK 1","Main1 DC Fail","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",15,10,233,"22KV CAPACITOR BANK 1","CB Unhealthy","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",15,11,234,"22KV CAPACITOR BANK 1","AC Fail","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",15,12,235,"22KV CAPACITOR BANK 1","Closing DC Fail","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",15,13,236,"22KV CAPACITOR BANK 1","Spring Rewind DC Fail","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",15,14,237,"22KV CAPACITOR BANK 1","Motorised Isolator DC Fail","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",15,15,238,"22KV CAPACITOR BANK 1","Secure Supply DC Fail","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",15,16,239,"22KV CAPACITOR BANK 1","Control DC Fail","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",16,1,240,"22KV CAPACITOR BANK 1","Indication DC Fail","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",16,2,241,"22KV CAPACITOR BANK 1","Circuit Breaker  OFF Remote","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",16,3,242,"22KV CAPACITOR BANK 1","CB SF6 Low","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",16,4,243,"22KV CAPACITOR BANK 1","CB SF6 Inhibit","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",16,5,244,"22KV CAPACITOR BANK 1","Magbolt Installed","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","SERIAL PORT",null,null,"----","----","----","----","----",16,6,245,"22KV CAPACITOR BANK 1","REF Trip","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","C60",null,null,"----","----","----","----","----",16,7,246,"22KV CAPACITOR BANK 1","Discharge Timer Active","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",16,8,247,"22KV CAPACITOR BANK 1","R- Trip Coil Supervision Fail","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",16,9,248,"22KV CAPACITOR BANK 1","W- Trip Coil Supervision Fail","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",16,10,249,"22KV CAPACITOR BANK 1","B- Trip Coil Supervision Fail","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",16,11,250,"22KV CAPACITOR BANK 1","Any Trip","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",16,12,251,"22KV CAPACITOR BANK 1","Protection Not Healthy","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",16,13,252,"22KV CAPACITOR BANK 1","Any Overcurrent Trip","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",16,14,253,"22KV CAPACITOR BANK 1","AVR ON","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",16,15,254,"22KV CAPACITOR BANK 1","Protection Not Healthy","HEALTHY","NOT HEALTHY"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",16,16,255,"22KV CAPACITOR BANK 2","CB_R- CLOSED","CLOSE= 0","OPEN = 1"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",17,1,256,"22KV CAPACITOR BANK 2","CB_W- CLOSED","CLOSE= 0","OPEN = 1"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",17,2,257,"22KV CAPACITOR BANK 2","CB_B- CLOSED","CLOSE= 0","OPEN = 1"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",17,3,258,"22KV CAPACITOR BANK 2"," Any EF_TRIP","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",17,4,259,"22KV CAPACITOR BANK 2","Breaker Fail Trip","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",17,5,260,"22KV CAPACITOR BANK 2","Any Over Voltage Trip","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",17,6,261,"22KV CAPACITOR BANK 2","Thermal Prot Operated","CLEAR","EARTHED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",17,7,262,"22KV CAPACITOR BANK 2","Cap Unbal Trip","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",17,8,263,"22KV CAPACITOR BANK 2","Any Unbalanced Alam","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",17,9,264,"22KV CAPACITOR BANK 2","Pole Disp Trip","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",17,10,265,"22KV CAPACITOR BANK 2","BusZone Trip","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",17,11,266,"22KV CAPACITOR BANK 2","External Trip","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",17,12,267,"22KV CAPACITOR BANK 2","Filter Unbalanced Trip","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",17,13,268,"22KV CAPACITOR BANK 2","Restricted Overload Trip","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",17,14,269,"22KV CAPACITOR BANK 2","Thermal Prot 2 Operated ","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",17,15,270,"22KV CAPACITOR BANK 2","TNS Not Normal","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","SERIAL PORT",null,null,"----","----","----","----","----",17,16,271,"22KV CAPACITOR BANK 2","Point of Wave","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","C60",null,null,"----","----","----","----","----",18,1,272,"22KV CAPACITOR BANK 2","Supervisory Isolated","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",18,2,273,"22KV CAPACITOR BANK 2","Main1 DC Fail","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",18,3,274,"22KV CAPACITOR BANK 2","CB Unhealthy","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",18,4,275,"22KV CAPACITOR BANK 2","AC Fail","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",18,5,276,"22KV CAPACITOR BANK 2","Closing DC Fail","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",18,6,277,"22KV CAPACITOR BANK 2","Spring Rewind DC Fail","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",18,7,278,"22KV CAPACITOR BANK 2","Motorised Isolator DC Fail","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",18,8,279,"22KV CAPACITOR BANK 2","Secure Supply DC Fail","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",18,9,280,"22KV CAPACITOR BANK 2","Control DC Fail","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",18,10,281,"22KV CAPACITOR BANK 2","Indication DC Fail","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",18,11,282,"22KV CAPACITOR BANK 2","Circuit Breaker  OFF Remote","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",18,12,283,"22KV CAPACITOR BANK 2","CB SF6 Low","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",18,13,284,"22KV CAPACITOR BANK 2","CB SF6 Inhibit","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",18,14,285,"22KV CAPACITOR BANK 2","Magbolt Installed","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",18,15,286,"22KV CAPACITOR BANK 2","REF Trip","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",18,16,287,"22KV CAPACITOR BANK 2","Discharge Timer Active","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",19,1,288,"22KV CAPACITOR BANK 2","R- Trip Coil Supervision Fail","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",19,2,289,"22KV CAPACITOR BANK 2","W- Trip Coil Supervision Fail","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",19,3,290,"22KV CAPACITOR BANK 2","B- Trip Coil Supervision Fail","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",19,4,291,"22KV CAPACITOR BANK 2","Any Trip","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",19,5,292,"22KV CAPACITOR BANK 2","Protection Not Healthy","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",19,6,293,"22KV CAPACITOR BANK 2","Any Overcurrent Trip","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",19,7,294,"22KV CAPACITOR BANK 2","AVR ON","CLEAR","SUSTAINED"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----","----",19,8,295,"22KV CAPACITOR BANK 2","Protection Not Healthy","HEALTHY","NOT HEALTHY"]

{"sheet":"D20 Controls","index":2,"n_rows":101,"n_cols":21,"rows_kept":101,"merged":[[4,2,4,3],[5,2,5,3],[6,2,6,9],[6,10,6,13],[7,2,7,5],[7,6,7,9],[74,8,74,10],[75,8,75,10],[82,8,82,10],[83,8,83,10],[90,8,90,10],[91,8,91,10],[96,8,96,10],[97,8,97,10]],"flags":["formulas_cached_only"]}
[]
[]
[{"$nulls":8},"TELECONTROL FUNCTION ALLOCATION AND WIRING RECORDS"]
[{"$nulls":9},"CONTROL OUTPUTS"]
[null,null,"STATION :",null,"MAKHATINI"]
[null,null,"ADDRESS :",null,7221]
[null,null,"I . D . F .",{"$nulls":7},"D20 RACK",{"$nulls":3},"Master Stn Address","D20 CONFIGURATION / MASTER STATION",{"$nulls":3},"TESTED TO","TESTED TO"]
[null,null,"PROTECTION",{"$nulls":3},"TELECONTROL",{"$nulls":12},"PROTECTION","SCADA"]
[null,null,"Vert","Block","-","+","Vert","Block","-","+","CARD #","-","+","Bit Type ",null,"DESCRIPTION "," CONTROL NAME","STATE '0'","STATE '1'"]
[null,null,"B",2,"1a","1b","A",7,"1a","1b","D20K 1","Cmn",4,"Trip",0,"132KV NONDABOYA ","132KV BREAKER","OPEN"]
[null,null,"B",2,"2a","2b","A",7,"2a","2b","D20K 1","Cmn",57,"Close",0,"132KV NONDABOYA ","132KV BREAKER","CLOSE"]
[null,null,"B",2,"3a","3b","A",7,"3a","3b","D20K 1","Cmn",58,"Trip",1,"132KV NONDABOYA ","132KV BREAKER","ARC ON"]
[null,null,"B",2,"4a","4b","A",7,"4a","4b","D20K 1","Cmn",6,"Close",1,"132KV NONDABOYA ","132KV BREAKER","ARC OFF"]
[null,null,"B",8,"2a","2b","A",7,"5a","5b","D20K 1","Cmn",7,"Trip",2,"132/22KV TRANSFORMER 1","132KV BREAKER","OPEN"]
[null,null,"B",8,"3a","3b","A",7,"6a","6b","D20K 1","Cmn",60,"Close",2,"132/22KV TRANSFORMER 1","132KV BREAKER","CLOSE"]
[null,null,"B",8,"4a","4b","A",7,"7a","7b","D20K 1","Cmn",61,"Trip",3,"132/22KV TRANSFORMER 1","22KV BREAKER","OPEN"]
[null,null,"B",8,"5a","5b","A",7,"8a","8b","D20K 1","Cmn",9,"Close",3,"132/22KV TRANSFORMER 1","22KV BREAKER","CLOSE"]
[null,null,"B",12,"9a","9b","A",7,"9a","9b","D20K 1","Cmn",10,"Trip",4,"132/22KV TRANSFORMER 1 TAP CHANGE","TAP CHANGE","AUTO"]
[null,null,"B",12,"10a","10b","A",7,"10a","10b","D20K 1","Cmn",63,"Close",4,"132/22KV TRANSFORMER 1 TAP CHANGE","TAP CHANGE","MANUAL"]
[null,null,"B",13,"1a","1b","A",8,"1a","1b","D20K 1","Cmn",64,"Trip",5,"132/22KV TRANSFORMER 1 TAP CHANGE","TAP CHANGE","RAISE"]
[null,null,"B",13,"2a","2b","A",8,"2a","2b","D20K 1","Cmn",12,"Close",5,"132/22KV TRANSFORMER 1 TAP CHANGE","TAP CHANGE","LOWER"]
[null,null,"B",16,"4a","4b","A",8,"3a","3b","D20K 1","Cmn",13,"Trip",6,"22KV NETWORK BREAKER 23","22KV BREAKER","OPEN"]
[null,null,"B",16,"5a","5b","A",8,"4a","4b","D20K 1","Cmn",66,"Close",6,"22KV NETWORK BREAKER 23","22KV BREAKER","CLOSE"]
[null,null,"B",16,"6a","6b","A",8,"5a","5b","D20K 1","Cmn",67,"Trip",7,"22KV NETWORK BREAKER 23","22KV BREAKER","ARC ON"]
[null,null,"B",16,"7a","7b","A",8,"6a","6b","D20K 1","Cmn",15,"Close",7,"22KV NETWORK BREAKER 23","22KV BREAKER","ARC OFF"]
[null,null,"B",16,"8a","8b","A",8,"7a","7b","D20K 1","Cmn",16,"Trip",8,"22KV NETWORK BREAKER 23","22KV BREAKER","SEF ON"]
[null,null,"B",16,"9a","9b","A",8,"8a","8b","D20K 1","Cmn",69,"Close",8,"22KV NETWORK BREAKER 23","22KV BREAKER","SEF OFF"]
[null,null,"B",19,"4a","4b","A",8,"9a","9b","D20K 1","Cmn",70,"Trip",9,"22KV NETWORK BREAKER 24","22KV BREAKER","OPEN"]
[null,null,"B",19,"5a","5b","A",8,"10a","10b","D20K 1","Cmn",18,"Close",9,"22KV NETWORK BREAKER 24","22KV BREAKER","CLOSE"]
[null,null,"B",19,"6a","6b","A",9,"1a","1b","D20K 1","Cmn",19,"Trip",10,"22KV NETWORK BREAKER 24","22KV BREAKER","ARC ON"]
[null,null,"B",19,"7a","7b","A",9,"2a","2b","D20K 1","Cmn",72,"Close",10,"22KV NETWORK BREAKER 24","22KV BREAKER","ARC OFF"]
[null,null,"B",19,"8a","8b","A",9,"3a","3b","D20K 1","Cmn",73,"Trip",11,"22KV NETWORK BREAKER 24","22KV BREAKER","SEF ON"]
[null,null,"B",19,"9a","9b","A",9,"4a","4b","D20K 1","Cmn",21,"Close",11,"22KV NETWORK BREAKER 24","22KV BREAKER","SEF OFF"]
[null,null,"B",22,"4a","4b","A",9,"5a","5b","D20K 1","Cmn",22,"Trip",12,"22KV NETWORK BREAKER 43","22KV BREAKER","OPEN"]
[null,null,"B",22,"5a","5b","A",9,"6a","6b","D20K 1","Cmn",75,"Close",12,"22KV NETWORK BREAKER 43","22KV BREAKER","CLOSE"]
[null,null,"B",22,"6a","6b","A",9,"7a","7b","D20K 1","Cmn",76,"Trip",13,"22KV NETWORK BREAKER 43","22KV BREAKER","ARC ON"]
[null,null,"B",22,"7a","7b","A",9,"8a","8b","D20K 1","Cmn",24,"Close",13,"22KV NETWORK BREAKER 43","22KV BREAKER","ARC OFF"]
[null,null,"B",22,"8a","8b","A",9,"9a","9b","D20K 1","Cmn",25,"Trip",14,"22KV NETWORK BREAKER 43","22KV BREAKER","SEF ON"]
[null,null,"B",22,"9a","9b","A",9,"10a","10b","D20K 1","Cmn",78,"Close",14,"22KV NETWORK BREAKER 43","22KV BREAKER","SEF OFF"]
[null,null,"B",25,"4a","4b","A",10,"1a","1b","D20K 1","Cmn",79,"Trip",15,"22KV NETWORK BREAKER 57","22KV BREAKER","OPEN"]
[null,null,"B",25,"5a","5b","A",10,"2a","2b","D20K 1","Cmn",27,"Close",15,"22KV NETWORK BREAKER 57","22KV BREAKER","CLOSE"]
[null,null,"B",25,"6a","6b","A",10,"3a","3b","D20K 1","Cmn",28,"Trip",16,"22KV NETWORK BREAKER 57","22KV BREAKER","ARC ON"]
[null,null,"B",25,"7a","7b","A",10,"4a","4b","D20K 1","Cmn",81,"Close",16,"22KV NETWORK BREAKER 57","22KV BREAKER","ARC OFF"]
[null,null,"B",25,"8a","8b","A",10,"5a","5b","D20K 1","Cmn",82,"Trip",17,"22KV NETWORK BREAKER 57","22KV BREAKER","SEF ON"]
[null,null,"B",25,"9a","9b","A",10,"6a","6b","D20K 1","Cmn",30,"Close",17,"22KV NETWORK BREAKER 57","22KV BREAKER","SEF OFF"]
[{"$nulls":6},"A",10,"7a","7b","D20K 1","Cmn",31,"Trip",18,"SPARE"]
[{"$nulls":6},"A",10,"8a","8b","D20K 1","Cmn",84,"Close",18,"SPARE"]
[{"$nulls":6},"A",10,"9a","9b","D20K 1","Cmn",85,"Trip",19,"SPARE"]
[{"$nulls":6},"A",10,"10a","10b","D20K 1","Cmn",33,"Close",19,"SPARE"]
[{"$nulls":6},"A",11,"1a","1b","D20K 1","Cmn",34,"Trip",20,"SPARE"]
[{"$nulls":6},"A",11,"2a","2b","D20K 1","Cmn",87,"Close",20,"SPARE"]
[{"$nulls":6},"A",11,"3a","3b","D20K 1","Cmn",88,"Trip",21,"SPARE"]
[{"$nulls":6},"A",11,"4a","4b","D20K 1","Cmn",36,"Close",21,"SPARE"]
[{"$nulls":6},"A",11,"5a","5b","D20K 1","Cmn",37,"Trip",22,"SPARE"]
[{"$nulls":6},"A",11,"6a","6b","D20K 1","Cmn",90,"Close",22,"SPARE"]
[{"$nulls":6},"A",11,"7a","7b","D20K 1","Cmn",91,"Trip",23,"SPARE"]
[{"$nulls":6},"A",11,"8a","8b","D20K 1","Cmn",39,"Close",23,"SPARE"]
[{"$nulls":6},"A",11,"9a","9b","D20K 1","Cmn",40,"Trip",24,"SPARE"]
[{"$nulls":6},"A",11,"10a","10b","D20K 1","Cmn",93,"Close",24,"SPARE"]
[{"$nulls":6},"A",12,"1a","1b","D20K 1","Cmn",94,"Trip",25,"SPARE"]
[{"$nulls":6},"A",12,"2a","2b","D20K 1","Cmn",42,"Close",25,"SPARE"]
[{"$nulls":6},"A",12,"3a","3b","D20K 1","Cmn",43,"Trip",26,"SPARE"]
[{"$nulls":6},"A",12,"4a","4b","D20K 1","Cmn",96,"Close",26,"SPARE"]
[{"$nulls":6},"A",12,"5a","5b","D20K 1","Cmn",97,"Trip",27,"SPARE"]
[{"$nulls":6},"A",12,"6a","6b","D20K 1","Cmn",45,"Close",27,"SPARE"]
[{"$nulls":6},"A",12,"7a","7b","D20K 1","Cmn",46,"Trip",28,"SPARE"]
[{"$nulls":6},"A",12,"8a","8b","D20K 1","Cmn",99,"Close",28,"SPARE"]
[{"$nulls":6},"A",12,"9a","9b","D20K 1","Cmn",100,"Trip",29,"SPARE"]
[{"$nulls":6},"A",12,"10a","10b","D20K 1","Cmn",48,"Close",29,"SPARE"]
[{"$nulls":6},"A",13,"1a","1b","D20K 1","Cmn",49,"Trip",30,"SPARE"]
[{"$nulls":6},"A",13,"2a","2b","D20K 1","Cmn",102,"Close",30,"SPARE"]
[{"$nulls":6},"A",13,"3a","3b","D20K 1","Cmn",103,"Trip",31,"SPARE"]
[{"$nulls":6},"A",13,"4a","4b","D20K 1","Cmn",51,"Close",31,"SPARE"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----",32,"132/22KV TRANSFORMER 2","132KV BREAKER","OPEN"]
[null,null,"----","----","----","----","----","----","SERIAL PORT",null,null,"----","----","----",32,"132/22KV TRANSFORMER 2","132KV BREAKER","CLOSE"]
[null,null,"----","----","----","----","----","----","SEL-487E",null,null,"----","----","----",33,"132/22KV TRANSFORMER 2","11KV BREAKER","OPEN"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----",33,"132/22KV TRANSFORMER 2","11KV BREAKER","CLOSE"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----",34,"132/22KV TRANSFORMER 2 TAP CHANGE","TAP CHANGE","MANUAL"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----",34,"132/22KV TRANSFORMER 2 TAP CHANGE","TAP CHANGE","AUTO"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----",35,"132/22KV TRANSFORMER 2 TAP CHANGE","TAP CHANGE","LOWER"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----",35,"132/22KV TRANSFORMER 2 TAP CHANGE","TAP CHANGE","RAISE"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----",36,"SPARE"]
[null,null,"----","----","----","----","----","----","SERIAL PORT",null,null,"----","----","----",36,"132/22KV TRANSFORMER 2 TAP CHANGE","TAP CHANGE","SETPOINT 1"]
[null,null,"----","----","----","----","----","----","REG-DA",null,null,"----","----","----",37,"SPARE"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----",37,"132/22KV TRANSFORMER 2 TAP CHANGE","TAP CHANGE","SETPOINT 2"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----",38,"SPARE"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----",38,"132/22KV TRANSFORMER 2 TAP CHANGE","TAP CHANGE","SETPOINT 3"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----",39,"SPARE"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----",39,"132/22KV TRANSFORMER 2 TAP CHANGE","TAP CHANGE","SETPOINT 4"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----",40,"22KV CAPACITOR BANK 1","CB_OPEN ","OPEN"]
[null,null,"----","----","----","----","----","----","SERIAL PORT",null,null,"----","----","----",40,"22KV CAPACITOR BANK 1","CB_ CLOSE","CLOSE"]
[null,null,"----","----","----","----","----","----","C60",null,null,"----","----","----",41,"22KV CAPACITOR BANK 1","BB 1 Isolator  OPEN","OPEN"]
[null,null,"----","----","----","----","----","----",{"$nulls":3},"----","----","----",41,"22KV CAPACITOR BANK 1","BB 1 Isolator CLOSE","CLOSE"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----",42,"22KV CAPACITOR BANK 1","AVR ON","OPEN"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----",42,"22KV CAPACITOR BANK 1","AVR OFF","CLOSE"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----",43,"22KV CAPACITOR BANK 2","CB_OPEN ","OPEN"]
[null,null,"----","----","----","----","----","----","SERIAL PORT",null,null,"----","----","----",43,"22KV CAPACITOR BANK 2","CB_ CLOSE","CLOSE"]
[null,null,"----","----","----","----","----","----","C60",null,null,"----","----","----",44,"22KV CAPACITOR BANK 2","BB 1 Isolator  OPEN","OPEN"]
[null,null,"----","----","----","----","----","----",{"$nulls":3},"----","----","----",44,"22KV CAPACITOR BANK 2","BB 1 Isolator CLOSE","CLOSE"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----",45,"22KV CAPACITOR BANK 2","AVR ON","OPEN"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----",45,"22KV CAPACITOR BANK 2","AVR OFF","CLOSE"]

{"sheet":"D20 Analogues","index":3,"n_rows":64,"n_cols":21,"rows_kept":64,"merged":[[4,2,4,3],[5,2,5,3],[6,2,6,9],[6,10,6,15],[6,16,6,17],[7,2,7,5],[7,6,7,9],[7,16,7,17],[8,16,8,17],[21,3,21,6],[46,7,46,9],[47,7,47,9],[54,7,54,9],[55,7,55,9],[61,7,61,9],[62,7,62,9]],"flags":["formulas_cached_only"]}
[]
[]
[{"$nulls":8},"TELECONTROL FUNCTION ALLOCATION AND WIRING RECORDS"]
[{"$nulls":9},"ANALOGUE INPUTS"]
[null,null,"STATION :",null,"MAKHATINI"]
[null,null,"ADDRESS :",null,7221]
[null,null,"I . D . F .",{"$nulls":7},"D20 RACK",{"$nulls":5},"D20 CONFIGURATION / MASTER STATION"]
[null,null,"PROTECTION",{"$nulls":3},"TELECONTROL",{"$nulls":12},"TESTED TO ","TESTED TO"]
[null,null,"Vert","Block","+","-","Vert","Block","+","-","CARD #","+","-","A/I #","Address (Master Stn)","SCADA Ratio ","DESCRIPTION ",null,"ANALOGUE","PROTECTION","SCADA"]
[null,null,"B",4,"10a","10b","A",2,"1a","1b","D20A 1",1,51,1,0,null,"132KV BUSBAR ","VOLTS","VOLTS"]
[null,null,"B",10,"5a","5b","A",2,"2a","2b","D20A 1",3,53,2,1,null,"22KV BUSBAR ","VOLTS","VOLTS"]
[null,null,"B",4,"7a","7b","A",2,"3a","3b","D20A 1",4,54,3,2,null,"132KV NONDABOYA","MW","MW"]
[null,null,"B",4,"8a","8b","A",2,"4a","4b","D20A 1",6,56,4,3,null,"132KV NONDABOYA","MVAr","MVAr"]
[null,null,"B",4,"9a","9b","A",2,"5a","5b","D20A 1",7,57,5,4,null,"132KV NONDABOYA","AMPS","AMPS"]
[null,null,"B",10,"2a","2b","A",2,"6a","6b","D20A 1",9,59,6,5,null,"132/22KV TRANSFORMER 1","MW","MW"]
[null,null,"B",10,"3a","3b","A",2,"7a","7b","D20A 1",10,60,7,6,null,"132/22KV TRANSFORMER 1","MVAr","MVAr"]
[null,null,"B",10,"4a","4b","A",2,"8a","8b","D20A 1",12,62,8,7,null,"132/22KV TRANSFORMER 1","AMPS","AMPS"]
[null,null,"B",16,"3a","3b","A",2,"9a","9b","D20A 1",13,63,9,8,null,"22KV NETWORK BREAKER 23","AMPS","AMPS"]
[null,null,"B",19,"3a","3b","A",2,"10a","10b","D20A 1",15,65,10,9,null,"22KV NETWORK BREAKER 24","AMPS","AMPS"]
[null,null,"B",22,"3a","3b","A",3,"1a","1b","D20A 1",16,66,11,10,null,"22KV NETWORK BREAKER 43","AMPS","AMPS"]
[null,null,"B",25,"3a","3b","A",3,"2a","2b","D20A 1",18,68,12,11,null,"22KV NETWORK BREAKER 57","AMPS","AMPS"]
[null,null,"----","PSEUDO ANALOGUE",{"$nulls":3},"----","----","----","----","----","----",13,12,"1 : 1","132/22KV TRANSFORMER 1 TAP CHANGE","POSITION","POSITION"]
[{"$nulls":6},"A",3,"3a","3b","D20A 1",19,69,14,13]
[{"$nulls":6},"A",3,"4a","4b","D20A 1",21,71,15,14]
[{"$nulls":6},"A",3,"5a","5b","D20A 1",22,72,16,15]
[{"$nulls":6},"A",3,"6a","6b","D20A 1",24,74,17,16]
[{"$nulls":6},"A",3,"7a","7b","D20A 1",25,75,18,17]
[{"$nulls":6},"A",3,"8a","8b","D20A 1",27,77,19,18]
[{"$nulls":6},"A",4,"9a","9b","D20A 1",28,78,20,19]
[{"$nulls":6},"A",4,"10a","10b","D20A 1",30,80,21,20]
[{"$nulls":6},"A",4,"1a","1b","D20A 1",31,81,22,21]
[{"$nulls":6},"A",4,"2a","2b","D20A 1",33,83,23,22]
[{"$nulls":6},"A",4,"3a","3b","D20A 1",34,84,24,23]
[{"$nulls":6},"A",4,"4a","4b","D20A 1",36,86,25,24]
[{"$nulls":6},"A",4,"5a","5b","D20A 1",37,87,26,25]
[{"$nulls":6},"A",4,"6a","6b","D20A 1",39,89,27,26]
[{"$nulls":6},"A",4,"7a","7b","D20A 1",40,90,28,27]
[{"$nulls":6},"A",4,"8a","8b","D20A 1",42,92,29,28]
[{"$nulls":6},"A",5,"9a","9b","D20A 1",43,93,30,29]
[{"$nulls":6},"A",5,"10a","10b","D20A 1",45,95,31,30]
[{"$nulls":6},"A",5,"1a","1b","D20A 1",46,96,32,31]
[{"$nulls":6},"A",5,"2a","2b","D20A 1",48,98,33,32]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----",33,null,"132/22KV TRANSFORMER 2","HV WHITE PHASE CURRENT","AMPS"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----",34,null,"132/22KV TRANSFORMER 2","HV RED-WHITE PHASE VOLTAGE","kVOLTS"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----",35,null,"132/22KV TRANSFORMER 2","HV 3-PHASE ACTIVE POWER","MW"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----",36,null,"132/22KV TRANSFORMER 2","HV 3-PHASE REACTIVE POWER","MVAr"]
[null,null,"----","----","----","----","----","SERIAL PORT",null,null,"----","----","----","----",37,null,"132/22KV TRANSFORMER 2","HV 3-PHASE APPARENT POWER","MVA"]
[null,null,"----","----","----","----","----","SEL-487E",null,null,"----","----","----","----",38,null,"132/22KV TRANSFORMER 2","MV WHITE PHASE CURRENT","AMPS"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----",39,null,"132/22KV TRANSFORMER 2","MV RED-WHITE PHASE VOLTAGE","kVOLTS"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----",40,null,"132/22KV TRANSFORMER 2","MV 3-PHASE ACTIVE POWER","MW"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----",41,null,"132/22KV TRANSFORMER 2","MV 3-PHASE REACTIVE POWER","MVAr"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----",42,null,"132/22KV TRANSFORMER 2","MV 3-PHASE APPARENT POWER","MVA"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----",43,null,"132/22KV TRANSFORMER 2","FREQUENCY","HERTZ"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----",44,null,"132/22KV TRANSFORMER 2 TAP CHANGE","POSITION","POSITION"]
[null,null,"----","----","----","----","----","SERIAL PORT",null,null,"----","----","----","----",45,null,"132/22KV TRANSFORMER 2 TAP CHANGE","NUMBER OF TAP OPERATIONS UNDER LOAD","NUMBER"]
[null,null,"----","----","----","----","----","REG-DA",null,null,"----","----","----","----",46,null,"132/22KV TRANSFORMER 2 TAP CHANGE","TOTAL NUMBER OF TAP OPERATIONS","NUMBER"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----",47,null,"132/22KV TRANSFORMER 2 TAP CHANGE","MV VOLTAGE (SECONDARY VOLATGE)","VOLTS"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----",48,null,"22kV CAPACITOR BANK 1","BREAKER","AMPS"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----",49,null,"22kV CAPACITOR BANK 1","BREAKER","kVOLTS"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----",50,null,"22kV CAPACITOR BANK 1","BREAKER","MW"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----",51,null,"22kV CAPACITOR BANK 1","BREAKER","MVAr"]
[null,null,"----","----","----","----","----","SERIAL PORT",null,null,"----","----","----","----",52,null,"22kV CAPACITOR BANK 1","BREAKER","MVA"]
[null,null,"----","----","----","----","----","C60",null,null,"----","----","----","----",53,null,"22kV CAPACITOR BANK 1","BREAKER","HZ"]
[null,null,"----","----","----","----","----","----","----","----","----","----","----","----",54,null,"22kV CAPACITOR BANK 1","BREAKER","Pf"]

{"sheet":"Revision History","index":4,"n_rows":8,"n_cols":5,"rows_kept":8,"flags":["formulas_cached_only"]}
[]
[null,"MAKHATINI","Revision History"]
[]
[null,"Date of Change","Reason for Change","Changed By","REV #"]
[]
[null,"April 17, 2019","Changed/Created format for D20, added extra battery charger alarms.","RC du Plessis","Rev 0"]
[null,"October 07, 2019","Updated IDF Protection position after Cutover","Brian Shabalala","Rev 1"]
[null,"2022-10-07","Updated for 2 x Cap Bank schemes -Provisional","Aroon Sukhnandan","Rev 1a"]

{"sheet":"C.T. & V.T.","index":5,"n_rows":12,"n_cols":5,"rows_kept":12,"merged":[[2,2,2,4]],"flags":["formulas_cached_only"]}
[]
[]
[null,null,"C. T. AND V. T. VALUES"]
[]
[null,null,"PROTECTION PANEL","CT","VT"]
[null,null,"132KV NONDABUYA","?00 / 1","132 000 / 1"]
[null,null,"132/22KV TRANSFORMER 1","?00 / 1","132_22 000 / 1"]
[null,null,"22KV NETWORK BREAKER 23","?00 / 1","22 000 / 1"]
[null,null,"22KV NETWORK BREAKER 24","?00 / 1","22 000 / 1"]
[null,null,"22KV NETWORK BREAKER 43","?00 / 1","22 000 / 1"]
[null,null,"22KV NETWORK BREAKER 57","?00 / 1","22 000 / 1"]
[null,null,"132/22KV TRANSFORMER 2","?00 / 1","132_22 000 / 1"]