| PART A REQUEST FOR REQUEST FOR INFORMATION (RFI) |  |  |  |
| --- | --- | --- | --- |
| Description of the works/goods/services | Gariep Power Station was initially commissioned in 1971 and some of the original supplied and installed valves are either obsolete or an exact like-for-like replacement is not available. Information is thus required in terms of current locally available Globe Valves in the market that is similar in design and fit for purpose. The current valve body and flanges are forged steel and welded. The flanges are not fully standard, thus the expectation is not to receive a valve that will be 100% the same, but to get an understanding of what can be supplied, even if it means to change the connecting/existing flanges on site to accommodate a new valve. Current Installed Valve Information: - Drawing: - The Valve drawing will be made available to the suppliers upon receipt of their RFI response and signing of a NDA. RFI response to be based on the information below. - Valve: - Type: Globe valve - Connection: Flanged globe valve - Purpose: Isolating valve in hydraulic oil system - Operated: Manually operated by handwheel - Trim: Bonnet/Disc - Style: Bolted Bonnet - Flange Type: SF-F BS10 Table H; Male-Female Flanges; Socket Type Welded Flange; Female Recess located on Valve Flange, while Male raised portion is located on existing site pipe flange. - Valve Dimensions - Nominal Size: 1 inch (25 mm) - Flange Specification: SF-F BS10 Table H - Outer Diameter of Flange (Ø): 120.6 mm - Flanges Face to Face Length: 180 mm - Flange Bolt Hole Circle Diameter/ PCD (Ø): 87,3 mm - Diameter of Bolts (Ø): 16 mm - Number of Bolt Holes: 4 mm - Diameter of Bolt Holes in Flange (Ø): 17,5 mm - Thickness of Flange: 19 mm - Female Recess Depth: 4 mm - Female Recess Diameter (Ø): 45 mm - Shut Overall Height/Length: 275 mm - Handwheel Diameter (Ø): 140 mm - Valve Material: - Valve Body: Forged Steel (SF 45) - Body Flange Material: Forged Steel (SF 45) - Gland: SS 41 - Gland Packing: Type JIS BS2403V - Gland Nut: SS41 - Lock Nut: SS41 - Handwheel: FC 20 - Packing Ring: SS41 - Bonnet: S25C - Stem: SUS403 - Disc Stem Ring: SUS420J2 - Disc: SUS420J2 - Seat Ring: SUS403 - Design Rating/Parameters: - Fluid Medium: Hydraulic Oil & Air - Design Pressure: 2,892 MPa (28,92 bar) - Hydraulic Testing Pressure: 4,338 MPa (43,38 bar) - System Temperature: 5 to 50 ˚C |  |  |
| Deadline for submission | 28 May 2025 | At (South African Standard Time) | 10H00 SATS |
| Tender Office address | Response to the RFI to be submitted online via Eskom E Tender Portal: https://www.eskom.co.za/tenders/ Note to Suppliers: Refer to E-Tendering Help Manual for instruction on how to register on Eskom Tender Bulletin. |  |  |

Eskom Holdings SOC Ltd (“Eskom”) invites you to submit an:

- Request for information (RFI) to submit information for the goods as stated in the table. This RFI is a stand-alone information-gathering and market-testing exercise, intended only to inform and assist Eskom’s further deliberation and development of a strategy for the Procurement of V6 Globe Valve for Gariep Hydro Power Station, Peaking Operating Unit.  Eskom may request indicative prices if so, stated in this RFI.

| Name | Designation | Signature | Date |
| --- | --- | --- | --- |
| Kim Hughes | Officer Procurement |  | 2025/04/30 |
| Telephone number | 021 550 4819 | E-mail address | Hughesk@eskom.co.za |

Eskom has delegated the responsibility for this RFI to the signatory of this document, whose details can be found below.

We look forward to receipt of your response.

Yours faithfully

| PART B RESPONSE SHEET IN TERMS OF A REQUEST FOR INFORMATION To be completed by the supplier |  |  |  |  |
| --- | --- | --- | --- | --- |
| To | Eskom Holdings SOC Ltd | Date |  | [insert today’s date] |
| Attention | Kim Hughes |  |  |  |
| Tel no | [insert your tel number] | E-mail address | [insert your e-mail address] |  |
| From | [insert the registered full legal name of the company] | Address | [insert the business address of the company] |  |
| Address | insert the physical address of the company] |  |  |  |
| Sender | [insert the full name of the sender at the company] |  |  |  |
| Description of the works/goods/services | [insert a description of the works as per part A] |  |  |  |

Please find below our response to Eskom’s questions:

| No. | Question | Please indicate your response in this column |
| --- | --- | --- |
| 1. | [your contact name and contact details] |  |
| 2. | [Company registration number] |  |
| 3. | [brief description of previous experience and Description of the solution that you can offer] |  |
| 4. | Indicative prices (optional and only for use of RFI’s) |  |
| 5. | [ Add applicable questions] |  |

Yours faithfully

| Name | Designation | Signature | Date |
| --- | --- | --- | --- |
| [insert your full name/s] | [Insert your full designation] |  |  |
| Telephone number |  | Fax and/or e-mail address |  |