{"text_format":"3","workbook":"xls","n_sheets":9,"sheets":["Pre-amble","Preliminaries","Compliance","IT Server Room","Summary","Basement - 2","Basement - 1","Ground Floor ","First Floor "],"not_rendered":{"external_links":1,"defined_names":5},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Pre-amble","index":0,"n_rows":18,"n_cols":6,"rows_kept":18,"flags":["formulas_cached_only"]}
[]
["No","Description","Unit","Qty","Rate","Amount"]
[null," "]
[null,{"$error":"#REF!"}]
[null," "]
[null,"AIR CONDITIONING PRE-AMBLE"]
[]
[null,"This BOQ is to be read inconjuction with specification document "]
[]
[null,"Where trades names are used, it shall be read to include the phrase \"or approved equal\"."]
[]
[null,"Installation and Commissioning of air conditioning units and ducting must include for all hangers, support, condensate drains and trunking"]
[]
[null,"\"Rate\" includes material, mark-up & installation labour."]
[]
[null,"All breaking and making good of building & door openings due to equipment penetrations shall be allowed for including transformations from & to fan, louvers, grills, diffusers, etc."]
[]
[null,"All items on the Bill are re-measurable"]

{"sheet":"Preliminaries","index":1,"n_rows":42,"n_cols":6,"rows_kept":42,"flags":["formulas_cached_only"]}
[]
["No","Description",null,"Qty","Rate","Amount"]
[null," "]
["B","IT SERVER ROOM - PRELIMINARY AND GENERAL"]
[]
[null,"Note: All items shall be priced for whatever cost may be consider necessary for Preliminary and General to carry out the Mechanical Installations in full, as detailed in the drawings, Specifications and Schedules, which shall include, but shall not be limited, to the following:"]
[]
["B1","Site establishment-over and above the main contractors including the removal thereof upon completion","Item",1]
[]
["B2","Company Head Office overhead costs","Item",1]
[]
["B3","Programming of work inline with the main contractor's construction programme","Item",1]
[]
["B4","Workshop drawings and equipment submittals","Item",1]
[]
["B5","Project engineering and management including coordination with other services on site","Item",1]
[]
["B6","Instructing and training the Employer's staff in operation of system and equipment prior to hand over to the Client.","Item",1]
[null," "]
["B7","Three copies of the O&M Manuals (hard copies and USB)","Item",1]
[]
["B8","As-Built Drawings (3 copies)","Item",1]
[null," "]
["B9","Any necessary calculations requested by the Engineer.","Item",1]
["B10","12 month guarantee period","Item",1]
[]
["B11","Provision of full maintenance and guarantee of mechanical equipment and installation for the full 12 month period. The maintenance period shall start after practical completion is achieved.  Service sheets to be submitted for every service carried out.  Refer to tender specification.","Item",1]
{"$rows_empty":14}
[null,"SUBTOTAL CARRIED FORWARD TO SUMMARY",{"$nulls":3},{"v":0,"d":"R 0.00"}]

{"sheet":"Compliance","index":2,"n_rows":49,"n_cols":6,"rows_kept":49,"flags":["formulas_cached_only"]}
[]
["No","Description",null,"Qty","Rate","Amount"]
[null," "]
["C","IT SERVER ROOM - COMPLIANCE"]
[]
[null,"Note: All items shall be priced for whatever cost may be consider necessary for Compliance to carry out the Mechanical Installations in full, as detailed in the drawings, Specifications and Schedules, which shall include, but shall not be limited, to the following:"]
[]
["C1","Compliance with OHS Regulations (latest version) and Site Specific Health & Safety Specification","Item",1]
[]
["C2","Clearing of rubble and housekeeping","Item",1]
[]
["C3","Scaffolding","Item",1]
[]
["C4","Protection of Equipment against damage during construction","Item",1]
[]
["C5","Transport and delivery","Item",1]
[]
["C6","Rigging and crane hire","Item",1]
[]
["C7","Provision of spare parts and all related accessories as per specification","Item",1]
[]
["C8","Builders work as required","Item",1]
[]
["C9","Electrical work as required","Item",1]
[]
["C10","Workshop drawings","Item",1]
[]
["C11","Testing, balancing, commissioning and handing over in full working order of entire HVAC system(s).","Item",1]
{"$rows_empty":20}
[null,"SUBTOTAL CARRIED FORWARD TO SUMMARY",{"$nulls":3},{"v":0,"d":"R 0.00"}]

{"sheet":"IT Server Room","index":3,"n_rows":46,"n_cols":6,"rows_kept":46,"flags":["formulas_cached_only"]}
["No","Description",null,"Qty","Rate","Amount"]
["D","IT SERVER ROOM"]
[]
[null,"Air-Conditioning "]
[]
["D1","DX type Inverter Split Unit"]
[]
[null,"Supply, deliver and install a DX type inverter split unit complete with indoor and outdoor unit including interconnecting piping and cabling between indoor and outdoor unit, filters, mounting brackets, condensate drain pumps, decorative panels  and all necessary accessories."]
[]
["D1.1","AC-01 - IT SERVER ROOM","No",4]
[null,"Type: Under Ceiling split unit Inverter Heat Pump"]
[null,"Cooling Capacity: 14.5 KW"]
[null,"Heating capacity: 14.8 KW"]
[null,"Size: 48000 BTU"]
[null,"Controller: Hard Wired "]
[null,"Condensate drain pump: Yes "]
[]
["D1.2","Supply and install wired wall mounted remote controller with temperature display, temperature set point, 3 fan speeds, heat/cool mode and ON/OFF functions.","No",4]
[]
["D1.3","20mm Diameter galvanised conduit for control wiring chased in wall  ","m",20]
[]
["D1.4","32mm Diameter uPVC drain piping including running joints, fittings, clamps and supports","m",20]
[]
["D1.5","300mm wide cable tray for wiring and refrigerant piping including installation, complete with 41mm galvanised unistrut type channel and 10mm galvanised threaded rods.","m",20]
[]
["D1.6","100mm wide x 50mm high PVC trunking c/w cover for cabling and refrigerant piping between Indoor and outdoor unit running on the outside wall.  Trunking to be painted to match background wall and include all installation ancillaries ","m",6]
[]
["D1.7","Decommissioning and removal of blow-down units. Complete with outdoor units, fans, ducting and all pipework. Areas to be made good and material to be disposed of.","Item",2]
[]
["D1.8","Supply temperature sensor and display for entire server room to be displayed outside the room in the corridor.","No",1]
[]
["D1.9","Drip trays to be gravity fed complete with condensate piping, mounting and all anciliary components.","No",4]
[]
["D1.10","AC-02 - UPS ROOM","No",1]
[null,"Type: Under Ceiling split unit Inverter Heat Pump"]
[null,"Cooling Capacity: 10.5 KW"]
[null,"Heating capacity: 10.8 KW"]
[null,"Size: 36000 BTU"]
[null,"Controller: Hard Wired "]
[null,"Condensate drain pump: Yes "]
[]
["D1.11","Decommissioning and removal of split units in UPS and Server room. Complete with outdoor units and all pipework. Areas to be made good and material to be disposed of.","Item",2]
[]
[]
[]
[null,"SUBTOTAL CARRIED FORWARD TO SUMMARY",{"$nulls":3},{"v":0,"d":"R 0.00"}]

{"sheet":"Summary","index":4,"n_rows":70,"n_cols":6,"rows_kept":70,"flags":["formulas_cached_only"]}
["No","Description",{"$nulls":3},"Amount"]
[]
[null,"AIR CONDITIONING "]
[]
["A","IT SERVER ROOM - SUMMARY"]
[]
["B","IT Server Room - Preliminary and General",{"$nulls":3},{"v":0,"d":"R 0.00"}]
[]
["C","IT Server Room - Compliance",{"$nulls":3},{"v":0,"d":"R 0.00"}]
[]
["D","IT Server Room",{"$nulls":3},{"v":0,"d":"R 0.00"}]
{"$rows_empty":54}
[null,"TOTAL",{"$nulls":3},{"v":0,"d":"R 0.00"}]
[]
[null,"ADD VAT (15%)",{"$nulls":3},{"v":0,"d":"R 0.00"}]
[]
[null,"GRAND TOTAL",{"$nulls":3},{"v":0,"d":"R 0.00"}]

{"sheet":"Basement - 2","index":5,"n_rows":115,"n_cols":6,"rows_kept":115,"hidden":true,"flags":["formulas_cached_only"]}
["No","Description","Unit","Qty","Rate","Amount"]
["G","HVAC - Basement - 2"]
[]
[null,"Air-Conditioning "]
[]
["G1","DX type Inverter Split Unit (Guard House)"]
[]
[null,"Supply, deliver and install a mid-wall split air conditioning unit complete with indoor and outdoor unit. Including decorative panel, piping between indoor and outdoor portion of unit, mounting brackets, condensate drain pumps and all necessary accessories."]
[]
["G1.2","Brand: Midea, LG, Daikin, Samsung or similar approved ","No",1]
[null,"Type: Midwall, Cassette, Hide-away, Under-ceiling"]
[null,"Cooling Capacity: (BTU or KW)"]
[null,"Heating capacity: (BTU or KW)"]
[null,"Reverse Cycle, cooling only, heating only "]
[null,"Refrigerant: "]
[null,"Inverter Type, Non-Inverter type "]
[null,"Controller: Wired or Wireless"]
[]
["G1.2","Supply and install wired wall mounted remote controller with temperature display, temperature set point, 3 fan speeds, heat/cool mode and ON/OFF functions.","No",1]
[]
["G1.3","Apply anti-corrosion treatment on all the condenser coils (Bluchem or equally approved). Certificate of treatment to be submitted to the design engineer. (Rate per split unit)","No",1]
[]
["G1.4","Additional Piping between Indoor and Outdoor unit including pipe ancillaries, wire mesh tray, pipe supports and installation ancillaries","m",1]
[]
["G2","Extraction System "]
[]
[null,"Supply, deliver and install the following items:"]
[]
["G2.1","Extract Fan (Waste Area)","No",1]
[null,"Fan Type: In-line Axial Fan, Centrifugal Fan, Wall Mounted "]
[null,"Fan Make: ………...or equal and approved"]
[null,"Fan Size: …….diameter or ….x….."]
[null,"Process Data: Airflow (L/s) @ Pressure"]
[null,"Rotational Speed: ……….rpm"]
[null,"Mounting: Anti-Vibration Mounts, Ceiling/Wall mounting kit "]
[null,"Motor Size: (KW)"]
[]
["G2.2","Sound Attenuator","No",2]
[null,"Diameter to suit fan, with flexible collars"]
[null,"Length: 600L, 900L"]
[null,"POD type"]
[null,"NC rating: 35"]
[]
["G2.3","Weather Louver","No",1]
[null,"Make: ………...or equal and approved"]
[null,"Model:  ………...or equal and approved"]
[null,"Size: "]
[null,"Finish: Epoxy Powder Coated or Aluminium Anodised"]
[null,"Hinged with Washable pleated Filter"]
{"$rows_empty":7}
[null,"TOTAL CARRIED FORWARD"]
[]
["No","Description","Unit","Qty","Rate","Amount"]
[null," "]
[null,"TOTAL BROUGHT DOWN"]
[]
["G2.4","Extract Air Grille","No",1]
[null,"Make: "]
[null,"Type: Egg Crate, disc valve"]
[null,"Size: "]
[null,"Finish: Epoxy Powder Coated, Aluminium Anodised or Standard colour to Arch's specification."]
[null,"Opposed Blade Damper (OBD): Y/N"]
[]
["G2.5","Door Grille","No",1]
[null,"Make: "]
[null,"Size: "]
[null,"Finish: Epoxy Powder Coated, Aluminium Anodised or Standard colour to Arch's specification."]
[]
["G2.6","Control Box for fan to switch on when lights are operational, position can be in service shaft, weather proof box with cabling and ancillaries or 24/7 timer","No",1]
[]
["G2.7","Ducting"]
[null,"Low Pressure Galvanised ducting including flexible connections, transformation pieces, bends, shoe pieces, spogots, stop ends and all duct fittings to SANS 1238, \"S\" slip & Drive Slip, 0.6mm ","Sqm"]
[null,"Category 1"]
[]
["G2.8","Flexible Duct"]
[null,"Supply and install wire reinforced aluminium flexible ducting complete with clamps; duct sealant and fixings. 1 500 long","No",1]
[null,"Diameter: "]
[]
["G2.9","Balancing Damper "]
[null,"Balancing Damper to suit duct, manual type, made of sheet metal","No",1]
[null,"Size: "]
[]
["G2.10","Fire Damper "]
[null,"2 hour fire rated Fire Damper with Fusible Link or motorised ","No",1]
[null,"Size: "]
[]
["G2.11","Extract Fan (Guard house toilet)","No",1]
[null,"Fan Type: Ceiling Mounted "]
[null,"Fan Make: ………...or equal and approved"]
[null,"Fan Size: …….diameter or ….x….."]
[null,"Process Data: Airflow (L/s) @ Pressure"]
[null,"Rotational Speed: ……….rpm"]
[null,"Mounting: Anti-Vibration Mounts, Ceiling/Wall mounting kit "]
[null,"Motor Size: (KW)"]
[]
["G2.12","Door Grille","No",1]
[null,"Make: "]
[null,"Size: "]
[null,"Finish: Epoxy Powder Coated, Aluminium Anodised or Standard colour to Arch's specification."]
[]
["G2.13","Control Box for fan to switch on when lights are operational","No",1]
{"$rows_empty":7}
[null,"SUBTOTAL CARRIED FORWARD TO SUMMARY"]

{"sheet":"Basement - 1","index":6,"n_rows":166,"n_cols":6,"rows_kept":166,"hidden":true,"flags":["formulas_cached_only"]}
["No","Description",null,"Qty","Rate","Amount"]
["H","HVAC - Basement - 1"]
[]
[null,"Air-Conditioning "]
[]
["H1","DX type Inverter Split Unit"]
[]
[null,"Supply, deliver and install a DX type inverter split unit complete with indoor and outdoor unit including piping between indoor and outdoor portion of unit, mounting brackets, condensate drain pumps and all necessary accessories."]
[]
["H1.2","Brand: Midea, LG, Daikin, Samsung or similar approved ","No",1]
[null,"Type: Hide-away (DV Retail Area)"]
[null,"Cooling Capacity: (BTU or KW)"]
[null,"Heating capacity: (BTU or KW)"]
[null,"Reverse Cycle, cooling only, heating only "]
[null,"Refrigerant: "]
[null,"Inverter Type, Non-Inverter type "]
[null,"Controller: Wired or Wireless"]
[]
["H1.3","Brand: Midea, LG, Daikin, Samsung or similar approved ","No",1]
[null,"Type: Cassette c/w decorative panel (BOH/Receiving/Office)"]
[null,"Cooling Capacity: (BTU or KW)"]
[null,"Heating capacity: (BTU or KW)"]
[null,"Reverse Cycle, cooling only, heating only "]
[null,"Refrigerant: "]
[null,"Inverter Type, Non-Inverter type "]
[null,"Controller: Wired or Wireless"]
[]
["H1.4","Supply and install wired wall mounted remote controller with temperature display, temperature set point, 3 fan speeds, heat/cool mode and ON/OFF functions.","No",2]
[]
["H1.5","Apply anti-corrosion treatment on all the condenser coils (Bluchem or equally approved). Certificate of treatment to be submitted to the design engineer. (Rate per split unit)","No",2]
[]
["H1.6","Additional Piping between Indoor and Outdoor unit including pipe ancillaries, wire mesh tray, pipe supports and installation ancillaries","m",1]
[]
["H2","Basement Parking Ventilation System"]
[]
[null,"Supply, deliver and install the following items:"]
[]
["H2.1","Ventilation Fan ","No",1]
[null,"Fan Type: In-line Axial Fan, Centrifugal Fan, Wall Mounted "]
[null,"Fan Make: ………...or equal and approved"]
[null,"Fan Size: …….diameter or ….x….."]
[null,"Process Data: Airflow (L/s) @ Pressure"]
[null,"Rotational Speed: ……….rpm"]
[null,"Mounting: Anti-Vibration Mounts, Ceiling/Wall mounting kit "]
[null,"Motor Size: (KW)"]
[]
["H2.2","Sound Attenuator","No",2]
[null,"Diameter to suit fan, with flexible collars"]
[null,"Length: 600L, 900L"]
[null,"POD type"]
[null,"NC rating: 35"]
[]
[]
[]
[]
[]
[]
[null,"TOTAL CARRIED FORWARD"]
[]
["No","Description","Unit","Qty","Rate","Amount"]
[null," "]
[null,"TOTAL BROUGHT DOWN"]
[]
["H2.3","Weather Louver","No",1]
[null,"Make: ………...or equal and approved"]
[null,"Model:  ………...or equal and approved"]
[null,"Size: "]
[null,"Finish: Epoxy Powder Coated or Aluminium Anodised"]
[null,"Hinged with Washable pleated Filter"]
[]
["H2.4","Control Box for fan to switch on when lights are operational, position can be in service shaft, weather proof box with cabling and ancillaries or 24/7 timer","No",1]
[]
["H2.5","Ducting"]
[null,"Low Pressure Galvanised ducting including all transformation pieces (including all brackets and supports) to SANS 1238, \"S\" slip & Drive Slip, 0,6mm ","Sqm"]
[null,"Category 1"]
[]
["H2.6","Inlet Cone"]
[null,"Supply and install fan inlet cone complete with bird proof wire mesh screen.","No",1]
[null,"Size: "]
[]
["H3","Alignment & Fitment Ventilation System"]
[]
[null,"Supply, deliver and install the following items:"]
[]
["H3.1","Ventilation Fan ","No",1]
[null,"Fan Type: In-line Axial Fan, Centrifugal Fan, Wall Mounted "]
[null,"Fan Make: ………...or equal and approved"]
[null,"Fan Size: …….diameter or ….x….."]
[null,"Process Data: Airflow (L/s) @ Pressure"]
[null,"Rotational Speed: ……….rpm"]
[null,"Mounting: Anti-Vibration Mounts, Ceiling/Wall mounting kit "]
[null,"Motor Size: (KW)"]
[]
["H3.2","Sound Attenuator","No",2]
[null,"Diameter to suit fan, with flexible collars"]
[null,"Length: 600L, 900L"]
[null,"POD type"]
[null,"NC rating: 35"]
[]
["H3.3","Weather Louver","No",1]
[null,"Make: ………...or equal and approved"]
[null,"Model:  ………...or equal and approved"]
[null,"Size: "]
[null,"Finish: Epoxy Powder Coated or Aluminium Anodised"]
[null,"Hinged with Washable pleated Filter"]
[]
["H3.4","Control Box for fan to switch on when lights are operational, position can be in service shaft, weather proof box with cabling and ancillaries or 24/7 timer","No",1]
[]
["H3.5","Ducting"]
[null,"Low Pressure Galvanised ducting including all transformation pieces (including all brackets and supports) to SANS 1238, \"S\" slip & Drive Slip, 0,6mm ","Sqm"]
[null,"Category 1"]
[]
[]
[]
[]
[null,"TOTAL CARRIED FORWARD"]
[]
["No","Description","Unit","Qty","Rate","Amount"]
[null," "]
[null,"TOTAL BROUGHT DOWN"]
[]
["H3.6","Inlet Cone"]
[null,"Supply and install fan inlet cone complete with bird proof wire mesh screen.","No",1]
[null,"Size: "]
[]
["H4","Extraction System (Storage)"]
[]
[null,"Supply, deliver and install the following items:"]
[]
["H4.1","Extraction Fan ","No",1]
[null,"Fan Type: Wall Mounted "]
[null,"Fan Make: ………...or equal and approved"]
[null,"Fan Size: …….diameter or ….x….."]
[null,"Process Data: Airflow (L/s) @ Pressure"]
[null,"Rotational Speed: ……….rpm"]
[null,"Mounting: Anti-Vibration Mounts, Ceiling/Wall mounting kit "]
[null,"Motor Size: (KW)"]
[]
["H4.2","Door Grille","No",1]
[null,"Make: "]
[null,"Size: "]
[null,"Finish: Epoxy Powder Coated, Aluminium Anodised or Standard colour to Arch's specification."]
[]
["H4.3","Control Box for fan to switch on when lights are operational.","No",1]
{"$rows_empty":21}
[null,"SUBTOTAL CARRIED FORWARD TO SUMMARY",{"$nulls":3},{"v":0,"d":"R 0.00"}]

{"sheet":"Ground Floor ","index":7,"n_rows":176,"n_cols":6,"rows_kept":176,"hidden":true,"flags":["formulas_cached_only"]}
["No","Description","Unit","Qty","Rate","Amount"]
["I","HVAC - Ground Floor "]
[]
["I1","Air-Conditioning "]
[]
["I1.1","Shop G002"]
[]
[null,"Chilled Water Fan-Coil Units (Hide-aways)"]
[]
[null,"Supply, installation and commissioning of high efficiency fan coil unit with, 2-pipe finned coil to provide cooling and electrical elements to provide electric heating as specified below c/w high efficiency EC fans and alluminium or copper air cooled fins."]
[]
[null,"Supply complete with solenoid valves, instrumentation, electrical equipment, wall mounted and fan coil mounted controller. Control to be integratable with BMS (by others) using Modbus, allowing the BMS operator to switch unit on/off, adjust set-point, and mode, and also to record fault signals"]
[]
["I1.1.1","Brand: Aermec, Trane, Sinko or similar approved","No",1]
[null,"Type: Hide-away "]
[null,"Cooling Capacity:    KW (Total)       KW (Sensible)"]
[null,"Heating capacity:    KW (Electric heating)"]
[null,"Supply airflow:     L/s (or better)"]
[]
["I1.1.2","Ducting - Un-insulated"]
[null,"Low Pressure Galvanised ducting including flexible connections, transformation pieces, bends, shoe pieces, spogots, stop ends and all duct fittings to SANS 1238, \"S\" slip & Drive Slip, 0.6mm ","Sqm"]
[null,"Category 1"]
[]
["I1.1.3","External duct insulation to SANS 10173, 25mm thick thermal insulation with aluminium foil vapour barrier (FRK)","Sqm"]
[]
["I1.1.4","Balancing Damper "]
[null,"Balancing Damper to suit duct, manual type, made of sheet metal","No",1]
[null,"Size: "]
[]
["I1.1.5","Flexible Duct - Externally insulated"]
[null,"Supply and install wire reinforced aluminium flexible ducting complete with clamps; duct sealant and fixings. 1 500mm long","No",1]
[null,"Diameter: "]
[]
["I1.1.6","Diffuser","No",1]
[null,"Brand:   or similar approved"]
[null,"Plenum or Collar"]
[null,"Size: "]
[null,"Finish: Epoxy Powder Coated or Standard colour"]
[]
["I1.1.7","Return Air Grille","No",1]
[null,"Make: "]
[null,"Type: Egg Crate, disc valve"]
[null,"Size: "]
[null,"Finish: Epoxy Powder Coated, Aluminium Anodised or Standard colour to Arch's specification."]
[null,"Opposed Blade Damper (OBD): Y/N"]
[null,"Return Air Filter Frame (RAFF): Y/N"]
[]
[]
[]
[]
[]
[null,"TOTAL CARRIED FORWARD"]
[]
["No","Description","Unit","Qty","Rate","Amount"]
[null," "]
[null,"TOTAL BROUGHT DOWN"]
[]
["I1.1.8","Insulated Condensate Drain","m",1]
[null,"Supply and install P-trapped uPVC drain piping including running joints, fittings, clamps, supports and connection to nearest drain point."]
[null,"Diameter: "]
[]
["I1.1.9","Stainless Steel Drip Tray","No",1]
[null,"Supply and install thermally insulated stainelss steel drip tray for the catment of any condensate from the valves."]
[null,"Size: "]
{"$rows_empty":11}
["I2","Extraction System "]
[]
[null,"Supply, deliver and install the following items:"]
[]
["I2.1","Extract Fan (Ablutions)","No",1]
[null,"Fan Type: In-line Axial Fan, Centrifugal Fan, Wall Mounted "]
[null,"Fan Make: ………...or equal and approved"]
[null,"Fan Size: …….diameter or ….x….."]
[null,"Process Data: Airflow (L/s) @ Pressure"]
[null,"Rotational Speed: ……….rpm"]
[null,"Mounting: Anti-Vibration Mounts, Ceiling/Wall mounting kit "]
[null,"Motor Size: (KW)"]
[]
["I2.2","Sound Attenuator","No",2]
[null,"Diameter to suit fan, with flexible collars"]
[null,"Length: 600L, 900L"]
[null,"POD type"]
[null,"NC rating: 35"]
[]
["I2.3","Weather Louver","No",1]
[null,"Make: ………...or equal and approved"]
[null,"Model:  ………...or equal and approved"]
[null,"Size: "]
[null,"Finish: Epoxy Powder Coated or Aluminium Anodised"]
[null,"Hinged with Washable pleated Filter"]
[]
["I2.4","Disc valves"]
[null,"Type: Extract air "]
[null,"Finish: Epoxy Powder Coated or Standard colour"]
[null,"Neck size: 100 mm dia","No",1]
[null,"Neck size: 150 mm dia","No",1]
[null,"Neck size: 200 mm dia","No",1]
[]
["I2.5","Door Grille","No",1]
[null,"Make: "]
[null,"Size: "]
[null,"Finish: Epoxy Powder Coated, Aluminium Anodised or Standard colour to Arch's specification."]
[]
[]
[]
[null,"TOTAL CARRIED FORWARD"]
[]
["No","Description","Unit","Qty","Rate","Amount"]
[null," "]
[null,"TOTAL BROUGHT DOWN"]
[]
["I2.6","Control Box for fan to switch on when lights are operational located in serrvice shaft or 24/7 timer.","No",1]
[]
["I2.7","Ducting"]
[null,"Low Pressure Galvanised ducting including flexible connections, transformation pieces, bends, shoe pieces, spogots, stop ends and all duct fittings to SANS 1238, \"S\" slip & Drive Slip, 0.6mm ","Sqm"]
[null,"Category 1"]
[]
["I2.8","Flexible Duct"]
[null,"Supply and install wire reinforced aluminium flexible ducting complete with clamps; duct sealant and fixings. 1 500 long","No",1]
[null,"Diameter: "]
[]
["I2.9","Balancing Damper "]
[null,"Balancing Damper to suit duct, manual type, made of sheet metal","No",1]
[null,"Size: "]
[]
["I2.10","Fire Damper "]
[null,"2 hour fire rated Fire Damper with Fusible Link or motorised ","No",1]
[null,"Size: "]
[]
["I3","Tempered Fresh Air System or Fans"]
{"$rows_empty":35}
[null,"SUBTOTAL CARRIED FORWARD TO SUMMARY",{"$nulls":3},{"v":0,"d":"R 0.00"}]

{"sheet":"First Floor ","index":8,"n_rows":158,"n_cols":6,"rows_kept":158,"hidden":true,"flags":["formulas_cached_only"]}
["No","Description","Unit","Qty","Rate","Amount"]
["J","HVAC - First Floor "]
[]
["J1","Air-Conditioning "]
[]
["J1.1","Shop F001"]
[]
[null,"Chilled Water Fan-Coil Units (Hide-aways)"]
[]
[null,"Supply, installation and commissioning of high efficiency fan coil unit with, 2-pipe finned coil to provide cooling and electrical elements to provide electric heating as specified below c/w high efficiency EC fans and alluminium or copper air cooled fins."]
[]
[null,"Supply complete with solenoid valves, instrumentation, electrical equipment, wall mounted and fan coil mounted controller. Control to be integratable with BMS (by others) using Modbus, allowing the BMS operator to switch unit on/off, adjust set-point, and mode, and also to record fault signals"]
[]
["J1.1.1","Brand: Aermec, Trane, Sinko or similar approved","No",1]
[null,"Type: Hide-away "]
[null,"Cooling Capacity:    KW (Total)       KW (Sensible)"]
[null,"Heating capacity:    KW (Electric heating)"]
[null,"Supply airflow:     L/s (or better)"]
[]
["J1.1.2","Ducting - Un-insulated"]
[null,"Low Pressure Galvanised ducting including flexible connections, transformation pieces, bends, shoe pieces, spogots, stop ends and all duct fittings to SANS 1238, \"S\" slip & Drive Slip, 0.6mm ","Sqm"]
[null,"Category 1"]
[]
["J1.1.3","External duct insulation to SANS 10173, 25mm thick thermal insulation with aluminium foil vapour barrier (FRK)","Sqm"]
[]
["J1.1.4","Balancing Damper "]
[null,"Balancing Damper to suit duct, manual type, made of sheet metal","No",1]
[null,"Size: "]
[]
["J1.1.5","Flexible Duct - Externally insulated"]
[null,"Supply and install wire reinforced aluminium flexible ducting complete with clamps; duct sealant and fixings. 1 500mm long","No",1]
[null,"Diameter: "]
[]
["J1.1.6","Diffuser","No",1]
[null,"Brand:   or similar approved"]
[null,"Plenum or Collar"]
[null,"Size: "]
[null,"Finish: Epoxy Powder Coated or Standard colour"]
[]
["J1.1.7","Return Air Grille","No",1]
[null,"Make: "]
[null,"Type: Egg Crate, disc valve"]
[null,"Size: "]
[null,"Finish: Epoxy Powder Coated, Aluminium Anodised or Standard colour to Arch's specification."]
[null,"Opposed Blade Damper (OBD): Y/N"]
[null,"Return Air Filter Frame (RAFF): Y/N"]
[]
[]
[]
[null,"TOTAL CARRIED FORWARD"]
[]
["No","Description","Unit","Qty","Rate","Amount"]
[null," "]
[null,"TOTAL BROUGHT DOWN"]
[]
["J1.1.8","Condensate Drain","m",1]
[null,"Supply and install P-trapped uPVC drain piping including running joints, fittings, clamps, supports and connection to nearest drain point."]
[null,"Diameter: "]
[]
["J1.1.9","Stainless Steel Drip Tray","No",1]
[null,"Supply and install thermally insulated stainelss steel drip tray for the catment of any condensate from the valves."]
[null,"Size: "]
[]
["J1.2","Shop F002"]
{"$rows_empty":7}
["J2","Extraction System "]
[]
[null,"Supply, deliver and install the following items:"]
[]
["J2.1","Extract Fan (Ablutions)","No",1]
[null,"Fan Type: In-line Axial Fan, Centrifugal Fan, Wall Mounted "]
[null,"Fan Make: ………...or equal and approved"]
[null,"Fan Size: …….diameter or ….x….."]
[null,"Process Data: Airflow (L/s) @ Pressure"]
[null,"Rotational Speed: ……….rpm"]
[null,"Mounting: Anti-Vibration Mounts, Ceiling/Wall mounting kit "]
[null,"Motor Size: (KW)"]
[]
["J2.2","Sound Attenuator","No",2]
[null,"Diameter to suit fan, with flexible collars"]
[null,"Length: 600L, 900L"]
[null,"POD type"]
[null,"NC rating: 35"]
[]
["J2.3","Weather Louver","No",1]
[null,"Make: ………...or equal and approved"]
[null,"Model:  ………...or equal and approved"]
[null,"Size: "]
[null,"Finish: Epoxy Powder Coated or Aluminium Anodised"]
[null,"Hinged with Washable pleated Filter"]
[]
["J2.4","Disc valves"]
[null,"Type: Extract air "]
[null,"Finish: Epoxy Powder Coated or Standard colour"]
[null,"Neck size: 100 mm dia","No",1]
[null,"Neck size: 150 mm dia","No",1]
[null,"Neck size: 200 mm dia","No",1]
[]
["J2.5","Door Grille","No",1]
[null,"Make: "]
[null,"Size: "]
[null,"Finish: Epoxy Powder Coated, Aluminium Anodised or Standard colour to Arch's specification."]
[]
[]
[]
[null,"TOTAL CARRIED FORWARD"]
[]
["No","Description","Unit","Qty","Rate","Amount"]
[null," "]
[null,"TOTAL BROUGHT DOWN"]
[]
["J2.6","Control Box for fan to switch on when lights are operational located in serrvice shaft or 24/7 timer.","No",1]
[]
["J2.7","Ducting"]
[null,"Low Pressure Galvanised ducting including flexible connections, transformation pieces, bends, shoe pieces, spogots, stop ends and all duct fittings to SANS 1238, \"S\" slip & Drive Slip, 0.6mm ","Sqm"]
[null,"Category 1"]
[]
["J2.8","Flexible Duct"]
[null,"Supply and install wire reinforced aluminium flexible ducting complete with clamps; duct sealant and fixings. 1 500 long","No",1]
[null,"Diameter: "]
[]
["J2.9","Balancing Damper "]
[null,"Balancing Damper to suit duct, manual type, made of sheet metal","No",1]
[null,"Size: "]
[]
["J2.10","Fire Damper "]
[null,"2 hour fire rated Fire Damper with Fusible Link or motorised ","No",1]
[null,"Size: "]
[]
["J3","Tempered Fresh Air System or Fans"]
{"$rows_empty":21}
[null,"SUBTOTAL CARRIED FORWARD TO SUMMARY",{"$nulls":3},{"v":0,"d":"R 0.00"}]