{"text_format":"3","workbook":"xls","n_sheets":10,"sheets":["Cover Page ","Pre-amble","Summary","Preliminaries","Compliance","Humidifiers","Basement - 2","Basement - 1","Ground Floor ","First Floor "],"not_rendered":{"images":1,"external_links":1,"defined_names":5},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Cover Page ","index":0,"n_rows":47,"n_cols":5,"rows_kept":47,"merged":[[42,0,42,1],[43,0,43,1],[45,1,45,2],[46,1,46,2],[47,1,47,2],[48,1,48,2],[49,1,49,2]],"flags":["formulas_cached_only"]}
{"$rows_empty":30}
["PROJECT: ",null,"SABS HVAC - Humidifiers"]
["DOCUMENT NAME: ",null,"Mechanical BOQ"]
{"$rows_empty":7}
["The following signatories have approved the report:"]
[]
["Name",null,"Purpose","Signature","Date"]
["Cornelis van Hoeve",null,"Generated"]
["Fannie Raseruthe",null,"Checked"]
[]
["Rev","Description",null,"Author","Pages"]
["A","Issued for Tender",null,"CvH","All"]

{"sheet":"Pre-amble","index":1,"n_rows":18,"n_cols":6,"rows_kept":18,"flags":["formulas_cached_only"]}
[]
["No","Description","Unit","Qty","Rate","Amount"]
[null," "]
[null,0]
[null," "]
[null,"HUMIDIFIERS PRE-AMBLE"]
[]
[null,"This BOQ is to be read inconjuction with specification document "]
[]
[null,"Where trades names are used, it shall be read to include the phrase \"or approved equal\"."]
[]
[null,"Installation and Commissioning Of humidifier units and ducting must include for all hangers, support, condensate drains and trunking"]
[]
[null,"\"Rate\" includes material, mark-up & installation labour."]
[]
[null,"All breaking and making good of building & door openings due to equipment penetrations shall be allowed for including transformations from & to fan, louvers, grills, diffusers, etc."]
[]
[null,"All items on the Bill are re-measurable"]

{"sheet":"Summary","index":2,"n_rows":36,"n_cols":6,"rows_kept":36,"flags":["formulas_cached_only"]}
["No","Description",{"$nulls":3},"Amount"]
[]
[null,"HUMIDIFIERS"]
[]
["A","SUMMARY"]
[]
["B","Preliminary and General",{"$nulls":3},{"v":0,"d":"R 0.00"}]
[]
["C","Compliance",{"$nulls":3},{"v":0,"d":"R 0.00"}]
[]
["D","Humidifiers",{"$nulls":3},{"v":100000,"d":"R 100,000.00"}]
{"$rows_empty":20}
[null,"TOTAL",{"$nulls":3},{"v":100000,"d":"R 100,000.00"}]
[]
[null,"ADD VAT (15%)",{"$nulls":3},{"v":15000,"d":"R 15,000.00"}]
[]
[null,"GRAND TOTAL",{"$nulls":3},{"v":115000,"d":"R 115,000.00"}]

{"sheet":"Preliminaries","index":3,"n_rows":39,"n_cols":6,"rows_kept":39,"flags":["formulas_cached_only"]}
[]
["No","Description",null,"Qty","Rate","Amount"]
[null," "]
["B","PRELIMINARY AND GENERAL"]
[]
[null,"Note: All items shall be priced for whatever cost may be consider necessary for Preliminary and General to carry out the Mechanical Installations in full, as detailed in the drawings, Specifications and Schedules, which shall include, but shall not be limited, to the following:"]
[]
["B1","Site establishment-over and above the main contractors including the removal thereof upon completion","Item",4,null,{"v":0,"d":"R 0.00"}]
[]
["B2","Company Head Office overhead costs","Item",4,null,{"v":0,"d":"R 0.00"}]
[]
["B3","Programming of work inline with the main contractor's construction programme","Item",4,null,{"v":0,"d":"R 0.00"}]
[]
["B4","Workshop drawings and equipment submittals","Item",4,null,{"v":0,"d":"R 0.00"}]
[]
["B5","Project engineering and management including coordination with other services on site","Item",4,null,{"v":0,"d":"R 0.00"}]
[]
["B6","Instructing and training the Employer's staff in operation of system and equipment prior to hand over to the Client.","Item",4,null,{"v":0,"d":"R 0.00"}]
[null," "]
["B7","Three copies of the O&M Manuals (hard copies and USB)","Item",4,null,{"v":0,"d":"R 0.00"}]
[]
["B8","As-Built Drawings (3 copies)","Item",4,null,{"v":0,"d":"R 0.00"}]
[null," "]
["B9","Any necessary calculations requested by the Engineer.","Item",4,null,{"v":0,"d":"R 0.00"}]
["B10","12 month guarantee period","Item",4,null,{"v":0,"d":"R 0.00"}]
[]
["B11","Provision of full maintenance and guarantee of mechanical equipment and installation for the full 12 month period. The maintenance period shall start after practical completion is achieved.  Service sheets to be submitted for every service carried out.  Refer to tender specification.","Item",4,null,{"v":0,"d":"R 0.00"}]
{"$rows_empty":11}
[null,"SUBTOTAL CARRIED FORWARD TO SUMMARY",{"$nulls":3},{"v":0,"d":"R 0.00"}]

{"sheet":"Compliance","index":4,"n_rows":45,"n_cols":6,"rows_kept":45,"flags":["formulas_cached_only"]}
[]
["No","Description",null,"Qty","Rate","Amount"]
[null," "]
["C","COMPLIANCE"]
[]
[null,"Note: All items shall be priced for whatever cost may be consider necessary for Compliance to carry out the Mechanical Installations in full, as detailed in the drawings, Specifications and Schedules, which shall include, but shall not be limited, to the following:"]
[]
["C1","Compliance with OHS Regulations (latest version) and Site Specific Health & Safety Specification","Item",4,null,{"v":0,"d":"R 0.00"}]
[]
["C2","Clearing of rubble and housekeeping","Item",4,null,{"v":0,"d":"R 0.00"}]
[]
["C3","Scaffolding (3 m high)","Item",4,null,{"v":0,"d":"R 0.00"}]
[]
["C4","Protection of Equipment against damage during construction","Item",4,null,{"v":0,"d":"R 0.00"}]
[]
["C5","Transport and delivery","Item",4,null,{"v":0,"d":"R 0.00"}]
[]
["C6","Rigging and crane hire (N/A)","Item"]
[]
["C7","Provision of spare parts and all related accessories as per specification","Item",4,null,{"v":0,"d":"R 0.00"}]
[]
["C8","Builders work as required (2 m2 doubble wall build)","Item",4,null,{"v":0,"d":"R 0.00"}]
[]
["C9","Electrical work as required (15 m cable + circuit breaker)","Item",4,null,{"v":0,"d":"R 0.00"}]
[]
["C10","Workshop drawings","Item",4,null,{"v":0,"d":"R 0.00"}]
[]
["C11","Testing, balancing, commissioning and handing over in full working order of entire HVAC system(s).","Item",4,null,{"v":0,"d":"R 0.00"}]
{"$rows_empty":16}
[null,"SUBTOTAL CARRIED FORWARD TO SUMMARY",{"$nulls":3},{"v":0,"d":"R 0.00"}]

{"sheet":"Humidifiers","index":5,"n_rows":173,"n_cols":6,"rows_kept":173,"flags":["formulas_cached_only"]}
["No","Description",null,"Qty","Rate","Amount"]
[]
["D","HUMIDIFIERS"]
[]
[]
["D1","See \"Humidifier Specifications\" for requirements"]
[]
[]
[]
["D1.2","Units required:"]
[]
["D1.3","Condair RS 8","No",1.5,null,{"v":0,"d":"R 0.00"}]
[null,"Single phase 230 V and 3-phase 380 V"]
[null,"8 kg/h"]
[]
["D1.4","Condair RS 16","No",1.5,null,{"v":0,"d":"R 0.00"}]
[null,"3-phase 380 V"]
[null,"16 kg/h"]
[]
["D1.5","Condair RS 24","No",1.5,null,{"v":0,"d":"R 0.00"}]
[null,"3-phase 380 V"]
[null,"24 kg/h"]
[]
["D1.6","Condair RS 40","No",1.5,null,{"v":0,"d":"R 0.00"}]
[null,"3-phase 380 V"]
[null,"40 kg/h"]
[]
["D1.7","Condair RS 60","No",1,null,{"v":0,"d":"R 0.00"}]
[null,"3-phase 380 V"]
[null,"60 kg/h"]
[]
["D1.8","Sensor Condair Duct - CDC","No",5,null,{"v":0,"d":"R 0.00"}]
[]
["D1.9","Contingency for installation","Amount",1,{"v":100000,"d":"R 100,000.00"},{"v":100000,"d":"R 100,000.00"}]
[]
[]
["D1.10","Additional costs for installation if not in Pretoria:"]
[null,"a.) Cape Town","Item",1]
[null,"b.) Durban","Item",1]
[null,"c.) Richards bay","Item",1]
[null,"d.) Secunda","Item",1]
[null,"e.) East London","Item",1]
{"$rows_empty":7}
[null,"SUBTOTAL CARRIED FORWARD TO SUMMARY",{"$nulls":3},{"v":100000,"d":"R 100,000.00"}]
{"$rows_empty":20}
[null,"Detail description of products and Scope of Work (SoW)"]
[null,"1.1 Work Included:"]
[null,"a.     Condair RS Series resistive element humidifier[s] as indicated on schedule."]
[null,"b.    Complete and operable humidification system [which meets applicable building codes]"]
[null,"c.     Equipment start-up and project inspection by qualified factory trained representative."]
[null,"1.2 Quality Assurance:"]
[null,"a.     Certifications, C-UL US Listed."]
[null,"b.    ISO 9001-2008."]
[null,"c.     ANSI/NFPA 70 - National Electrical Code."]
[null,"d.    AHRI 640, \"Standard for Commercial and Industrial Humidifiers.\""]
[null,"e.     ASHRAE Standard 135 BACnet"]
[null,"1.3 Related Sections:"]
[null,"BoQ"]
[null,"1.4 Submittals:"]
[null,"a.     Submit product data. Include product description, model, dimensions, component sizes, rough-in requirements, service sizes, and finishes. Include rated capacities, operating weights, furnished specialties, and accessories."]
[null,"b.    Submit manufacturer's installation instructions."]
[null,"c.     Submit operation and maintenance data."]
[null,"d.    Submit coordination drawings. Detail fabrication and installation of humidifiers. Include piping details, plans, elevations, sections, details of components, and dispersion tubes. Detail humidifiers and adjacent equipment. Show support locations, type of support, weight on each support, and required clearances."]
[null,"e.     Submit wiring diagrams including power, signal, and control wiring. Differentiate between manufacturer-installed and field-installed wiring."]
[null,"f.     Submit water pressure requirements."]
[null,"1.5 Schedules:"]
[null,"a.     Refer to information contained in schedule[s] attached to this specification."]
[null,"b.    Humidifiers to be of type, capacity, and arrangement as listed in schedule[s]."]
[null,"c.     Include accessories listed in schedule[s] and those accessories required for type of unit."]
[]
[null,"ELECTRIC STEAM HUMIDIFICATION SYSTEM - MODEL CONDAIR RS"]
[null,"PART 2 - PRODUCTS"]
[null,"2.1 Provide Condair RS resistive element humidifier generating mineral-free, sterile steam for use with potable, De-Ionized (DI), or Reverse Osmosis (RO) water. Packaged unit, wall mounted, atmospheric steam generation using resistive heating element. Electrode technology and boiler steam (pressure steam) technology not acceptable."]
[null,"2.2 Unit[s] to be complete with:"]
[null,"a.     Touchscreen controller with standard building automation and Online connectivity:"]
[null,"                        i.         Intuitive touchscreen control with color graphic user interface."]
[null,"                      ii.         Standard building automation communication protocols BACnet IP, BACnet MSTP and Modbus. Additional hardware required for building automation communication not acceptable."]
[null,"                    iii.         Embedded web interface for easy configuration and remote monitoring from any computer with a web browser over a local area network (LAN) connection."]
[null,"                    iv.         USB interface for new software/feature upload and download of operational information."]
[null,"                      v.         Single or dual channel analog signal acceptance, supporting both demand and transducer control. Ability to control setpoint from humidifier control when using transducer controls."]
[null,"b.     "]
[null,"c.     Packaged system with Condair resistive element technology:"]
[null,"                        i.         Incoloy based resistive heating element for steam production."]
[null,"                      ii.         Modulating output between 4% and 100% of rated capacity."]
[null,"                    iii.         Control accuracy of up to +/- 1% RH using optional Precision solid state relay control and high precision humidistat."]
[null,"                    iv.         Separate scale collection chamber external from main boiling tank when using optional Scale Management system."]
[null,"                      v.         Dual magnetic electronic float system, located outside of the boiling water to ensure accurate water level control and reduced maintenance. Systems using conductivity probes or floats located within hot reservoir are not acceptable."]
[null,"                    vi.         Self-diagnostics during start-up of system to prevent unsafe operation of the unit[s]:"]
[null,"a.     Fill valve check."]
[null,"b.    Float level check."]
[null,"c.     Drain pump check."]
[null,"                   vii.         Durable powder coated steel cabinet with zero side clearance requirement for minimal footprint."]
[null,"                 viii.         Insulating air gap between plumbing and electrical compartment for increased electronic reliability."]
[null,"                    ix.         Standard internal drain water tempering to ensure maximum 140°F [60°C] drain water. External drain water cooler not acceptable."]
[null,"                      x.         Integral fill cup with minimum 1-inch [25 mm] air gap to prevent back siphoning."]
[null,"                    xi.         Automatic off-season shut-down [after 3 days of \"no call\"] will completely drain the boiling tank[s] and automatically restart on call for humidity."]
[null,"                   xii.         Programmable drain settings too allow cycling small water quantities during operation without interrupting steam production."]
[null,"                 xiii.         Integral design allowing easy installation and access for servicing."]
[null,"2.3 Optional Accessories"]
[null,"a.     Steam lance and piping for allowing steam to be released into ducts. See BoQ."]
[null,"PART 3 - EXCECUTION"]
[null,"3.1 Installation:"]
[null,"a.     Install humidifiers per manufacturers' instructions."]
[null,"b.    Install with required clearance for service and maintenance."]
[null,"3.2 Accessories:"]
[null,"a.     Install accessories in accordance with manufacturer's recommendations."]
[null,"3.3 Commissioning:"]
[null,"a.     Start-up of humidifier to be by factory trained technician."]
[]
[]
[]
[]
[null,"Units required:"]
[]
[null,"Condair RS 8"]
[null,"Single phase 230 V and 3-phase 380 V"]
[null,"8 kg/h"]
[]
[null,"Condair RS 16"]
[null,"3-phase 380 V"]
[null,"16 kg/h"]
[]
[null,"Condair RS 24"]
[null,"3-phase 380 V"]
[null,"24 kg/h"]
[]
[null,"Condair RS 40"]
[null,"3-phase 380 V"]
[null,"40 kg/h"]
[]
[null,"Condair RS 60"]
[null,"3-phase 380 V"]
[null,"60 kg/h"]
[]
[null,"Condair RS 60"]
[null,"3-phase 380 V"]
[null,"Master slave configuration"]
[null,"30 + 30 kg/h"]
[]
[null,"Condair RS 120"]
[null,"3-phase 380 V"]
[null,"Master slave configuration"]
[null,"3 x 40 kg/h"]
[]
[null,"Condair RS 160"]
[null,"3-phase 380 V"]
[null,"Master slave configuration"]
[null,"4 x 40 kg/h"]

{"sheet":"Basement - 2","index":6,"n_rows":115,"n_cols":6,"rows_kept":115,"hidden":true,"flags":["formulas_cached_only"]}
["No","Description","Unit","Qty","Rate","Amount"]
["G","HVAC - Basement - 2"]
[]
[null,"Air-Conditioning "]
[]
["G1","DX type Inverter Split Unit (Guard House)"]
[]
[null,"Supply, deliver and install a mid-wall split air conditioning unit complete with indoor and outdoor unit. Including decorative panel, piping between indoor and outdoor portion of unit, mounting brackets, condensate drain pumps and all necessary accessories."]
[]
["G1.2","Brand: Midea, LG, Daikin, Samsung or similar approved ","No",1]
[null,"Type: Midwall, Cassette, Hide-away, Under-ceiling"]
[null,"Cooling Capacity: (BTU or KW)"]
[null,"Heating capacity: (BTU or KW)"]
[null,"Reverse Cycle, cooling only, heating only "]
[null,"Refrigerant: "]
[null,"Inverter Type, Non-Inverter type "]
[null,"Controller: Wired or Wireless"]
[]
["G1.2","Supply and install wired wall mounted remote controller with temperature display, temperature set point, 3 fan speeds, heat/cool mode and ON/OFF functions.","No",1]
[]
["G1.3","Apply anti-corrosion treatment on all the condenser coils (Bluchem or equally approved). Certificate of treatment to be submitted to the design engineer. (Rate per split unit)","No",1]
[]
["G1.4","Additional Piping between Indoor and Outdoor unit including pipe ancillaries, wire mesh tray, pipe supports and installation ancillaries","m",1]
[]
["G2","Extraction System "]
[]
[null,"Supply, deliver and install the following items:"]
[]
["G2.1","Extract Fan (Waste Area)","No",1]
[null,"Fan Type: In-line Axial Fan, Centrifugal Fan, Wall Mounted "]
[null,"Fan Make: ………...or equal and approved"]
[null,"Fan Size: …….diameter or ….x….."]
[null,"Process Data: Airflow (L/s) @ Pressure"]
[null,"Rotational Speed: ……….rpm"]
[null,"Mounting: Anti-Vibration Mounts, Ceiling/Wall mounting kit "]
[null,"Motor Size: (KW)"]
[]
["G2.2","Sound Attenuator","No",2]
[null,"Diameter to suit fan, with flexible collars"]
[null,"Length: 600L, 900L"]
[null,"POD type"]
[null,"NC rating: 35"]
[]
["G2.3","Weather Louver","No",1]
[null,"Make: ………...or equal and approved"]
[null,"Model:  ………...or equal and approved"]
[null,"Size: "]
[null,"Finish: Epoxy Powder Coated or Aluminium Anodised"]
[null,"Hinged with Washable pleated Filter"]
{"$rows_empty":7}
[null,"TOTAL CARRIED FORWARD"]
[]
["No","Description","Unit","Qty","Rate","Amount"]
[null," "]
[null,"TOTAL BROUGHT DOWN"]
[]
["G2.4","Extract Air Grille","No",1]
[null,"Make: "]
[null,"Type: Egg Crate, disc valve"]
[null,"Size: "]
[null,"Finish: Epoxy Powder Coated, Aluminium Anodised or Standard colour to Arch's specification."]
[null,"Opposed Blade Damper (OBD): Y/N"]
[]
["G2.5","Door Grille","No",1]
[null,"Make: "]
[null,"Size: "]
[null,"Finish: Epoxy Powder Coated, Aluminium Anodised or Standard colour to Arch's specification."]
[]
["G2.6","Control Box for fan to switch on when lights are operational, position can be in service shaft, weather proof box with cabling and ancillaries or 24/7 timer","No",1]
[]
["G2.7","Ducting"]
[null,"Low Pressure Galvanised ducting including flexible connections, transformation pieces, bends, shoe pieces, spogots, stop ends and all duct fittings to SANS 1238, \"S\" slip & Drive Slip, 0.6mm ","Sqm"]
[null,"Category 1"]
[]
["G2.8","Flexible Duct"]
[null,"Supply and install wire reinforced aluminium flexible ducting complete with clamps; duct sealant and fixings. 1 500 long","No",1]
[null,"Diameter: "]
[]
["G2.9","Balancing Damper "]
[null,"Balancing Damper to suit duct, manual type, made of sheet metal","No",1]
[null,"Size: "]
[]
["G2.10","Fire Damper "]
[null,"2 hour fire rated Fire Damper with Fusible Link or motorised ","No",1]
[null,"Size: "]
[]
["G2.11","Extract Fan (Guard house toilet)","No",1]
[null,"Fan Type: Ceiling Mounted "]
[null,"Fan Make: ………...or equal and approved"]
[null,"Fan Size: …….diameter or ….x….."]
[null,"Process Data: Airflow (L/s) @ Pressure"]
[null,"Rotational Speed: ……….rpm"]
[null,"Mounting: Anti-Vibration Mounts, Ceiling/Wall mounting kit "]
[null,"Motor Size: (KW)"]
[]
["G2.12","Door Grille","No",1]
[null,"Make: "]
[null,"Size: "]
[null,"Finish: Epoxy Powder Coated, Aluminium Anodised or Standard colour to Arch's specification."]
[]
["G2.13","Control Box for fan to switch on when lights are operational","No",1]
{"$rows_empty":7}
[null,"SUBTOTAL CARRIED FORWARD TO SUMMARY"]

{"sheet":"Basement - 1","index":7,"n_rows":166,"n_cols":6,"rows_kept":166,"hidden":true,"flags":["formulas_cached_only"]}
["No","Description",null,"Qty","Rate","Amount"]
["H","HVAC - Basement - 1"]
[]
[null,"Air-Conditioning "]
[]
["H1","DX type Inverter Split Unit"]
[]
[null,"Supply, deliver and install a DX type inverter split unit complete with indoor and outdoor unit including piping between indoor and outdoor portion of unit, mounting brackets, condensate drain pumps and all necessary accessories."]
[]
["H1.2","Brand: Midea, LG, Daikin, Samsung or similar approved ","No",1]
[null,"Type: Hide-away (DV Retail Area)"]
[null,"Cooling Capacity: (BTU or KW)"]
[null,"Heating capacity: (BTU or KW)"]
[null,"Reverse Cycle, cooling only, heating only "]
[null,"Refrigerant: "]
[null,"Inverter Type, Non-Inverter type "]
[null,"Controller: Wired or Wireless"]
[]
["H1.3","Brand: Midea, LG, Daikin, Samsung or similar approved ","No",1]
[null,"Type: Cassette c/w decorative panel (BOH/Receiving/Office)"]
[null,"Cooling Capacity: (BTU or KW)"]
[null,"Heating capacity: (BTU or KW)"]
[null,"Reverse Cycle, cooling only, heating only "]
[null,"Refrigerant: "]
[null,"Inverter Type, Non-Inverter type "]
[null,"Controller: Wired or Wireless"]
[]
["H1.4","Supply and install wired wall mounted remote controller with temperature display, temperature set point, 3 fan speeds, heat/cool mode and ON/OFF functions.","No",2]
[]
["H1.5","Apply anti-corrosion treatment on all the condenser coils (Bluchem or equally approved). Certificate of treatment to be submitted to the design engineer. (Rate per split unit)","No",2]
[]
["H1.6","Additional Piping between Indoor and Outdoor unit including pipe ancillaries, wire mesh tray, pipe supports and installation ancillaries","m",1]
[]
["H2","Basement Parking Ventilation System"]
[]
[null,"Supply, deliver and install the following items:"]
[]
["H2.1","Ventilation Fan ","No",1]
[null,"Fan Type: In-line Axial Fan, Centrifugal Fan, Wall Mounted "]
[null,"Fan Make: ………...or equal and approved"]
[null,"Fan Size: …….diameter or ….x….."]
[null,"Process Data: Airflow (L/s) @ Pressure"]
[null,"Rotational Speed: ……….rpm"]
[null,"Mounting: Anti-Vibration Mounts, Ceiling/Wall mounting kit "]
[null,"Motor Size: (KW)"]
[]
["H2.2","Sound Attenuator","No",2]
[null,"Diameter to suit fan, with flexible collars"]
[null,"Length: 600L, 900L"]
[null,"POD type"]
[null,"NC rating: 35"]
[]
[]
[]
[]
[]
[]
[null,"TOTAL CARRIED FORWARD"]
[]
["No","Description","Unit","Qty","Rate","Amount"]
[null," "]
[null,"TOTAL BROUGHT DOWN"]
[]
["H2.3","Weather Louver","No",1]
[null,"Make: ………...or equal and approved"]
[null,"Model:  ………...or equal and approved"]
[null,"Size: "]
[null,"Finish: Epoxy Powder Coated or Aluminium Anodised"]
[null,"Hinged with Washable pleated Filter"]
[]
["H2.4","Control Box for fan to switch on when lights are operational, position can be in service shaft, weather proof box with cabling and ancillaries or 24/7 timer","No",1]
[]
["H2.5","Ducting"]
[null,"Low Pressure Galvanised ducting including all transformation pieces (including all brackets and supports) to SANS 1238, \"S\" slip & Drive Slip, 0,6mm ","Sqm"]
[null,"Category 1"]
[]
["H2.6","Inlet Cone"]
[null,"Supply and install fan inlet cone complete with bird proof wire mesh screen.","No",1]
[null,"Size: "]
[]
["H3","Alignment & Fitment Ventilation System"]
[]
[null,"Supply, deliver and install the following items:"]
[]
["H3.1","Ventilation Fan ","No",1]
[null,"Fan Type: In-line Axial Fan, Centrifugal Fan, Wall Mounted "]
[null,"Fan Make: ………...or equal and approved"]
[null,"Fan Size: …….diameter or ….x….."]
[null,"Process Data: Airflow (L/s) @ Pressure"]
[null,"Rotational Speed: ……….rpm"]
[null,"Mounting: Anti-Vibration Mounts, Ceiling/Wall mounting kit "]
[null,"Motor Size: (KW)"]
[]
["H3.2","Sound Attenuator","No",2]
[null,"Diameter to suit fan, with flexible collars"]
[null,"Length: 600L, 900L"]
[null,"POD type"]
[null,"NC rating: 35"]
[]
["H3.3","Weather Louver","No",1]
[null,"Make: ………...or equal and approved"]
[null,"Model:  ………...or equal and approved"]
[null,"Size: "]
[null,"Finish: Epoxy Powder Coated or Aluminium Anodised"]
[null,"Hinged with Washable pleated Filter"]
[]
["H3.4","Control Box for fan to switch on when lights are operational, position can be in service shaft, weather proof box with cabling and ancillaries or 24/7 timer","No",1]
[]
["H3.5","Ducting"]
[null,"Low Pressure Galvanised ducting including all transformation pieces (including all brackets and supports) to SANS 1238, \"S\" slip & Drive Slip, 0,6mm ","Sqm"]
[null,"Category 1"]
[]
[]
[]
[]
[null,"TOTAL CARRIED FORWARD"]
[]
["No","Description","Unit","Qty","Rate","Amount"]
[null," "]
[null,"TOTAL BROUGHT DOWN"]
[]
["H3.6","Inlet Cone"]
[null,"Supply and install fan inlet cone complete with bird proof wire mesh screen.","No",1]
[null,"Size: "]
[]
["H4","Extraction System (Storage)"]
[]
[null,"Supply, deliver and install the following items:"]
[]
["H4.1","Extraction Fan ","No",1]
[null,"Fan Type: Wall Mounted "]
[null,"Fan Make: ………...or equal and approved"]
[null,"Fan Size: …….diameter or ….x….."]
[null,"Process Data: Airflow (L/s) @ Pressure"]
[null,"Rotational Speed: ……….rpm"]
[null,"Mounting: Anti-Vibration Mounts, Ceiling/Wall mounting kit "]
[null,"Motor Size: (KW)"]
[]
["H4.2","Door Grille","No",1]
[null,"Make: "]
[null,"Size: "]
[null,"Finish: Epoxy Powder Coated, Aluminium Anodised or Standard colour to Arch's specification."]
[]
["H4.3","Control Box for fan to switch on when lights are operational.","No",1]
{"$rows_empty":21}
[null,"SUBTOTAL CARRIED FORWARD TO SUMMARY",{"$nulls":3},{"v":0,"d":"R 0.00"}]

{"sheet":"Ground Floor ","index":8,"n_rows":176,"n_cols":6,"rows_kept":176,"hidden":true,"flags":["formulas_cached_only"]}
["No","Description","Unit","Qty","Rate","Amount"]
["I","HVAC - Ground Floor "]
[]
["I1","Air-Conditioning "]
[]
["I1.1","Shop G002"]
[]
[null,"Chilled Water Fan-Coil Units (Hide-aways)"]
[]
[null,"Supply, installation and commissioning of high efficiency fan coil unit with, 2-pipe finned coil to provide cooling and electrical elements to provide electric heating as specified below c/w high efficiency EC fans and alluminium or copper air cooled fins."]
[]
[null,"Supply complete with solenoid valves, instrumentation, electrical equipment, wall mounted and fan coil mounted controller. Control to be integratable with BMS (by others) using Modbus, allowing the BMS operator to switch unit on/off, adjust set-point, and mode, and also to record fault signals"]
[]
["I1.1.1","Brand: Aermec, Trane, Sinko or similar approved","No",1]
[null,"Type: Hide-away "]
[null,"Cooling Capacity:    KW (Total)       KW (Sensible)"]
[null,"Heating capacity:    KW (Electric heating)"]
[null,"Supply airflow:     L/s (or better)"]
[]
["I1.1.2","Ducting - Un-insulated"]
[null,"Low Pressure Galvanised ducting including flexible connections, transformation pieces, bends, shoe pieces, spogots, stop ends and all duct fittings to SANS 1238, \"S\" slip & Drive Slip, 0.6mm ","Sqm"]
[null,"Category 1"]
[]
["I1.1.3","External duct insulation to SANS 10173, 25mm thick thermal insulation with aluminium foil vapour barrier (FRK)","Sqm"]
[]
["I1.1.4","Balancing Damper "]
[null,"Balancing Damper to suit duct, manual type, made of sheet metal","No",1]
[null,"Size: "]
[]
["I1.1.5","Flexible Duct - Externally insulated"]
[null,"Supply and install wire reinforced aluminium flexible ducting complete with clamps; duct sealant and fixings. 1 500mm long","No",1]
[null,"Diameter: "]
[]
["I1.1.6","Diffuser","No",1]
[null,"Brand:   or similar approved"]
[null,"Plenum or Collar"]
[null,"Size: "]
[null,"Finish: Epoxy Powder Coated or Standard colour"]
[]
["I1.1.7","Return Air Grille","No",1]
[null,"Make: "]
[null,"Type: Egg Crate, disc valve"]
[null,"Size: "]
[null,"Finish: Epoxy Powder Coated, Aluminium Anodised or Standard colour to Arch's specification."]
[null,"Opposed Blade Damper (OBD): Y/N"]
[null,"Return Air Filter Frame (RAFF): Y/N"]
[]
[]
[]
[]
[]
[null,"TOTAL CARRIED FORWARD"]
[]
["No","Description","Unit","Qty","Rate","Amount"]
[null," "]
[null,"TOTAL BROUGHT DOWN"]
[]
["I1.1.8","Insulated Condensate Drain","m",1]
[null,"Supply and install P-trapped uPVC drain piping including running joints, fittings, clamps, supports and connection to nearest drain point."]
[null,"Diameter: "]
[]
["I1.1.9","Stainless Steel Drip Tray","No",1]
[null,"Supply and install thermally insulated stainelss steel drip tray for the catment of any condensate from the valves."]
[null,"Size: "]
{"$rows_empty":11}
["I2","Extraction System "]
[]
[null,"Supply, deliver and install the following items:"]
[]
["I2.1","Extract Fan (Ablutions)","No",1]
[null,"Fan Type: In-line Axial Fan, Centrifugal Fan, Wall Mounted "]
[null,"Fan Make: ………...or equal and approved"]
[null,"Fan Size: …….diameter or ….x….."]
[null,"Process Data: Airflow (L/s) @ Pressure"]
[null,"Rotational Speed: ……….rpm"]
[null,"Mounting: Anti-Vibration Mounts, Ceiling/Wall mounting kit "]
[null,"Motor Size: (KW)"]
[]
["I2.2","Sound Attenuator","No",2]
[null,"Diameter to suit fan, with flexible collars"]
[null,"Length: 600L, 900L"]
[null,"POD type"]
[null,"NC rating: 35"]
[]
["I2.3","Weather Louver","No",1]
[null,"Make: ………...or equal and approved"]
[null,"Model:  ………...or equal and approved"]
[null,"Size: "]
[null,"Finish: Epoxy Powder Coated or Aluminium Anodised"]
[null,"Hinged with Washable pleated Filter"]
[]
["I2.4","Disc valves"]
[null,"Type: Extract air "]
[null,"Finish: Epoxy Powder Coated or Standard colour"]
[null,"Neck size: 100 mm dia","No",1]
[null,"Neck size: 150 mm dia","No",1]
[null,"Neck size: 200 mm dia","No",1]
[]
["I2.5","Door Grille","No",1]
[null,"Make: "]
[null,"Size: "]
[null,"Finish: Epoxy Powder Coated, Aluminium Anodised or Standard colour to Arch's specification."]
[]
[]
[]
[null,"TOTAL CARRIED FORWARD"]
[]
["No","Description","Unit","Qty","Rate","Amount"]
[null," "]
[null,"TOTAL BROUGHT DOWN"]
[]
["I2.6","Control Box for fan to switch on when lights are operational located in serrvice shaft or 24/7 timer.","No",1]
[]
["I2.7","Ducting"]
[null,"Low Pressure Galvanised ducting including flexible connections, transformation pieces, bends, shoe pieces, spogots, stop ends and all duct fittings to SANS 1238, \"S\" slip & Drive Slip, 0.6mm ","Sqm"]
[null,"Category 1"]
[]
["I2.8","Flexible Duct"]
[null,"Supply and install wire reinforced aluminium flexible ducting complete with clamps; duct sealant and fixings. 1 500 long","No",1]
[null,"Diameter: "]
[]
["I2.9","Balancing Damper "]
[null,"Balancing Damper to suit duct, manual type, made of sheet metal","No",1]
[null,"Size: "]
[]
["I2.10","Fire Damper "]
[null,"2 hour fire rated Fire Damper with Fusible Link or motorised ","No",1]
[null,"Size: "]
[]
["I3","Tempered Fresh Air System or Fans"]
{"$rows_empty":35}
[null,"SUBTOTAL CARRIED FORWARD TO SUMMARY",{"$nulls":3},{"v":0,"d":"R 0.00"}]

{"sheet":"First Floor ","index":9,"n_rows":158,"n_cols":6,"rows_kept":158,"hidden":true,"flags":["formulas_cached_only"]}
["No","Description","Unit","Qty","Rate","Amount"]
["J","HVAC - First Floor "]
[]
["J1","Air-Conditioning "]
[]
["J1.1","Shop F001"]
[]
[null,"Chilled Water Fan-Coil Units (Hide-aways)"]
[]
[null,"Supply, installation and commissioning of high efficiency fan coil unit with, 2-pipe finned coil to provide cooling and electrical elements to provide electric heating as specified below c/w high efficiency EC fans and alluminium or copper air cooled fins."]
[]
[null,"Supply complete with solenoid valves, instrumentation, electrical equipment, wall mounted and fan coil mounted controller. Control to be integratable with BMS (by others) using Modbus, allowing the BMS operator to switch unit on/off, adjust set-point, and mode, and also to record fault signals"]
[]
["J1.1.1","Brand: Aermec, Trane, Sinko or similar approved","No",1]
[null,"Type: Hide-away "]
[null,"Cooling Capacity:    KW (Total)       KW (Sensible)"]
[null,"Heating capacity:    KW (Electric heating)"]
[null,"Supply airflow:     L/s (or better)"]
[]
["J1.1.2","Ducting - Un-insulated"]
[null,"Low Pressure Galvanised ducting including flexible connections, transformation pieces, bends, shoe pieces, spogots, stop ends and all duct fittings to SANS 1238, \"S\" slip & Drive Slip, 0.6mm ","Sqm"]
[null,"Category 1"]
[]
["J1.1.3","External duct insulation to SANS 10173, 25mm thick thermal insulation with aluminium foil vapour barrier (FRK)","Sqm"]
[]
["J1.1.4","Balancing Damper "]
[null,"Balancing Damper to suit duct, manual type, made of sheet metal","No",1]
[null,"Size: "]
[]
["J1.1.5","Flexible Duct - Externally insulated"]
[null,"Supply and install wire reinforced aluminium flexible ducting complete with clamps; duct sealant and fixings. 1 500mm long","No",1]
[null,"Diameter: "]
[]
["J1.1.6","Diffuser","No",1]
[null,"Brand:   or similar approved"]
[null,"Plenum or Collar"]
[null,"Size: "]
[null,"Finish: Epoxy Powder Coated or Standard colour"]
[]
["J1.1.7","Return Air Grille","No",1]
[null,"Make: "]
[null,"Type: Egg Crate, disc valve"]
[null,"Size: "]
[null,"Finish: Epoxy Powder Coated, Aluminium Anodised or Standard colour to Arch's specification."]
[null,"Opposed Blade Damper (OBD): Y/N"]
[null,"Return Air Filter Frame (RAFF): Y/N"]
[]
[]
[]
[null,"TOTAL CARRIED FORWARD"]
[]
["No","Description","Unit","Qty","Rate","Amount"]
[null," "]
[null,"TOTAL BROUGHT DOWN"]
[]
["J1.1.8","Condensate Drain","m",1]
[null,"Supply and install P-trapped uPVC drain piping including running joints, fittings, clamps, supports and connection to nearest drain point."]
[null,"Diameter: "]
[]
["J1.1.9","Stainless Steel Drip Tray","No",1]
[null,"Supply and install thermally insulated stainelss steel drip tray for the catment of any condensate from the valves."]
[null,"Size: "]
[]
["J1.2","Shop F002"]
{"$rows_empty":7}
["J2","Extraction System "]
[]
[null,"Supply, deliver and install the following items:"]
[]
["J2.1","Extract Fan (Ablutions)","No",1]
[null,"Fan Type: In-line Axial Fan, Centrifugal Fan, Wall Mounted "]
[null,"Fan Make: ………...or equal and approved"]
[null,"Fan Size: …….diameter or ….x….."]
[null,"Process Data: Airflow (L/s) @ Pressure"]
[null,"Rotational Speed: ……….rpm"]
[null,"Mounting: Anti-Vibration Mounts, Ceiling/Wall mounting kit "]
[null,"Motor Size: (KW)"]
[]
["J2.2","Sound Attenuator","No",2]
[null,"Diameter to suit fan, with flexible collars"]
[null,"Length: 600L, 900L"]
[null,"POD type"]
[null,"NC rating: 35"]
[]
["J2.3","Weather Louver","No",1]
[null,"Make: ………...or equal and approved"]
[null,"Model:  ………...or equal and approved"]
[null,"Size: "]
[null,"Finish: Epoxy Powder Coated or Aluminium Anodised"]
[null,"Hinged with Washable pleated Filter"]
[]
["J2.4","Disc valves"]
[null,"Type: Extract air "]
[null,"Finish: Epoxy Powder Coated or Standard colour"]
[null,"Neck size: 100 mm dia","No",1]
[null,"Neck size: 150 mm dia","No",1]
[null,"Neck size: 200 mm dia","No",1]
[]
["J2.5","Door Grille","No",1]
[null,"Make: "]
[null,"Size: "]
[null,"Finish: Epoxy Powder Coated, Aluminium Anodised or Standard colour to Arch's specification."]
[]
[]
[]
[null,"TOTAL CARRIED FORWARD"]
[]
["No","Description","Unit","Qty","Rate","Amount"]
[null," "]
[null,"TOTAL BROUGHT DOWN"]
[]
["J2.6","Control Box for fan to switch on when lights are operational located in serrvice shaft or 24/7 timer.","No",1]
[]
["J2.7","Ducting"]
[null,"Low Pressure Galvanised ducting including flexible connections, transformation pieces, bends, shoe pieces, spogots, stop ends and all duct fittings to SANS 1238, \"S\" slip & Drive Slip, 0.6mm ","Sqm"]
[null,"Category 1"]
[]
["J2.8","Flexible Duct"]
[null,"Supply and install wire reinforced aluminium flexible ducting complete with clamps; duct sealant and fixings. 1 500 long","No",1]
[null,"Diameter: "]
[]
["J2.9","Balancing Damper "]
[null,"Balancing Damper to suit duct, manual type, made of sheet metal","No",1]
[null,"Size: "]
[]
["J2.10","Fire Damper "]
[null,"2 hour fire rated Fire Damper with Fusible Link or motorised ","No",1]
[null,"Size: "]
[]
["J3","Tempered Fresh Air System or Fans"]
{"$rows_empty":21}
[null,"SUBTOTAL CARRIED FORWARD TO SUMMARY",{"$nulls":3},{"v":0,"d":"R 0.00"}]