Agriculture Research Council (ARC) Virology Incubator room to be converted room and shelves specifications:

  - To supply and install a cold room(indoor and outdoor  for the Agricultural Research Council (ARC), Onderstepoort Veterinary Research Institute (OVR), Virology

Cold room unit (indoor and outdoor) to be installed in this specific area assigned inside the ARC-OVR-Virology Department

The existing dimensions (external) of the room is as follows:

Width – 2.8m

Depth – 1.7m

Height – 2.3m.

- To supply and install evaporator and condenser (with compressor) and Door must be replaced to a refrigeration panels and must be lockable.

- Cold room should correlate to maintain a cold-room temperature of between 2-6°C at all times.

- To supply and install cooling unit/s with the capacity to cool and maintain the inside temperature of this room of 2-6°C at all times. The cooling capacity of the cooling unit/s must be calculated by the supplier based on the room size and Sample stored

- To supply and install:

- DB+PLUGS+LIGHTS

- Lights (water proof) must be installed to allow at least 2.1m clearance from floor level.

- Main switch with single phase circuit breaker 63A

- 10 mm cable 4 core plus earth surfix, length to be confirmed.

- 4mm cable X 3core surfix and 40A single phase circuit breaker

- 1x Sub DB Board with the double pole surge protection unit (20A) capability.

- 2x 4ft Light fittings (condensation proof lights) with LED tubes and light switches

- 4x 4x4 Double plugs and 8x Single plugs

- Each single plug to have its own circuit breaker (20A) and the earth leakage (63A)

- Cable, trunkings and fittings to be included

- Approximately ~110m of cabling required from the main DB to the cold room location, confirmation to be done on site briefing.

- Double pole main isolator and trip switch on main DB board required.

- Aluminium gripping floor

- Floor slab

- Electrical contractor must be registered with department of labour for doing any electrical work and issuing a certificate of compliance after completing the work.

- Cooling unit/s installer must after the completion of the installation issue a (CoC) certificate of conformity by a Registered Authorized Refrigeration Gas Practitioner.

- The company must be a member with SARACCA

- The technician must be registered with SAQCC GAS

- Refrigeration Trade test( red Seal) with C.V

- Strictly copper tubbing

- Brazing with nitrogen pegging

- Delivery period should not exceed 6 weeks

- All bidders are to attend a compulsory once-off site meeting that will be arranged before providing a quote and only quotes from those who attended the site meeting will be accepted. Measurements provided are only an estimation. There are restrictions to sizes of passages and door openings, thus the supplier must view the site to determine how the requirements will be executed and achieved.

- 5 year manufacturer’s guarantee/warranty required.

- Installation and operational qualification validation by the end user.

1.2 To supply 4 x Industrial duty Tier shelves

Width-4.2m

Depth-4.2m

-Supply and install 4 x Steel shelving

-Shelve Dimension 2m x 2m x 60cm

-Shelve Description: Industrial duty Tiers Shelve which can carry 200kg