SPECIFICATIONS FOR TAD VACCINE PRODUCTION GAS LINES

Date: 01 Dec 2025

| ITEM | SCOPE | MATERIALS | LENGTH AND DIAMETER | ADDITIONAL INFO |
| --- | --- | --- | --- | --- |
| MEDICAL CO2 & MEDICAL OXYGEN | - Construct a new fenced and roofed storage area to accommodate 12 cylinders (6xCO2, & 6x O2). Just next to the current existing gas supply facility. - Install a control station regulated at 2-Bar for (2xCO2, & 2x O2) in use. - Install audible alarm and the system must be able to switch automatically between cylinders once one is empty. - Audible alarm must stay active until both main cylinders reach the 2-Bar pressure. - Install new medical grade pipe lines from the regulation station to the end-user points in sections TC, Block H, Pilot plant and buffer zone. (TC and buffer zone excluded for medical O2 pipes installation). - All pipes must be clearly identifiable (marked and color coded) at the end-user point. - The existing medical CO2 line must be pressure tested, and the identified leaks must be repaired/replaced. | To be agreed in the compulsory site briefing | To be agreed in the compulsory site briefing | - All pipes be securely onto the concrete walls or roof by clamps. - Colour coded and 10 tags be supplied. - Issue a CoC - The installations must meet and comply to all legislative compliance requirements. - A 25mm diameter hole already exists through the building wall into block H. |
| L.P. GAS | - Pressure test and repair/ replace all pipes with new feeding into blocks H, G, Buffer zone and T.C. - Supply and install new regulators and gauges from the 2x cylinders to the main supply line. | To be agreed in the compulsory site briefing | To be agreed in the compulsory site briefing | The storage station already exists but improvement recommendation for compliance will be agreed upon in the site briefing. Issue a CoC |
| VACUUM LINE | - Pressure test all existing lines and issue certificate of compliance | As installed | As installed | Supply a spare 10-meter length pipe for future corroded pipework. |
| VACUUM PUMPS | Service the existing 2x pumps. Install a drainable filter between the existing incoming line and the vessel. | OEM backed materials | OEM backed materials | Pumps are based in the basement and can be outsourced with a service report and recommended follow up service interval. Pumps capacity is: -27HG |
| COMPRESSED AIR LINES | Pressure test all existing lines (3 bar & 8 bar) and issue certificate of compliance Repair all detected leaks. | As installed | As installed | All compressed airlines from the compressor room to block H, TC and Pilot Plant |
| CHILLED WATER LINE | Pressure test the Daiken chiller supply and return water lines | As installed | As installed | All supply lines from source to block H, TC, Pilot plant and buffer zone. Issue certificate of compliance (CoC). |
| SUPPLY AS BUILT DRAWINGS TO ARC | Develop and supply schematic drawings for on different lines having worked on by 2 copies each per scope | As detailed on scope with recommendations for future upgrades | As detailed on scope with recommendations for future upgrades | Drawings will remain the property of ARC and cannot be shared with any outside parties. Copyrights and confidentiality regulations will apply. |

EVALUATION CRITERIA

| ITEM | COMPLY or NOT COMPLY | COMMENTS |
| --- | --- | --- |
| MEDICAL CO2 & MEDICAL OXYGEN |  |  |
| L.P. GAS |  |  |
| VACUUM LINE |  |  |
| VACUUM PUMPS |  |  |
| COMPRESSED AIR LINES |  |  |
| CHILLED WATER LINE |  |  |
| SUPPLY AS BUILT DRAWINGS TO ARC |  |  |