BID NUMBER: RW103932223/2021

P.02537- Hyd/Pow/Reservoirs/Syt-Spec

DESIGN, MANUFACTURE, SUPPLY, DELIVERY, INSTALLATION, TEST, COMMISSION, OPERATE AND MAINTAIN A HYDROPOWER PLANTS AT RAND WATER BRONBERG, BRAKFONTEIN, HARTEBEESTHOEK AND KLIPFONTEIN RESERVOIR SITES – SYSTEM SPECIFICATION

Table of Contents

1.	SCOPE	3

2.	APPLICABLE DOCUMENTS	3

2.1.	External Documents	3

2.2.	Internal Rand Water Documents	7

2.3.	List of Drawings	8

3.	HYDROPOWER SYSTEM REQUIREMENTS	9

3.1.	System Definition	9

3.2.	Major Component List	12

3.3.	Rand Water Furnished Items	14

3.4.	System Characteristics	16

3.5.	Design and Construction	20

3.6.	Documentation	20

3.7.	Major Component Characteristics	22

3.7.1.	Civil Structures and Building	22

3.7.2.	Structural Engineering Requirements	25

3.7.3.	Architectural Requirements	27

3.7.4.	Pipelines	34

3.7.5.	General Mechanical	80

3.7.6.	Hydro-Mechanical	108

3.7.7.	Electrical Sub-Systems	68

3.7.8.	Automation	98

3.7.9.	Logistical sub-systems	112

4.	VERIFICATION	114

5.	PREPARATION FOR DELIVERY	115

# SCOPE

This document is a functional specification for the hydropower system to be designed, manufactured, supplied, delivered, installed, tested, commissioned, operated and maintained at Rand Water Bronberg, Brakfontein, Hartebeesthoek And Klipfontein Reservoir Sites

IT IS CRITICAL THAT WATER SUPPLY OVERRIDES POWER SUPPLY. THEREFORE, WATER SUPPLY REQUIREMENTS SHALL BE MET FIRST AND THEN POWER GENERATION REQUIREMENTS SHALL FOLLOW.

This document shall be read in conjunction with the feasibility study report conducted for Bronberg, Brakfontein, Hartebeesthoek and Klipfontein Reservoir Sites Reservoir documents:

- Report No 4500210976 – BBR – Version 3, Bronberg Reservoir Site.

- Report No 4500210976 – BR – Version 2, Brakfontein Reservoir Site.

- Report No 4500210976 ‐ KR – Version 3, Klipfontein Reservoir Site.

- Report No 4500210976 – HR –Version 3, Hartebeesthoek Reservoir Site.

# APPLICABLE DOCUMENTS

The following specifications, standards, and handbooks of the exact revision listed below form a part of this specification to the extent specified herein.

Where reference is made to a code, specification or standard, the reference shall be taken to mean the latest edition available at the date of submission of the tender of that code, specification or standard, including addenda, supplements and revisions thereto.

In the event of a conflict between the text of this specification and the references cited herein, the text of this specification takes precedence. Nothing in this specification, however, supersedes applicable laws and regulations unless a specific exemption has been obtained.

# External Documents

    - SANS Specifications

SANS 763 – 1988: Hot-dip (galvanized) zinc coatings

SANS 1339: Electrical cables-cross linked polyethylene (XLPE) - insulated cables for voltages from 3,3/6,6 kV to 19/33 kV

SANS ISO 9001, Parts I, II and III: Quality systems

SANS 1091: National colour standards for paint

SANS IEC-34: Rotating electrical machines. Parts 1 to 18

SANS 719: Electric welded low Carbon steel pipes for aqueous fluids (ordinary duties)

SANS 10100-1: The Structural use of concrete Part 1: Design

SANS 10100-2: The structural use of concrete PART 2: Materials and execution of work.

SANS 10160: The general procedures and loadings to be adopted in the design of buildings.

SABS 0161: The design of foundations for buildings

SANS 10164-1: The structural use of masonry Part 1: Unreinforced masonry walling

SANS 10162 PART 1: The structural use of steel

SANS 1123:2000: Pipe Flanges

SANS 10064: The preparation of steel surfaces for coating

SANS 10400: The application of the National Building Regulations

SANS 1200 HC: Corrosion protection of structural steelwork

SANS 1091: National colour standards for paint

SANS 460: Plain-ended solid drawn copper tubes for potable water

SANS 455: Covered electrodes for the manual arc welding of carbon and carbon manganese steels

SANS 966-1: Components of pressure pipe systems Part 1: Unplasticized poly(vinyl chloride) (PVC-U) pressure pipe systems

SANS 967: Unplasticized poly (vinyl chloride) (PVC-U) soil, waste and vent pipes and pipe fittings SANS 10044: Welding : Parts I to VII

SANS 10238: Welding and thermal cutting processes – Health and safety

SABS EN 10240: Internal and/or external protective coatings for steel tubes – Specification for hot-dip galvanized coatings applied in automatic plants.

SANS 121: Hot-dip galvanized coatings on fabricated iron and steel articles – Specification and test methods.

SANS ISO 3575: Continuous hot-dip zinc-coated carbon steel sheet of commercial, lock forming and drawing qualities

SANS 10214 : The design, fabrication and inspection of articles for hot-dip galvanising

SANS 1186-1 : Symbolic Safety Signs Part I : Standard signs and general requirements.

SANS 62 : Steel Pipes Part 1 : Steel pipes of NB not exceeding 200 mm.

SANS 62 : Steel Pipes Part 2 : Pipes and pipe fittings of nominal bore not exceeding 150 mm, made from steel pipe.

SANS 0147 : Refrigerating System including Plants associated with air-conditioning systems.

SANS 1125 : Room air conditioners and heat pumps

SANS 719 : Electric welded low carbon steel pipes for aqueous fluids (ordinary duties)

SANS 193 : Fire Dampers

SABS 10173 : The installation, testing and balancing of air-conditioning duct work

SANS 10103 : The measurement and rating of environmental noise with respect to annoyance and speech communication

SANS 10140 : Identification colour marking

SANS 630 : Decorative high-gloss enamel paint for interior and exterior

SANS 1238 : HVAC duct construction standards - air conditioning ductwork

SANS 1062 : Pressure and vacuum gauges

SANS 10227-2 : Pressure vessels, inspectorates, certification (approval), modified or repaired pressure vessels.

SANS 1424 : Filters for use in air-conditioning and general ventilation

SANS 1019 : Standard voltages, currents and insulation levels for electricity supply

SANS IEC 60529 : Degrees of protection provided by enclosures (IP code)

SANS 1091 : National paint colour standards

SANS IEC-60034 : Rotating electrical machines. Parts 1 to 31

SANS 1804 : Parts 1 and 2: Low voltage three phase standard induction motors

SANS IEC 62271 : Part 100- High Voltage Circuit Breakers above 1 kV up to 52 kV

SANS IEC 62271 : Part 200- AC metal enclosed switchgear and control gear

SANS 60255 : Parts 1 to 25 – Electrical Relays

SANS 62052-11 : Electricity metering equipment (a.c) – General requirements, tests and test conditions SANS 1652 : Battery chargers- Industrial type

SANS 1632 : Parts 1, 2 and 3:-Stationary Batteries

SANS IEC-60060 : Parts 1 to 3:- High Voltage Test Techniques – Part 2: Test procedures

SANS 1339 : Electrical cables-cross linked polyethylene (XLPE) - insulated cables for  voltages  from 3,3/6,6 kV to 19/33 kV

SANS 1507 : Electric cables with extruded solid dielectric insulation for fixed installations (300/500 V to 1 900/3 300V)

SANS 10198 : Parts 1 to 14:- The selection, handling and installation of electric power cables of rating not exceeding 33 kV

SANS 61024 : Parts 1 & 2:- Protection of structures against lightning

SANS 60199 : The design and installation of earth electrodes

SANS 1063 : Earth rods, couplers and connections

SANS 10292 : Earthing of low-voltage (LV) distribution systems

SANS 10200:- Neutral earthing in medium voltage industrial power systems

SANS 62040 : Parts 1, 2, 3:- Uninterruptible power systems

SANS 8528 : Parts 1 to 12: Reciprocating internal combustion engine driven alternating current generating sets

SANS IEC 60439 Parts 1 to 4 : Low voltage switchgear and control gear assemblies

SANS IEC 60947 Parts 1 to 5 : Low Voltage Switchgear and Control Gear

SANS 1973; Parts 1, 3, 7 & 8 : Low voltage switchgear and assemblies

SANS IEC 60076 Parts 1 to 10 : Power transformers

SANS 555 : Mineral Insulating Oils

SANS 1029 : Miniature substations

SANS 60099 Parts 1, 4, 5, 6 and 7 : Surge Arrestors

SANS 60265 Parts 1 and 2 : High Voltage switches

SANS 60305 : Insulators for overhead lines with a voltage above 1000 V a c

SANS 60282 : Parts 1 and 2: High Voltage Fuses

SANS 10114 : Parts 1 and 2: Interior Lighting

SANS 10389 : Parts 1 and 2: Exterior Lighting

SANS 10142-1 : Code of Practice for the Wiring of Premises

SANS 1200 A : Preliminary and General

SANS 1200 AA : General (Small Works) SANS 1200 AB : Engineer's Office

SANS 1200 C : Site Clearance

SANS 1200 DA : Earthworks (Small Works) SANS 1200 DB : Earthworks (Pipe Trenches) SANS 1200 G : Concrete (Structural)

SANS1200 HA : Structural Steelwork (Sundry Items) SANS 1200 L : Medium Pressure Pipelines

SANS 1200 LE : Stormwater Drainage SANS 1200 M : Roads (general)

As well as specified elsewhere in the system specifications

    - British Standard Specifications

BS 4504 – 1969 : Steel, cast iron and copper alloy flanges, tables 10/3, 25/3 or 64/3

BS 4999 : Specification General requirements for rotating electrical machines. Part 133

BS 5316 : Precision class tests

BS 6861 : Mechanical balancing of rotating bodies

BS 4190 : Specification for ISO metric black hexagon bolts, screws and nuts

BS 5328-1 : Concrete. Guide to specifying concrete

BS 5337 : Structural use of concrete for retaining aqueous liquids

BS 8007 : Code of practice for design of concrete structures for retaining aqueous liquids.

BS 10 ; Specification for flanges and bolting for piping, valves and fittings.

BS EN 10216/7-1 : Specification for carbon steel pipes and tubes with specified room temperature properties for pressure purposes

BS 4504 : Circular flanges for pipes, valves and fittings (PN designated)

3.1 : Specification for steel flanges

3.3 : Specification for copper alloy and composite flanges.

BS 13001-1&2 : Machines for miscellaneous applications.

As well as specified elsewhere in the system specifications

    - International Electrotechnical Commission (IEC) Publications

IEC-34 : Parts 1 to 18 Rotating Electrical Machines

IEC-60-2 : High Voltage Test Techniques - Part 2: Test procedures

IEC 60909- Parts 0 to 4: Short Circuits in three phase a c systems

IEC 60071- Parts 1 to 4:- Insulation Co-ordination

IEC 60056- High Voltage Circuit Breakers IEC 60044-1:- Current Transformers

IEC 60044-2:- Inductive Voltage Transformers

IEC 60044-3:- Combined Instrument Transformers

As well as specified elsewhere in the system specifications

    - Other codes of practice and guidelines

ARP 013 – 1990: Technical specifications, Guidelines for drafting

Swedish Standard SIS-055900-1967 SA 2 1/2

Geometric Design: TRH 17 (1988) - Geometric Design of Rural Roads

Road Markings and Signage: SADC Road Traffic Signs Manual, 3rd Edition CKS 389: Specification for flexible polyvinyl chloride water stops.

ISO 9905 - 1994: Technical specifications for centrifugal pumps

– Class I ISO 5199: 2002: Technical specifications for centrifugal pumps

– Class II ISO 9908: 1993: Technical specifications for centrifugal pumps

– Class III ISO 76:1987: Rolling bearings – Static load ratings

ISO 281:1990: Rolling bearings – Dynamic load ratings and rating life

ISO 2372:1974: Mechanical vibration of machines with operating speeds from 10 to 200 rev/s – Basis for specifying evaluation standards

ISO 3069:1974: End suction centrifugal pumps – Dimensions of cavities for mechanical seals and for soft packing

ISO 7005-1:1992 : Metallic flanges – Part 1: Steel flanges

ISO 1940-1:2003 : Metallic flanges – Part 2: Cast Iron

ISO 9906 : Rotordynamic pumps – Hydraulic performance acceptance tests – Grades 1 and 2

*(ISO 9906 replaces ISO 3555 and ISO 2548)

*ISO 3555:1977 : Centrifugal, mixed flow and axial flow pumps – Code for acceptance tests – Class B

*ISO 2548:1973 : Centrifugal, mixed flow and axial flow pumps – Code for acceptance tests – Class C

NRS 033- Electricity distribution - Guidelines for the application design, planning and construction of medium voltage overhead power lines up to and including 22 kV, using wooden pole structures and bare conductors NRS 048- Parts 2, 4 and 6- Electricity Supply- Quality of Supply

# Internal Rand Water Documents

The following Rand Water specifications form part of this documentation and must further be adhered to:

RW-00320-AS-978 : Medium voltage switchgear

RW-00320-AS-909 : Instrument Transformers for Medium Voltage Systems

RW-00320-AS-491-D : Factory Built Assemblies of Low Voltage Switchgear

RW-00320-AS-492 : Low Voltage Asynchronous Motors

RW-00320-AS-495 : Low Voltage Diesel Engine Driven Standby Generators

RW-00320-AS-493 : Control Panels

RW-00320-AS-494 : Uninterruptible Power Supplies

RW-00320-AS-489 : Earthing and Lightning Suppression

RW-00320-AS-500 : Building Electrical Installations

RW-00320-AS-488 : Control of Plant and Equipment

RW-00320-AS-496 : Installation of Plant and Equipment

RW-00320-S-001-D : Design and Selection of Electrical Plant

RW-EES-002 : Electrical Drawings Standard Detail Engineering Package Checklist- Rev 01

RW /0310/ AS0460 Rev 3: Rand Water Specification for Sluice, Air, Butterfly, Resilient Seal Gate- And Ball

Valves And Powered Actuators

SAM DOP 00001 TS – Pipeline Design Technical Specification Rev02

# List of Drawings

The following drawings are applicable for this tender

Bronberg, Brakfontein, Hartebeesthoek and Klipfontein Reservoir Sites Reservoir:

| Item No. | Drawing No. | Description |
| --- | --- | --- |
| 1 | R024047_100 | Bronberg-Site layout with Hydro Building |
| 2 | R024047-801 | Site Layout showing Construction Access Road |
| 3 | 12205/188 | Hartesbeeshoek 100 ML- General Arrangement of Upgraded Inlet/Outlet system to Hartesbeeshoek Rersevoir |
| 4 | R029423 | Hartebeeshoek Layout with Proposed Hydro Building |
| 5 | R029422 | Brakfontein Reservoir Layout WITH Hydro Power Building |
| 6 | RO29421 | Klipfonten Reservoir Layout with Hydro Power Building |
| 7 | RA_20941 | Typical Small Power and Lighting SLD and Floor Plan Layout |
| 8 | RB_40570 | 400V MCCB Switchboard Typical Schematics |
| 9 | RB_40571 | 110VDC Battery Charger Typical Schematics |
| 10 | RB_40572 | 400V Generator Typical Schematics |
| 11 | RB_21023 | 400V Motor Feeder and Protection Relay Typical Schematics |
| 12 | RB_21032 | UPS Circuit Typical Schematic |
| 13 | RB_20092 | Motor Feeder Typical Schematic |
| 14 | RB_20093 | Valve Chamber DB Typical SLD |
| 15 | RB_20094 | Heater Control Typical Schematics |
| 16 | RB_20099 | Cooling Water Pump Typical Schematics |
| 17 | RB_20100 | Sump Pump Typical Schematic |
| 18 | RB_6443 | Cable Trench Cross Section |
| 19 | R0_40548 | Proposed location for Hydro Power Plant Site layout Klipfontein |
| 20 | R0_40549 | Proposed location for Hydro Power Plant Site layout Brakfontein |
| 21 | R0_40550 | Proposed location for Hydro Power Plant Site layout Hartebeesthoek |
| 22 | R0_40551 | Proposed location for Hydro Power Plant Site layout Bronberg |

# HYDROPOWER SYSTEM REQUIREMENTS

# System Definition

This paragraph defines the major components of the Hydropower System.

    - System Breakdown Structure

The System Breakdown Structures (SBS) provided show the major sub-systems of the Hydropower System.

The Hydropower System comprises the following Main Sub-systems (refer 3.2 for breakdown):

      - Hydropower

      - Civil structure and buildings

      - Architecture

      - Electrical

      - Mechanical

      - Automation

      - Mechanical and

      - Logistical

The following external systems interface with the Hydropower System:

      - Existing upstream pipe work

      - Existing downstream pipe work

      - Brakfontein, Bronberg, Klipfontein and Hartebeesthoek Turbine Room Telemetry shall be linked to Reservoir Level Telemetry

      - Central Depot, Benoni Depot and Esselen Park Depot Control Room via telemetry

      - Brakfontein, Bronberg, Klipfontein and Hartebeesthoek SBS.

      - Area Municipality for Brakfontein, Bronberg, Klipfontein and Hartebeesthoek

      - Sub-Stations at the proposed Power Supply Utility.

    - Operational Requirements

      - Primary Supply

IT IS CRITICAL THAT WATER SUPPLY OVERRIDES POWER SUPPLY. THEREFORE, WATER SUPPLY REQUIREMENTS SHALL BE MET FIRST AND THEN POWER GENERATION REQUIREMENTS SHALL FOLLOW.

The hydropower Generation infrastructure (Turbine room, control room/ systems, turbines, pipes, valves etc.) shall not impede Rand Water infrastructure’s intended operability, accessibility and maintainability.

      - Proposed Operational Philosophy

It is proposed to harness the available water head and flow energy to generate the hydropower by bypassing the existing energy dissipation devices before discharging into the Reservoirs.

The System shall be designed ensuring that the existing control philosophy at Brakfontein, Bronberg, Klipfontein and Hartebeesthoek Reservoir is complied with. When the reservoir is full no flow shall be allowed to go through into the reservoir and create unnecessary overflow.

    - Interface Definition

      - External Interfaces

        - Turbine Room Telemetry

- The Bronberg Reservoir -1 level shall be measured and be interfaced to Bronberg Turbine Room via Telemetry System.

- The Brakfontein Reservoir -1 level shall be measured and be interfaced to Brakfontein Turbine Room via Telemetry System.

- The Klipfontein Reservoir -1 level shall be measured and be interfaced to Klipfontein Turbine Room via Telemetry System.

- The Hartebeeshoek Reservoir -1 level shall be measured and be interfaced to Hartebeeshoek Turbine Room via Telemetry System.

        - Existing Upstream Pipe to Inlet pipe

Pipe to pipe interfaces are specified in section 3.7.

        - Existing Upstream Pipe to Bypass Valve

Pipe to valve interfaces are specified in section 3.7.

        - Existing Downstream Pipe to Outlet pipe

Pipe to pipe interfaces are specified in section 3.7.

        - Existing Downstream Pipe to Bypass Valve

Pipe to pipe interfaces are specified in section 3.7.

        - Transmission Line

Power Generated at the reservoirs shall be transmitted to a proposed Sub-station in the respective reservoir’s feasibility report. The transmission line (overhead line, underground cables or combination of both) shall conform to NRS, SANS standards and to all Eskom requirements. The cable route shall be determined and approved in liaison with the Area Municipality.

        - Power Sub-stations

The contractor shall facilitate with Rand Water to get Modifications/Alterations Designs and Approvals required for the successful connection into the Power Sub-station’s grid shall be completed and approved by the Power Utility.

      - Internal Interfaces

        - Pipe to pipe

Pipe to pipe interfaces are specified in section 3.7.

        - Pipe to valve

Pipe to valve interfaces are specified in section 3.7.

        - Pipe to plinth

Pipe to plinth interfaces are specified in section 3.7.

        - Pipe to building

Pipe to building interfaces are specified in section 3.7.

        - Device to plinth

Device to plinth interfaces are specified in section 3.7.

        - Automation

Automation devices interface with

          - UPS by means of cabling, which is specified in section 3.7

          - Each other by means of Profibus or Ether networks both specified in section 3.7.

        - Electrical

Electrical devices and cables selection, design and installation shall meet Rand Water and national standards.

        - Mechanical

Equipment selection, design and installation shall meet Rand Water and national standards.

# Major Component List

It is envisaged that the Hydropower System shall comprise of, at least but not limited, to the following major components:

    - Hydro-mechanical power Sub-systems

      - Inlet valve

      - Flow straightener

      - Turbine

      - Gearbox

      - Generator

      - Cooling system

      - Outlet Valve

      - Bypass Valve

    - General-mechanical power Sub-systems

      - Surge Protection

      - HVAC

      - Pumps

    - Pipeline, Civil structures and Building

      - Inlet Pipe

      - Outlet Pipe

      - Turbine Inlet Pipe

      - Turbine Outlet Pipe

      - Sub-structure

      - Super-structure

      - Building small power and lighting

      - Building plumbing

      - Loading Bay

      - Plinths for valves, turbine, generator, gearbox, etc

      - Pipeline support structures

      - Surge protection support structures

      - Access road

      - Fencing

      - Rerouting of existing services

    - Architecture

      - Circulation, staircases, passages and Entrance lobby

      - Turbine room

      - Storage area

      - Loading zone

      - Ablutions

      - MV Switchgear Room

      - LV Switchgear Room

      - Transformer bays

      - Standby Generator room

      - Battery and UPS rooms

    - Electrical Sub-systems

      - Turbine Generator

      - Excitation and Synchronization Control System for the Turbine Generator

      - MV Switchgear

      - LV Switchgear

      - Protection Systems, Configuration and Metering Panels

      - 400V Distribution and Control Panels for the overall system

      - 110 VDC Batteries with charger

      - Power transformers

      - Revenue metering

      - Transmission line

      - Backup generator

      - Uninterrupted Power Supply (UPS)

      - Small Power and Lighting

      - Earthing and Lighting protection system

      - Cabling

      - Breaker Protection

    - Automation Sub-systems

      - Instrumentation

      - Flowmeter

      - Programmable Logic Controllers (PLC’s)

      - Supervisory Control and Data Acquisition (SCADA)

      - Human Machine Interface (HMI)

      - Tele-communications

      - Ethernet switches

      - Communication network

    - Logistical Sub-systems

      - Maintenance Personnel

      - Operating Personnel

      - Spares

      - Documents

      - Tools

# Rand Water Furnished Items

The following items shall be furnished by Rand Water:

      - Existing Upstream Pipe

      - Existing Downstream Pipe

      - Reservoir level meters

      - Existing Reservoir Inlet Structures

      - Rand Water Standards and Specifications

      - Construction Sites

      - Water Use Licenses (where applicable)

      - A connection point for potable water, equivalent for domestic use.

      - Electricity for construction offices (the contractor to provide power for all other construction power: welding, operating construction machinery etc

# System Characteristics

    - Required states and modes

The operation of the hydropower sites shall be according to the following modes:

- Bypass or Standby Mode

- Startup Mode

- Run Mode

- Shutdown Mode

- Trip Mode

- Emergency Trip mode

- Maintenance Mode

- Alarm mode.

Trip

Shutdown

Run

Startup

Bypass

/      Standby

Emergency Trip

Monitor for Emergency Trip

Raise Alarms

Maintenance

IT IS CRITICAL THAT WATER SUPPLY OVERRIDES POWER SUPPLY. THEREFORE, WATER SUPPLY REQUIREMENTS SHALL BE MET FIRST AND THEN POWER GENERATION REQUIREMENTS SHALL FOLLOW.

The reservoir’s hydropower operational requirement is through water flow control. Depending on the demand for water, a certain flow is ordered from Rand Water’s Bulk Water Distribution which becomes the flow set point which has to be maintained.

It is important that the average flow is according to the set point and that the water level in the reservoir is controlled within predefined levels. It shall also be possible to vary the set point and operational mode remotely from the control room at   Central Depot, Benoni Depot and Esselen Park Depot.

      - Bypass or Standby Mode

The construction of hydropower plants shall allow for a Bypass or Standby mode. In this mode the hydropower plant is not in operation and the Employer’s hydraulic system is operated exactly as it was operated prior to the installation of the hydropower system using the pressure break inlet structure at the reservoir site. The generating plant needs to be bypassed for whatever reason.

      - Startup Mode

The Startup mode is the transition from the Bypass/Standby to Run mode and includes:

- Enablement of Startup mode by means of a Human Machine Interface (HMI) command or a system automated Startup command

- Indication that startup sequencing is in progress

- All startup sequencing processes i.e.

  - system status checks

  - closing and opening of valves

  - closing and opening of electrical circuits

  - starting up of cooling systems

  - checking of levels, pressures, flows, etc

  - any other check or action required for startup

- Confirmation that all startup interlocks are in order (i.e. the whole plant is ready for operation)

- Opening and closing of valves to gradual rotational speed increase up to synchronous speed

- Confirmation that startup sequencing process is complete and that the system is ready to synchronize

- Indication that the system is “Ready for Synchronisation”

During the execution of the Bypass/Standby mode, the system shall monitor for any alarm condition in which case the alarm shall be raised. During the execution of the Bypass/Standby mode the system shall monitor for any trip condition in which case the Startup mode shall be aborted and the Shutdown mode shall be immediately activated.

      - Run Mode

The Run mode covers the running of the hydropower system and includes:

- Gradual increasing of the turbine load

- Gradual opening of the radial gates as the turbine load  increases

- Management of electricity output within the hydraulic constraints of the Employer

During the execution of the Run mode the system shall monitor for any alarm condition in which case the alarm shall be raised.

During the execution of the Run mode the system shall monitor for any trip condition in which case the Start- up mode shall be aborted and the Shutdown mode shall be immediately activated.

      - Shutdown Mode

This Shutdown mode is the transition from the Run to the Trip modes and includes:

- Enablement of the Shutdown mode by means of a Human Machine Interface (HMI) command or System automated Shutdown command

- Indication of shutdown sequencing in progress

- All shutdown sequencing processes i.e.

  - system status checks

  - closing and opening of valves

  - closing and opening of electrical circuits

  - checking of levels, pressures, flows, etc

  - any other check or action required for shutdown

- Confirmation that all shutdown interlocks are in order (i.e. the whole plant is ready for shutdown)

- Actions required to reduce load on the turbine gradually to zero

- Confirmation that the sequencing process is complete and that the system is ready to trip.

During the execution of the Shutdown mode the system shall monitor for any alarm condition in which case the alarm shall be raised.

During the execution of the Shutdown mode the system shall monitor for any trip condition in which case the Shutdown mode shall be aborted and the Trip mode shall be immediately activated.

      - Trip Mode

This Trip mode is the transition from the Shutdown to the Bypass/Standby modes and includes:

- Enablement of the Trip mode by means of a Human Machine Interface (HMI) command or System automated Trip command

- Disconnection of the Generator from the supply

- Indication of trip sequence in progress

- All trip sequencing processes i.e.

  - system status checks

  - closing and opening of valves

  - closing and opening of electrical circuits

  - checking of levels, pressures, flows, etc

  - any other check or action required for tripping

- Actions required to reduce speed on the turbine gradually to zero

- Confirmation that the trip process is complete and that the system is ready to go into Standby Mode

During the execution of the Trip mode the system shall monitor for any alarm condition in which case the alarm shall be raised.

During the execution of the Trip mode the system shall monitor for any emergency trip condition in which case the Trip mode shall be aborted and the Emergency Trip mode shall be immediately activated.

      - Emergency Trip Mode

The Emergency Trip mode is the Trip mode combined with an emergency trip condition which requires the system to be tripped immediately. Precautionary measures shall be built into the system to minimize the risk of damage of any kind to the hydraulic network (i.e. pressure surges) of the Employer.

In the event of an electrical or mechanical fault or protection operation, the Generating Plant shall automatically shut down in a controlled manner and be electrically and hydraulically isolated even if the local power supply is lost.

The unit shall remain isolated until the arrival of an operator at the site to check and manually restart the Generating Plant. Provision shall however be provided for future remote resetting of any protection relays prior to restarting.

- Enablement of the System automated Trip command

- Disconnection of the Generator from the supply

- Pressure surge control

- All Emergency Trip sequencing processes i.e.

  - system status checks

  - closing and opening of valves

  - closing and opening of electrical circuits

  - checking of levels, pressures, flows, etc

  - any other check or action required for Emergency Trip

- Actions required to reduce speed on the turbine gradually to zero

- Confirmation that the trip process is complete and that the system is ready to go into Standby mode.

During the execution of the Emergency Trip mode, the system shall raise the alarm condition(s) which caused the Emergency trip.

      - Maintenance Mode

The Maintenance mode shall be used when the system is taken out of operation for maintenance or repairs and shall disable the use of the system.

      - Execute alarms

Alarm conditions shall continuously be monitored and alarm shall be raised when it occurs.

# Design and Construction

Design and construction requirements for sub-systems are dealt with in section 3.7.

# Documentation

All relevant documentation shall be forwarded to the Engineers representative for acceptance prior to manufacture.

Drawings and information

- Should the makers consider any of the drawings or information to be confidential, the documents shall be marked "CONFIDENTIAL" and they will be treated as such by Rand Water.

- Sufficient information shall be given on the drawings to enable replacement parts to be identified and ordered, if necessary.

- All communications, pamphlets and technical literature shall be in English.

- Two sets of CD shall be supplied with the accepted "CAD" drawings tabled and stored in a format that can be loaded, edited and printed

- All drawings shall utilise the WKS codification system for identification of plant  elements.

- Drawings shall have the following information near the title block or within the title block:

  - Station's name

  - Location where used

  - Equipment/infrastructure description

  - Drawing description

  - Drawing number

  - Revision umber Drawing and information to be supplied

- The following drawings and information (as a minimum) shall be submitted with the tenders. these drawings shall be supplied in both an electronic (1 X CD) and hardcopy format (3 x sets):

  - Overall hydroelectric plant layout.

  - Hydroelectric power plant buildings.

  - Details for the proposed connections to existing Rand Water infrastructure (provision must be made to generate As-Built drawings for proposed existing Rand Water infrastructure – there are no As-Built drawings for existing infrastructure)

  - Typical detail drawings of main proprietary items (but specifically the hydromechanical set and its auxiliaries).

- The following preliminary and detail drawings (shall be supplied by the contractor for acceptance by the Engineer after receipt by the contractor of Rand Water's letter of acceptance of the tender before manufacture commences. These drawings shall be supplied in both an electronic (1 X CD) and hardcopy format (5 x sets). The drawings shall include as a minimum but may not be limited to the following details:

  - Detail construction drawings of all civil / structural plant.

  - Detail drawings of all equipment as well as details of the combined equipment sets.

  - Safety plan and COVID plan.

  - Detailed manufacturing programme with milestones for activities such as drawings, approval of drawings, galvanising, pre-machining etc.

  - All general, assembly and detail drawings necessary.

  - Quality assurance plan and Quality Control Plan

- The engineer may require the contractor to submit, for acceptance, drawings additional to those listed above. The contractor shall supply a complete set of final drawings covering all the equipment supplied and shall submit a list of the final drawings and information that it is proposed to supply. This list shall include all the drawings listed above and shall be approved by the engineer.

- No construction, manufacture, assembly or any undertaking before drawings are reviewed and approved by the Rand Water engineer or delegated representative(s).

Operating and maintenance manuals

- Fully indexed illustrated operating and maintenance manuals for the complete equipment shall be provided. The draft copy shall be submitted to the engineer for approval four weeks before the plant is put into service. Three copies of the approved manual shall be supplied to the engineer within four weeks of the draft copy being approved.

- The manuals shall cover the following aspects in detail, with photographs, isometric assembly drawings, illustrations and drawings:

  - Detailed operating instructions

  - proposed preventive maintenance schedule and programme covering each component including lubrication and special lubricants

  - spare parts list

  - schedule of manufacturing drawings and parts list

  - schedule of maintenance tools provided and the use of special tools

- For ease of reference and handling, the document may be divided into separate volumes each relating to the specific sections of the work.

- After installation of the equipment, alignment records shall be provided for inclusion in the manual.

- All data included in the manual shall be produced on standard A4 size sheets. The materials used shall be resistant to oil and dirt

- Each document shall bear the title specified

- Should the makers consider any of the drawings or information to be confidential, they will be treated as such by Rand Water. Final payment will not be made until the final approved versions of operating and maintenance manuals have been received.

# Major Component Characteristics

# Civil Structures and Building

      - Scope

This Schedule sets out the design and construction requirements for civil structures and building works including but not limited to;

- Detection, rerouting and protection of existing services

- Geotechnical investigations at the specific location of hydropower infrastructure namely: Bronberg, Hartebeeshoek, Brakfontein and Klipfontein reservoir sites where building structures will be constructed

- Reinforced concrete structure to house the Hydro power turbines with beams for the crane system

- Plinths for valves, turbine, generator, gearbox, etc.

- Loading Bay

- Building plumbing

- Electrical and Automation Equipment Buildings at the sites

- Access platforms and installation of hand railing where required

- Access roads, the contractor should confirm with Rand Water Team as some of the site already have ongoing access road projects outside this project

- Allowance for overflow system

- Storm Water drainage system

- Valve chambers where required

- Fencing to the various buildings

- Pipeline support structures

- Surge protection support structures

- Attending to defects during the defects liability period

      - Design criteria

The design shall be in accordance South African Design Codes and other relevant British codes.

The design and materials used for construction shall be in accordance with the relevant standards specified in the Contract. Where no particular standard has been specified the use of South African Standards will be applied.

      - Civil structures and buildings

The Contractor shall allow for the appointment of a Civil and Structural Engineer registered as a Professional Engineer or Technologist with the Engineering Council of South Africa, who shall provide full civil and structural engineering services related to any and all elements affecting the structural integrity of the works including, geotechnical survey, foundations, reinforced concrete, load bearing brickwork, steel and timber roof construction, pipe work and specials and any external work such as paving, road works, concrete chambers, storm water and drainage.

The buildings and structures must be designed, fit for purpose and in line with Rand Water’s high standards for buildings. The design shall be done by a Professional Civil Structural Engineer registered with the Engineering Council of South Africa.

The best material and furnishes shall be used to ensure an expected life span of 50 years minimum. The design shall provide for all applicable services including electrical (small power), sanitation, ventilation etc. in accordance to SANS 10400.

Where applicable the material and furnishes of the proposed buildings should match the existing structures on site.

      - Valve chambers

Where Valve chambers have to be constructed, these shall be designed to provide adequate working space around the pipes for the installation and removal of valves and pipe fittings. Valve chambers shall have adequate ventilation and should comply with the Rand Water functional specification for Chambers as provided.

Please refer to the Valve Chamber functional specification as provided for additional requirements – Document: Chambers Functional Spec_Rev 4.

      - Roads

Roads within the power plant / reservoir perimeter must be paved and designed to the following standards:

Geometric Design: TRH 17 (1988) - Geometric Design of Rural Roads Road Markings and Signage: SADC Road Traffic Signs Manual, 3rd Edition

The Contractor shall ensure that the geometric design of the roads is sufficient to accommodate the delivery trucks and construction equipment. All roads shall have a minimum width of 6 m.

All roads and paved areas, such as parking areas must be kerbed in accordance with SANS 927. Sidewalks must be constructed with inter-locking paving blocks to connect all buildings and shall have a minimum width of 1000 mm.

All standard road signs, road markings, as well as direction signs to the various areas and buildings around the power plant must be provided.

      - Storm water

The routing of storm water should ensure that all runoff flows do not cause any erosion, piping or damage to the natural environment. The stormwater network must be designed to the South African National Roads Agency Limited Drainage Manual 6th Edition. Stormwater management should take cognisance of the Guidelines for Human Settlement Planning and Design (Department of Housing, South Africa, 2000).

The contractor shall develop a Storm water Drainage Plan for all sites and will be responsible to ensure that the run-off from the site will discharged to the drainage ways and river where applicable without causing erosion, piping or damage to the natural environment. No facilities shall cause flooding of the site during a 100-year storm event. The Storm water Drainage Plan shall be submitted to the Engineer for approval.

The Contractor shall satisfy himself as to the characteristics of the water tables at the various plants. If necessary the Contractor shall allow in his design of all structures for the drainage of sub-surface water away from all structures. This water shall be safely conveyed to the stormwater system as part of the Stormwater Drainage Plan.

Construction and post-development peak flows from the site shall not exceed the pre-development peak flows for the 2, 5 and 10 year storm events respectively.

      - Construction

All civil works shall be constructed in accordance with the requirements of SANS 1200 as may be modified by the variations and additions to the standard specifications.

      - Fencing

Fencing shall be the same as what exist on the respective sites.

# Structural Engineering Requirements

      - Scope

This Schedule sets out the design and construction requirements for the structural engineering works.

      - Design criteria

The design will be in accordance with South African Design Codes, or in the event of the non-existence of a particular Code, the design will be in accordance with British Design Codes.

Load considerations to be adopted in the design of the structures shall include, but may not be limited to, as described in the relevant codes:

- Uplift forces

- Live and dead loads

- Earth loads

- Wind forces

- Applicable environmental loads

- Seismic activity

- Equipment vibration

Should hydraulic testing of the structures be carried out prior to the backfilling against walls, the design must allow for this loading condition.

This type of development usually requires the design of reinforced concrete tanks and channels for the various processes to be impermeable, and the design of single story masonry structures to house the controls and to serve as storage areas. Other auxiliary items such as access walkways, overhead gantries, thrust-blocks, etc, may also be required.

The design criteria shall be in accordance with the SANS 10400: The application of the National Building Regulations

Other relevant applicable design codes are:

SANS 10100-1 : The Structural use of concrete Part 1: Design

SANS 10100-2 : The structural use of concrete PART 2: Materials and execution of work.

SANS  10160: The general procedures and loadings to be adopted in the design of buildings.

SANS 10161 : The design of foundations for buildings

SANS 10164-1 : The structural use of masonry Part 1: Unreinforced masonry walling

SANS 10162 PART 1 : The structural use of steel

BS EN 206-1:2000 Concrete. Guide to specifying concrete

BS 8007 : Code of practice for design of concrete structures for retaining aqueous liquids.

BS 8110 : Structural use of concrete Part 1: 1997

      - Foundations and below ground structures

The foundation type and size shall be based on geotechnical investigations. The onus will be on the Contractor to establish the safe bearing capacity of the foundations and to design them accordingly.

      - Water retaining structures

Water retaining structures are to be designed in accordance with BS 8007, allowing a hydrostatic pressure of 10 kN/m2 per metre depth.

The concrete mix, spacing and type of movement joints, the reinforcement detailing, etc, shall be such to take the water-tightness requirements into consideration. Where required, concrete surfaces shall be sealed protecting it against chemical attack.

No wood shuttering will be allowed. Un-formed surfaces in water retaining structures shall be steel-floated. Power plant and building floors shall be wood-floated.

A gasket shall be installed at the bottom of formwork to prevent loss of fines.

A maximum design crack width of 0,2mm is specified for water retaining structures.

The minimum wall thickness of structural walls will be 250 mm and that of baffle and channel walls will be 200 mm.

A minimum 5 day delay between adjacent concrete placements must be allowed to minimize the effects of shrinkage.

All civil works shall be constructed in accordance with the requirements of SANS 1200 as may be modified by the Particular specifications included in Portion 2 of these Employer’s requirements.

Continuous water stops shall be PVC

      - Construction

The structural works shall be constructed in accordance with the requirements of SANS 1200, BS 8007, BS 8110 and BS EN 206-1:2000

No wood shuttering will be allowed for external, above ground level applications. Un-formed surfaces in water retaining structures shall be steel-floated and pump-station and building floors shall be wood-floated. A Degree of Accuracy II, as defined in SABS 1200G, will be applicable on all structural work.

The Contractor’s attention is particularly drawn to the fact that no honeycombing will be tolerated in walls that form part of a water retaining structure. In order to ensure this, the mix proportions of the first 250mm depth of concrete placed in contact with the horizontal joint may be adjusted, with the approval of the Engineer, by reducing the amount of coarse aggregate. The Engineer may instruct the use of trunking in placing the concrete to avoid losses of fines due to adherence to reinforcement and formwork. The concrete shall be placed evenly over the surface to be covered without reliance on vibration to transport it horizontally. Special care shall be given in order to ensure full compaction at water stops.

Should honeycombing occur on water retaining and non-water retaining structures, the Contractor shall submit a method statement for the proposed repair of the affected area for the approval of the Engineer.

# Architectural Requirements

      - Scope

This section covers the design criteria which shall be used for all architectural work related to this project. Architectural work includes:

        - All buildings,

        - Aesthetics and colour.

      - General design criteria

Design shall be in accordance with South African Building Regulations SABS 0400:1990 and local bylaws. All buildings shall be aesthetically compatible with existing structures on site. Buildings shall be of fire resistive construction in accordance with SANS 10177:2007, SANS 1709:2008 and SANS 11820:2008. The buildings shall have access allowances for removal, replacement or addition of equipment. Energy conservation measures, in accordance with SANS 204:2008, shall be incorporated into building design.

Interior finishes shall be durable and easily cleaned. Floors shall be finished to provide a smooth, dust free surface and shall be graded to provide adequate drainage.

Specifications for materials shall generally follow the standard specifications of the South African Bureau of Standards (SABS, SANS). Unless otherwise required, building design shall conform to the South African National Building Regulations.

The buildings and structures must be designed, fit for purpose and in line with Rand Water’s high standards for buildings. The design shall be done by a Professional Architect (Pr Arch) registered with the South African Council of the Architectural Profession.

      - Specific design criteria

In addition to the Design Criteria referenced above, there are specific supplemental design criteria required for the Project. These supplemental design criteria shall be included in the Contractor’s design.

Building layouts, room arrangements, general massing of building elements, and architectural concepts are at the discretion of the Contractor provided that the intent of the Contract Documents, state of the industry architectural and engineering standards, state of the industry operation and maintenance standards and requirements, and specific requirements of the Employer are satisfied. Useable floor areas shall be greater than minimum code or standard requirements.

A separate room with controlled access for medium voltage switchgear shall be provided with clearances as follows:

- Rear- Not less than 1500 mm but not exceeding 1800 mm at every point of the switchgear room.

- Front- Double the depth of the switchboard at every point along the length of the switchboard to allow for the withdrawal and handling of circuit breakers.

- Sides- 2500 mm on each side of the switchboard.

- MV switchgear rated at different voltages will be housed in separate MV rooms.

The floor and finish and levelling tolerances of the floor shall be strictly in accordance with the specifications of the switchgear supplier to ensure trouble free operation of the withdrawable switchgear trucks. False floor arrangements will under no circumstances be accepted.

The switchgear rooms shall be equipped with a double door with sufficient dimensions (width and especially height) to enable the switchgear to be installed into the room. Particular attention shall be paid to the landing area outside the doors, preferably a concrete base to enable the switchgear tier sections to be placed comfortably and safely for further installation into the switchgear room.

Each switchgear room shall be provided with two doors preferably at opposite ends of the room for access by operating and maintenance personnel and providing an escape route out of the room in the event of fire or explosion. The doors shall be provided with panic bar ironmongery to facilitate the easy egress from the room.

Custom constructed concrete cable ducts of a minimum depth of 800 mm shall be provided for power cables to be installed on cable racks mounted against the walls of the ducts and to ensure that minimum cable bending radii requirements are met.

The roof or ceiling height of the switch room shall be minimum 3000mm from finished floor level to meet the switchgear arc venting requirements, but shall be determined by the final fault rating of the switchgear and the switchgear suppliers’ arc venting design including possible arc vent ducting, plasma deflectors and absorbers.

No PLC panel, Battery Charger and batteries and UPS’s shall be housed in the any medium voltage or Low Voltage switchgear rooms.

A separate room housing each of the following equipment shall be supplied:

- 400V switchgear or Distribution Switchboard

- Battery charger and stationary tripping batteries

- Transformer bays - separate transformer bay for each transformer unit

- Generator room

- Room for Synchronising panel(s), changeover panel(s) and panel(s) for transformer protection schemes (separate suit of panels for each of these functions where required).

The standby diesel generator and auxiliary transformer shall each be housed in separate rooms and be supplied with roller shutter doors for access to the exterior of the building.

The Contractor in his design shall account for the potential for rainfall and therefore shall eliminate the option of rainfall from buildings cascading down and potentially staining, or causing major maintenance of, exterior surfaces. The architectural style shall convey this sense of function and durability yet shall be compatible with existing building styles.

All buildings shall be of reinforced concrete, including but not limited to:

- Substructures and slabs;

- Frame;

- Stairways; and

- Roofs.

All building infill shall be concrete masonry units. All floors shall be hardened concrete finish.

Parapets and screens shall be of reinforced concrete and shall conform to the same functional and aesthetic qualities of buildings. Where sunshade type structures are permitted, they can be constructed from appropriately sized structural steel members that shall be painted following erection. Local construction materials and techniques shall be utilized when practical and consistent with long facility life.

Minimum ceiling height in all buildings shall be 3 meters. Buildings where hoists or cranes are permanently installed, or where temporary hoists are required, shall have heights dictated by appropriate distances and clearances for the hoisting equipment, hoisting motors, chains and hooks; equipment being moved; and level of receiving vehicle.

The Employer shall approve all arrangements, building and room sizes, massing of building elements, architectural treatments and proposed materials to be used prior to final design. The Employer reserves the right to reject any architectural concepts and details and to require rework and re-submittal to satisfy strictly aesthetic, as well as size, material and functional, concerns.

Storage facilities shall be designed and built according to the agreed requirements of the operating entity. The Contractor shall design and construct storage facilities for spares and / or other materials required for the operation of the works. Separate storage areas shall be provided for dry and liquid materials. Areas for liquid materials shall be bunded to contain the liquids. Storage facilities for hazardous chemicals shall comply with the requirements of the relevant safety regulations.

      - Roofs

All roof coverings shall be according to codes and South African National Standards (SANS) standards. All roofs shall slope to external walls and not over doorways, sidewalks, or other areas likely to be occupied by personnel. Parapets may not be used at roof edges to control drainage and shall discharge into concealed gutters and conveyed down walls via downpipes. All drainage systems shall include provisions to control sand infiltration and blockage.

Roof hatches shall be installed to give roof access where required for access to equipment and to each level of structures to allow convenient access from the interior of the buildings.

Roof insulation above all ceilings shall be installed and shall consist of at least 100 mm of fiberglass. Insulation below all roof coverings shall consist of Sisalation, or equal approved.

      - Exterior Doors, Windows and Louvres

Windows areas in buildings shall provide a light, airy and comfortable environment.

Windows and louvres shall be of bronze anodized aluminum. Doors shall be bronze anodized aluminum or steel suiting the application. All doors, windows and louvers shall be of highest quality. All gaps between doors, windows and other opening frames and the wall shall be appropriately sealed for the atmospheric conditions. Doors and windows shall have appropriate seals for extreme weather conditions. Glazing shall be thermally efficient, tinted to control ultraviolet light and contain reinforcement as required by codes and SANS standards. All doors shall have fire safety panic hardware where required, swing out, and have locks with a keying scheme acceptable to the Employer.

Buildings containing equipment that requires removal by hoists or other mechanical means shall be provided with equipment access doors of sufficient width and height to permit appropriate movement of the equipment and any vehicle access required. Separate personnel access doors shall be provided in addition to the equipment doors.

      - Fire and safety design criteria

Fire and safety design shall be in accordance with Code of Practice for the application of the National Building Regulations.

The design shall comply with the following standards:

- SANS 10400 - A: 2010: General Principles and Requirements.

- SANS 10400 - W: 2011: Fire Installations.

- SANS 10400 – T: 2011: Fire Protection.

- SANS 10252 – 1: 2012: Water Supply Installation for Building.

SANS 10139: 2012: Fire Detection and Alarm Systems for Buildings – Systems Design, Installation and Services

All structures shall be designed with fire resistant materials and adequate fire exits to minimize risk to personnel. Fire suppression and detection systems shall be provided as required.

      - Interior lighting

The lighting system shall provide personnel with illumination for operation under normal conditions, means of egress under emergency conditions, and emergency lighting to perform manual operations during a power outage.

Natural lighting shall be used where possible in the switchgear and control rooms. Care shall be taken that there are no reflections from natural lighting on instrument and relay facias installed on the switchgear.

Minimum lighting levels at floor level shall be 300 lux both in front and at the rear of medium voltage switchgear panels, and 500 lux in the control room. The lighting systems shall be designed in accordance with the illumination to applicable levels recommended by SANS Standards, Industrial Lighting.

Emergency lighting shall be powered from the standby diesel generator set to be supplied. Lighting levels in front and behind the switchgear panels and in the control room shall be a minimum of 150 lux under emergency lighting conditions.

The selection of light fittings shall be such as to achieve the highest possible energy efficiency.

The permanent lighting system shall be used for construction lighting in areas where early installation is feasible. Temporary construction lighting shall be utilized in all other areas.

The power supply for the lighting systems shall be from 220/380 volt, 3-phase, and 4 wire lighting panel boards.

      - Submittals

The Contractor shall prepare the following submittals for Employer review and final selection before work begins:

- Plans, sections and elevations

- Room data sheets

- Finish schedule for each room in each building;

- Door and window schedule;

- Hardware schedule;

- Material samples and colour boards. The samples and boards shall be of appropriate size and organized in such a manner as to artistically and effectively illustrate both the selection and coordination of colours and finishes for the exteriors of buildings and in each room and work area; and

- Lighting fixture schedule and luminosity values proposed for each room in each building.

- Heating, ventilation and air-conditioning requirements for each room

- Concrete formwork or shuttering

      - Painting and coating

        - General

The Contractor shall paint/coat surfaces subject to weathering, deterioration and corrosion with appropriate materials to provide highest quality protective coatings capable of meeting or exceeding manufacturer’s longevity guarantees under the service and environments to be experienced by the materials and coatings. All coating materials, to the extent feasible, shall be from one manufacturer.

The Contractor shall provide the following at least thirty days prior to starting any painting on the project:

- A list of all surfaces to be painted/coated, the type of the proposed material, and the type of any factory installed primary coatings to be covered along with the paint/coating manufacturer’s recommended compatibility. In addition, manufacturer’s leaflets including directions for the preparation of surfaces, usage of products and recommended thickness of dry coats;

- Colour scales with all available colours. After approval of the colours selected, the Contractor shall submit samples of each colour paint with dimensions 300 x 300 mm. Each sample shall be designated with the type of finish, number and name of the colour, type of lustre, units of lustre and batch number.

- The manufacturer’s recommended quality control program for testing and control of the materials to be used shall be complied with.

- Paints and coating materials shall be delivered in factory-sealed containers with a label indicating

the name of the manufacturer, the type of paint/coating, production date and instructions for mixing and thinning.

- Adequate enclosed and well-ventilated storage areas shall be provided separate from storage for other construction materials. Storage temperature of these areas shall be maintained within ranges recommended by the manufacturer.

- Paint/coating containers shall only be opened immediately before usage. Materials with expired dates of usage shall not be used.

- The supply of all paint materials shall come from highly reputable and internationally acknowledged paint manufacturers, and shall be of the highest quality.

- Field applied intermediate and finish coats shall be compatible with factory applied primary coatings. Products used for successive coats shall come from the same manufacturer.

- To the extent possible, all stored paint/coating materials shall be ready for use as stored. Insoluble pigments shall be completely ground so as to present the texture of a soft putty and be capable of being evenly spread as a homogeneous mixture using a brush, a roller or a spray gun according to recommendations of the manufacturer.

        - Surface preparation

Surfaces shall be smooth and without faults. Appropriate fillers providing maximum bonding capability may be used. Fillers shall be used as recommended by the filler and paint/coating manufacturer’s recommendations.

All metal surfaces shall be made near white.

All surfaces shall be smoothed, dried and cleaned in accordance with the paint/coating manufacturer’s recommendations. The Contractor shall pay particular attention to surface and atmospheric humidity requirements and shall not apply paints and coatings when surface and/or atmospheric humidity are within 75% of the paint/coating manufacturer’s recommended maximum limits. Bare surfaces shall be primed as soon as possible after preparation is completed, and in all cases never longer than the paint/coating manufacturer’s recommended time limit.

        - Application

The paint/coatings shall have an adequate fluidity, and shall be applied so that the application:

- Dries and hardens without streaks, drips or swellings;

- Has a uniform lustre, colour and texture; and

- Provides a straight, uniform and professional looking delineation between painted/coated surfaces and surfaces not painted/coated, and between surfaces of different colour.

The paint shall be carefully applied according to manufacturer’s instructions. The thickness of the wet coat should be appropriately checked. Each coat of material should be left to dry completely before the application of successive coats in accordance with the manufacture’s recommendations.

Items such as electrical wall plates, metal pieces of frames, handles, locks, and fixtures shall be removed before painting/coating. These items shall be carefully stored, cleaned and replaced to their proper position at the end of the work. The cleaning of metal parts should not be attempted with solvents that may harm their permanent coatings. Items that cannot practically be removed shall be covered.

Grills, caps and inspection covers of electrical and mechanical equipment shall be removed and painted separately.

Conduits, junction boxes, special supports, collars and brackets shall be primed and painted. All conduits and electrical equipment exposed within painted areas shall be painted in the colour and texture to match the adjacent surfaces.

All equipment and pipes shall be painted according to colour codes required by the relevant codes and standards. This includes items such as arrows indicating the direction of flow, inscriptions with identification names, and numbering.

        - Damaged surfaces

Painting/coating shall include restoring paints/coatings in damaged areas to their original thickness and type.

Painted/coated surfaces that have received splatters from painting/coating or other construction activities such as welding, concrete, or plastering work, which results in finish damage or items stuck to the surface, shall be cleaned or washed immediately to clean the surface and remove the items. Repairs or restoration required to a damaged surface shall take place before the surface is repainted/recoated. The surface shall then be restored to its original state. Each coat of new painting/coating shall overlap the existing coat by at least 50 mm.

For the repair of all damaged surfaces, and in particular epoxy layers, only suitable materials recommended and supplied by the manufacturer of the original paint/coating shall be used. The materials shall be applied according to the instructions of the manufacturer.

      - Landscaping

Provision is to made in all open areas between buildings, structures and roads for planting of indigenous trees and other flora to present attractive and pleasing settings which can be easily maintained by local labourers. A landscaping plan shall be forwarded to the Client for review before any such planting is expedited.

# Pipelines

      - Scope

        - Design criteria and scope for the Construction of Pipes and Pipe Specials

      - Design Criteria

- Determine pipe size

Outside diameter for flanged pipes to be determine with the assistance of Rand Water’s Standard Flange Dimensions, drawing number A11791, with the following guidelines:

- 600mm – 1500mm with minimum 4mm deducted from Bore of loose flange.

- 1600mm – 3500mm with minimum 6mm deducted from Bore of loose flange

- Determine thickness of the pipe based on design pressure and slenderness ratio’s with ranges as below:

- D/t≤120 - Plain wall pipes

- D/t>120 ≤150 - Plain wall pipes or Stiffened pipes

- D/t>150 – Stiffened pipes

The final thickness to be determined based on loading, buckling and deflection based on BS EN 1295: 1998.

- Decide the grade of steel with at least two alternatives

- Develop a general long pressure section drawing which should confirm steel grade choice

- Design all openings, fittings and branches to be designed according to BS EN 13445-3

- Design for relevant structural condition e.g, buckling, deflection and vacuum considering soil and traffic load based on BS EN 1295:1998. The pipe must be designed for full vacuum.

- Design for buoyancy

- Determine the maximum and minimum cover

- Determine bedding type based on the Geotechnical Investigation

- Size and decided on valves location including test pressures

- Design corrosion protection including lining and coating

- Chamber design, mechanical and automation and relevant disciplines

- Jointing of pipes

- Include sufficient allowance for transient pressure

- Allow for different operating pressure

- Recommendations of operation and maintenance manual

- Design of Blasting requirements

- Design of protection of existing services

- Design for construction

- Prepare bill of quantities

- Prepare technical specifications

- Do cost estimate

See table below for design parameters that needs to be adhered to:

Table 1: Pipeline Design Criteria

      - List of standard drawings

These documents generally refer to general requirements in the designing and building of a pipeline and do not convey substantially the system design, however these are indicative and the Contractor must neither consider these as detailed designs nor approved for construction nor suitable for use in deriving the costs estimates on which the contractor can determine the contract price.

The following drawings can be found under standard drawings in Appendix F.

Table 2: Standard Drawings Pipelines

| Number & Title/Description | Type |
| --- | --- |
| - A5478 Standard Colour for Marking Steel Pipes | Typical |
| - A9548 Insulating Flanges | Typical |
| - A11791 Flange Dimensions | Typical |
| - A12210 Valve Support | Typical |
| - B1933 Details of culvert for road crossings | Typical |
| - B1934 Details of saddles | Typical |
| - 13057 Sluice valve | Typical |
| - R023517 Details Air Valve Chambers in road | Typical |
| - R023518 Details of Air Valve Chambers in road | Typical |
| - RA23557 Fabrication details of pipe-ends | Typical |
| - RA26448 Typical Puddle Flanges | Typical |
| - RA26732 Tapers and Bends | Typical |
| - R028060 Details of Air Valve Chambers | Typical |
| - R0238061 Details of Scour Chambers | Typical |
| - RB18951 River Crossing | Typical |
| - R027141 Trench Excavation and backfilling | Typical |
| - R028537 Typical Sign Board | Typical |
| - Cathodic Protection Typical Cable Trench | Typical |

      - The Construction Scope of the Pipeline Section covers:

- General Requirements

- Transporting and Unloading of Pipes

- Handling of Pipes

- Rerouting of Pipelines

- Installation of Steel Pipes/Specials

- Welded Joints

- Specials

- Welding

- Cleaning

- Charging of Pipeline

- Maintenance

- Acceptance of pipeline

      - General Requirements

Under this Section of the contract the Contractor shall:

(i)	Identify, establish and prepare to the satisfaction of the Engineer, temporary lay-down areas for the pipes and specials to be delivered to site.

- Arrange for the unloading of pipes and specials from the trucks to be delivered to site.

- Identify and check the conditions of the steel pipes and specials as they are delivered to site. Any pipes that are defective are to be reported to the Engineer and arrangements made with the Contractor for its repair.

- Install the pipes and specials in the trenches and make the necessary joints.

(ix)      Provide equipment and material and carry out radiographic examination of welded joints.

(xii)    Make good the external coating, internal epoxy lining at joints and clean out the pipeline.

      - Transporting and Unloading of Pipes

The Contractor shall examine visually and by means of the appropriate detectors, on arrival of the pipes prior to off-loading, the external coating and internal lining of all pipes in the presence of a Rand Water representative. Any defects must be recorded and shall be repaired by the pipe supplier.

The Contractor shall unload the pipes from the supplier’s trucks and lay them down in the temporary indicated lay-down area and/or certain positions along the route of the pipeline on sand bags.

The pipes at all stages, shall be protected against damage, and shall be lifted by means of approved broad- band slings and spreader beams.

The use of chains, wire ropes, etc, will not be permitted and the pipes shall be supported on pipe storage mounds provided by the Contractor while in the storage areas or when placed alongside the trench. (Sawdust filled bags shall not be used).

      - Handling of pipes

The Tenderer shall state in his offer the plant he proposes to use for unloading, bracing and placing the pipes and specials in the trench. All plant shall be subject to the approval of the Engineer. The plant and bracing shall be designed so as not to damage the pipes, the lining and sheeting or disturb existing pipelines.

Before placing the pipes in the trench the measures taken to ensure the safety of the operations, the material and compaction of the trench floor and the finished line and grade of the pipe bed shall be carefully checked between survey pegs by the Contractor. The Contractor shall check the joint holes for each pipe length and permission to lay obtained from the Engineer’s Representative. The pipes and specials shall then be placed in the trench, installed and jointed in accordance with the specification.

The Contractor shall keep the pipe trench and excavations free from water at all times during the pipe laying operations.

      - Rerouting of Pipeline

The required activities are as follows:

- Investigate proposed route.

- Design pipeline for selected route.

- Supply additional pipe and bends as required.

- Install pipeline (clear and grubbing, excavation, bedding, pipe laying, jointing, lining and coating, testing and commissioning).

- Remove installed pipe to Emhlangeni storage site if not used.

- Join new pipe into existing pipe (this will require RW’s shut down procedures to be adhered and the involvement of internal stakeholders).

The pipe need to be at least 10m clear of the Proposed Turbine Hall Structure. All pipeline designs need to be as per the 3.7.4.2 and the installation should be as per the rest of this section; and the SAM DOP 00001 TS should be consulted on any additional activities.

      - Installation of steel pipes/specials

Preparation

- Before a pipe and specials section is placed in the trench the internal and external protective coatings shall be examined visually and by means of a Holiday detector of the correct type and rating for the particular coating system. No pipe shall be laid without the permission of the Engineer’s Representative. The Tenderer shall state in his offer details of the equipment that will be provided to carry out Holiday detection on the site.

- Any manufacturing defects located in the coatings shall be reported immediately to the Engineer who will make arrangements for the repair of the defects.

- Any damage to the sheathing caused during unloading or while the pipes are stored on the site. The Contractor shall make the site good.

- When making joints or doing any other work inside the pipe, every care shall be taken to avoid damage to protective coatings. Rubber matting shall protect the invert surfaces of the pipe or by timber duck-boards at least 400mm wide and the coatings shall be protected during welding from weld spatter, hot slag, etc. using rubber matting.

Cleaning of Joints

- Just prior to the installation of any section of pipe, all foreign matter of every nature and all protective material shall be removed from the surfaces that are to be in contact at joints, so as to leave thoroughly clean surfaces for metal-to-metal contact in the field joints.

Laying Pipe

- Each pipe/special shall be accurately laid on the prepared bed to the required line and grade. In placing pipe in the trench, the pipe shall be held by an approved sling, at least 0.4m wide, and the pipe/special shall not be dragged on the bottom of the trench but shall be supported by the sling while being fitted to the adjacent pipe/special section.

- After each pipe/special has been set into position it shall be attached to the adjoining pipe/special by means of an arc-welded joint. The use of dogs, clips, lugs or equivalent devices welded to the pipe for the purpose of forcing it into position will not be permitted.

- The Contractor shall remove any dents, which appear in the wall of the pipe, after the cause or the object causing the dent has been located and removed. The cost of removing the dent and making good the lining, wrapping and backfilling shall be borne by the Contractor.

- Any damage to the pipe during or after laying shall be made good and for this purpose the Inspector may require the pipe or section thereof to be removed from the trench and replaced with pipe which is free from defects.

Completing coatings at joints.

- As soon as the field joints have been welded the coating at such field joints shall be completed in accordance with the following procedures:

External coating (Butyl Mastic Strips) (when applicable)

- Feathering of the Sintacote edges

- Removal of all grease and other deleterious matter.

- Cleaning, scraping and abrading to obtain ISO 8501-1 St 2

- Removal of weld splatter.

- Application of Denso primer D or equivalent primer to all prepared surfaces including overlap on to the Sintacote.

- Profiling of welds and Sintakote prepared edges with Denso quad ply tape or equivalent tape.

- Application of Denso CPT 1000/400 tape or equivalent tape at 55%overlap to all primed surfaces.

- Hi spark test at 20,000 volts DC.

All air bubbles shall be excluded. No other product shall be used unless the Contractor has obtained the written permission of the Engineer.

External coating (Glass-fiber reinforced bitumen) (when applicable)

- After welding and the necessary examination have been carried out, the surface of the pipe to be made good shall be wire brushed, using mechanically operated tools, to remove loose rust and slag from the weld. The surface roughness shall be minimum 50 µm. The cleaned area has to be primed using Bitugaurd Synthetic or equivalent primer which has to be spray or brush applied.

- Application of Bitugaurd Field Joint membrane or equivalent membrane can be performed by either manual or semi automatic application techniques. The membrane has to be pressed firmly against the pipeline steel until whilst being heated by a propane torch. The membrane is progressively unrolled around the pipeline circumference, keeping a thin bead of molten adhesive between the steel and membrane. This techniques ensures that all air is expelled.

External coating (Rigid Polyurethane) (when applicable) Preparation of the field joint for coating

General

- The surface to be coated shall be, at the time of application of the coating, dry and free of any contamination (such as dust, non adhesive particles, grease, oil, soluble salts, etc.) detrimental to surface preparation or to adhesion of the coating on the steel.

If appropriate, extra cleaning shall be carried out to remove the following :

- Greasy and waxy substances (using a totally volatile solvent, as required), or other contamination;

- Weld spot, slag, burrs that can pierce the coating (using approved grinding or filling techniques)

- Areas of rust or scaling shall be removed by spot abrasive blast cleaning as indicated on the appropriate application procedure.

Blast Cleaning

- All  types  of  abrasive  that  are  used  in  the  preparation  of   field  joints   shall  comply   with   ISO 11123-2 to 4.

- The preferred method of preparation of the substrate shall be abrasive blast cleaning. Recycling of abrasive is accepted only if suitable abrasive and equipment is used by the applicator. The minimum standard of cleanliness of the surface after abrasive blast cleaning shall be ISO 8501-1 SA 2.5.

- All surface imperfections, that are detrimental to the performance of the field joint coating, shall be removed by an approved technique, and the residual thickness of the pipe wall checked. This shall satisfy the minimum tolerance of the standard. The profile / roughness shall be checked in accordance with the requirements of ISO 8503-1 or ISO 8503-4, or Iso 8503-5.

- The profile shall be of and angular and dense nature. In areas where the roughness of the profile has been lessened or lost , abrasive blast cleaning shall be undertaken again, in order to restore the required roughness and profile, the roughness/profile shall be rechecked. All dust detritus and soluble salts etc. shall be removed from the substrate following the initial surface preparation procedure. The level of soluble salts shall be measured in accordance with the requirements of ISO 8502-9 and shall be less than 30mg/m2.

Reconditioning

- If, after preparation of the surface of the joint to be coated, the substrate is contaminated or corroded, the joint shall undergo further partial or total surface preparation in order to be able to apply the coating to a surface that has been cleaned in accordance with the manufacturer’s recommendation.

Preparation of the adjoining plant applied coating

- The factory coated area, either side of the exposed steel pipe, shall be prepared to facilitate the adhesion of the of the field joint coating by sweep blasting far a minimum of 50mm on each side of the joint.

Application of the field joint coating Requirements

- The temperature of the joint substrate shall be at least 3°C above the dew point, and the shall be dry and free from any contamination

- Before applying the coating, the surface of the joint shall be cleaned of any residual abrasive dust or deleterious materials by a suitable method as given in the coating application and repair procedure.

- The joint shall not be exposed for a length of time which could result in oxidisation of its surface, detrimental to the quality and adhesion of the coating.

- At the time of application of the coating, the temperature of the substrate shall be within the temperature ranges specified by the manufacturer.

- The temperature of the joint shall be monitored using a suitable means in order to make sure that the application conditions are fully satisfied (steel substrate and factory applied coating).

- During bad weather (rain, wind, airborne dust etc.) cleaning and coating operations may only continue is effective protective enclosures are installed.

- Application if mainline coating is PU

- Application of the field joint coating if main line coating is PU can be achieved as follows :

- The edges of the mainline PU should be chamfered.

- The chamfered edges of the mainline coating should be sanded or grit blasted in order to achieve a surface roughness with an Rz value of 40 – 70 µm.

- The PU overlap onto the parent coating shall be minimum 50mm.

Visual inspection of the applied coating

- When inspected visually the applied coating shall be homogeneous across the entire field joint. In particular no surface defects detrimental to the quality of the coating (grit foreign particles, pitting, blisters etc.) shall be observed.

Holiday detection

- Holidays including pinholes are not acceptable. It is recommended that the electrically non conductive pipeline coating system is inspected for holidays in accordance with NACE RP 0188-99 using a high voltage pore testing device (DIN 55670). The test should be carried out on the coating after 50% of the full cure time (see product data sheet). An indication of the voltage to be used is 500 volts per 100 microns with a maximum of 7.5kV.any defect detected shall be repaired in accordance with this specification. (Holidays and areas of less than 250cm2 shall be repaired using SigmaLine 855 or Sigmaline 523 REPAIR material.

External Coating

- The external coating will consist of polyurethane SIGMA LINE 855 or Polyclad 777with a thickness of 2.0mm. (Minimum 1.5mm and average 1.85mm)

Internal coating (cement mortar lining) (when applicable)

- After welding and the necessary examinations have been carried out, the surface of the pipe to be made good shall be wire brushed; using mechanically operated tools to remove loose rust and slag from the weld

- The cement mortar mixture shall consist of cement, sand, water and if required, admixture that are well mixed and of proper consistency to obtain a dense, homogeneous coating of the required thickness that will adhere firmly to the pipe. Cement mortar shall have a maximum sand to cement ration by mass of 2,8 and a minimum sand to cement ration by mass of 1,0.

- Sand shall be river sand, natural pit sand, crusher sand or a blend of the sands provided it is clean and the grains are inert, hard, durable and uncoated. Sand grading shall show that it complies with the following grading requirements.

| Sieve Size (mm) | Percentage passing by Mass |
| --- | --- |
| 1,180 | 100 |
| 0,075 | 0 to 10 |

- The water demand for sand is defined as the quantity of water in liters to make on cubic meter of a mortar which having a sand to cement ration by mass of 1,0 has a consistency of 8,5 mm DB penetration when tested in accordance with BS 455: 1980. The water demand of the sand shall not exceed 340 l/m³.

- Cement shall be Ordinary Portland Cement or Rapid Hardening Portland Cement or a combination of these cements, which shall comply with the latest requirements of SABS 471.

Internal coating (Epoxy Lining) (when applicable)

- Abrasive Strip blast to SA 3 a strip when that includes all the unpainted section and overlaps the epoxy coated section by 50mm. This section is to have a minimum surface profile of 60 to 85 microns.

- Check surface cleanliness to SABS769 – 0.2% Dust and Debris max.

- Apply 2 to 3 coats Sigmaguard CSF or similar product that has been approved by the Engineer by brush or roller to achieve a min DFT of 400 microns.

- Wet Sponge Holiday detection 90 volts 5 megaohms 100% pinhole free Completion of epoxy linings will be executed as per the supplier’s requirements and specifications

      - Welded joints

Welding

- Jointing shall be by butt and/or fillet welding laid down in accordance with API5l and API 1104

- Welding joints shall be made in accordance with approved welding techniques and to the standard specified in TS2.6.2 and TS2.6.3. All welding shall be electric fusion welding and be acceptable to the Engineer.

- Aligning – the edges to be joined shall be aligned so that overlap in abutting edges shall not exceed 1.5mm.

- Uniformity of appearance – all welds shall be substantially uniform in appearance and shall show full fusion and penetration throughout their lengths.

- Undercut – welds shall be substantially free from undercut and, if present,

        - the depth of the undercut shall not exceed 12½ percent of the nominal wall thickness or 1mm, whichever is the lesser in depth and;

        - the aggregate length of undercut in any 1m length of welding shall not exceed 50mm.

- Weld bead tolerances – the outer weld bead shall not exceed a height of 3mm. The inner weld bead shall not project more than 1mm and all excess weld metal shall be removed to the satisfaction of the Engineer.

- In butt welds made from one side only a root groove may be present provided that it has a rounded outline and does not penetrate below the level of the adjacent surfaces on the parent plate.

- Freedom from defects – the weld, heat affected zone and surrounding parent metal shall be free from cracks, porosity cavities and trapped slag.

- Transverse tensile strength of welded joint – the welded joint shall have an ultimate tensile strength at least equal to 95% of the minimum tensile strength of the parent plate.

- Fillet welding shall comply with the following requirements and the details shown on the drawings no RA23557.

- A visual inspection shall be carried out after cleaning the slag off every fillet weld before completion of the external coatings

- Welds shall not have a concave surface. There shall be no undercutting of adjacent plate. Welds shall be free from cracks, slag intrusions and porosity.

Welding tests on butt welds only

- The Contractor shall supply on the site all equipment, materials and personnel to carry out radiographic examination of the full length of 10% of the circumferential welds made during installation of the pipeline, after 100% x-rays results have been accepted on the first 10 sequential joints. Should 100% pass rate not be achieved on these initial joints, x-rays shall continue to be taken until 10 sequential joints results are achieved.

- Cracks, lack of complete penetration, or lack of complete fusion shall be considered injurious defects. The standard for acceptance of minor imperfections such as slag inclusions or gas pockets shall be that laid down in Clauses 6.5 and 6.6 of American Petroleum Institute Standard 1104.

- Any weld rejected as a result of radiographic examination any be repaired at the option of the Contractor and such repair shall be carried out in accordance with TS2.6.4. The repaired weld shall be re-examined radiographically and re-examination shall extend for the full length of the weld in which the repair has been carried out.

Repairs

- Repairs of welded joints shall be permitted. Where repairs are required the defective weld metal shall be cut out, and the parent metal prepared by grinding and re-welded to the satisfaction of the Engineer.

- The repairs procedure and performance, and welders employed on repairs shall be qualified in accordance with Appendix B of American Petroleum Institute Standard 5L. Each repair weld shall be marked with the welder’s identifying stamp.

- On discovery of reject welds the Engineer may, at his discretion, call for additional radiographic examination at the Contractor’s cost until it is shown that the necessary standard is being maintained

      - Specials

- The steel plate and/or coil shall be free from seams, cracks, laminations and other injurious defects. The external diameter shall conform to the relevant dimensions given in the schedules and the outside diameter and circumference of specials with a diameter exceeding 400mm shall be subject to tolerances of + 300mm and ± 6mm respectively.

- Ends of specials shall be cleanly cut and be free from burrs. The ends shall not deviate more that 3mm at any point from a true plane at right angles to the axis of the pipe.

- Where pipes are to be joined by butt welding the ends shall be bevelled to an angle of 30 ± 5 degrees measured from a plane perpendicular to the axis of the pipe, and shall include a root face of 2mm ± 1mm. (Refer to Drawing No. RA23557)

- Care should be taken not to tamper with the stiffeners and compromise the pipe stability.

      - Welding

- Welding shall be in accordance with American Petroleum Institute API 1104 and API 5L. Welding Tests

- All weld tests need to be conducted in accordance to TS 2.7.3

- The Contractor shall supply all equipment and carry out radiographic examination of the full length of all welds made on specials with a diameter of 500mm and upward.

Test of specials with a diameter below 500mm.

- All piping used for the fabrication of specials shall be subject to an approved hydrostatic test to a pressure that will result in a stress of 85 per cent of the guaranteed minimum yield strength for the steel plate.

Repairs

- Repairs of welded joints shall be permitted.

Cleaning

- Each steel special shall be thoroughly cleaned and freed from all mill scale, foreign matter or rust especially along the weld and shall be approved by the Inspector immediately before coating. The exterior and interior of the special shall be cleaned by steel shot blasting and will not be accepted unless the operation provides a roughened surface equivalent to SA 2½ of Swedish Specification SIS 055900-1967.

Coatings

- After cleaning and inspection, the external surface shall be treated.

- After cleaning and inspection, the internal surface shall be treated.

      - Cleaning

- The interior of the pipes shall be swept clean at the start of each working shift and more frequently if required by the Engineer. Particular care is to be taken to prevent the tramping in of sand grains. No equipment other than pipe jacks, welding conductors, cutting torches and equipment for making good internal joints shall be taken inside the pipe without the Engineer’s permission.

- After working hours ingress to the pipeline shall be prevented by the fitting of approved end plates.

      - Charging of pipeline

- On completion of the pipeline, Rand Water will arrange to fill it with water for testing in accordance with TS2.30.

- Pipes laid under streams shall be encased in concrete. Thereafter backfilling shall be completed and the stream restored.

      - Maintenance

- The Contractor shall be responsible for all defects in the pipeline during the construction and maintenance periods and shall immediately make good any defects that arise.

      - Acceptance of pipeline

- On completion of the laying of the specific sections of the pipeline and associated structures, the Contractor shall, where necessary, supply temporary pressure testing domes, install and weld the domes on the end of the pipeline, make the necessary preparations, provide the testing equipment and carry out water tightness and structural strength tests of the pipeline system. The length of each section to be individually tested will be defined by the Engineer.

- After filling the section to be tested the section shall be allowed to stand for a minimum of 24 hours. The Contractor shall then place the pipeline under a test pressure corresponding to the relevant design head for that section of the pipeline determined by interpolation from the design elevations from the mean seal level as indicated on the general long section and on the hydraulic long section.

- Water shall be fed into the system through a calibrated meter and the pressure in the system measured by a calibrated gauge. The Contractor shall provide the necessary pumping system, connection, meter gauges and labour. Each test shall continue for at least three days. Any decrease in pressure shall be made up every hour and the quantity of makeup water measured. The pipeline will not be considered satisfactory until the average leakage is less than 0.01 litres/mm diameter/kilometre/24 hours/30m head.

- Any visible leak in the pipeline shall be made good by the Contractor. If any valve leaks it will be made tight by the supplier of the valve.

- If the average leakage per 24 hours from each individually tested section of the pipeline is greater than that specified, the Contractor shall take immediate steps to reduce the leakage and shall at his own expense do any excavating necessary to locate the repair leaks or other defects which may develop under test, including removal of backfill already placed, shall make all repairs necessary to secure the necessary water tightness, shall replace such excavated materials, after which the test shall be repeated until the pipe under test is found satisfactory.

# General Mechanical

      - Scope

The Rand Water Bronberg, Brakfontein, Klipfontein and Hartebeesthoek Reservoirs Hydropower schedule sets out the design, manufacture, supply, and installation requirements for general mechanical infrastructure including but not limited to:

- General mechanical works

- Pumps

- Cranes (lifting equipment)

- Valves

      - Design criteria

        - General

The operational life cycles of mechanical equipment and subsystem such as pumps, cranes and valves shall be designed to have a minimum design life cycle of 30 years.

A high quality standard for mechanical works is demanded and reliability, long life, trouble free operation, efficiency, ease of maintenance and operation, and neatness are essential. All manufacturers / suppliers must have good experience in the water and water treatment industry in Southern Africa and have locally based after sales and repair / service facilities as follows:

- shall have furnished equipment of the type and size specified in similar applications that has been in successful operation in Southern Africa for not less than the past 10 years, including at least 5 years of similar applications on International Projects.

- shall have had maintenance and repair facilities established and in operation in Southern Africa for a period of not less than five years at the time bids are received. Such facilities shall be fully equipped and staffed with qualified personnel for making repairs to equipment provided under the Contract. The facilities shall carry a full line of normal maintenance spare parts

- The specialist undertaking Mechanical design and execution of the work shall be a professionally registered person with ECSA or similar bodies.  The individual shall be in good standing, has a minimum of ten (10) years in designing and constructing similar systems and has a good track record. The Curriculum Vitae (CV) of the professional engineer doing the designs, or certifying the designs and or doing the execution work must be supplied.

All plant and equipment shall be of robust construction and the design shall, as applicable, be based on:

- the full range of duties which can be reasonably anticipated;

- the power and torque transmitted by the driver system under full load and stalled conditions;

- the maximum pressure or vacuum which can be produced by pumps, blowers and compressors under all conditions including blocked or closed inlet and outlet circuits;

- conservative service and safety factors based on approved standards or laid down in the printed specifications of reputable and approved manufacturers;

- twenty-four hours per day operation;

- a minimum bearing life of 100 000 hours before repair or major part replacement;

- prevention of serious damage from normal operational problems such as blockages, blinding, jamming, seizure, malfunction and, as far as is practical, mal-operation; if these occurrences cannot be avoided by good design

- the provision of pressure gauges on suction and delivery pipes of pumps, blowers and compressors.

- the minimum requirements of listed manufacturers

Machines with non-overloading characteristics shall be selected wherever possible; e.g.: motors shall be sized so that they cannot be overloaded by the driven machine.

Variable Speed Drives of any type shall not be used on equipment having motors greater than 5kW.

        - Safety

Safety shall be an all-important and overriding consideration and proper attention shall be paid to this aspect at the design stage. Equipment which is potentially dangerous shall be designed in accordance with a relevant South African or international Standard.

The following must be noted:

- Hazards must be avoided or guarded. Nip points shall be guarded; sharp corners shall be rounded off; operating handles, supports and protrusions shall be kept clear of access ways; and so forth.

- The Contractor's Drawings and specifications shall clearly specify the structural requirements of the Works and the Contractor shall be responsible for covering all unsafe gaps and openings left in structures after installation.

- Moving parts shall be properly guarded to the satisfaction of the Engineer.

- An emergency stop button shall be installed in a convenient position next to each machine. The installation shall be designed to provide immediate access without the danger of accidental operation. In addition, trip wires which will stop the driving motor when pulled shall be provided along the accessible side/s of moving conveyor belts, chains and the like irrespective of operating speed and irrespective of guards provided.

- Where, in the opinion of the Engineer, an installation is not safe, the Contractor shall remedy such defect at his own cost to the satisfaction of the Engineer.

Where damage can occur from normal operational or other foreseeable problems, plant, equipment and systems must be designed to be fail safe; i.e. must have built-in redundant elements, or be fail-to-safe; i.e. must return to a safe condition where no further damage can be done in the event of a failure, malfunction, mal-operation, overload and, as far as practical, misuse. All reasonable and economically justifiable protections to prevent or limit damage to plant and equipment, particularly in high risk situations, must be incorporated.

Protections shall:

- be directed at the source of the problem, limit forces to safe levels and act quickly enough to prevent damage (electrical thermal type overloads are inadequate);

- stop or prevent from starting all equipment at risk;

- activate an alarm with a labelled indicator on the control panel whenever a protection operates;

- not permit unauthorised tampering;

- operate reliably after long inactive periods exposed to corrosive and dirty conditions.

        - Moving parts

The following general requirements apply not only to machines but to all equipment with moving parts such as headstocks, extension spindles, swivelling davits, heavy duty hinges, pivots and the like:

All rotating or swivelling shafts, pins and the like, shall be adequately supported, guided and restrained by lubricated or self-lubricating bearings, collars and/or bushes.

Swivelling joints on linkages and the like shall be of the "universal" or fork and rod type with bearings or bushes fitted to the eyes or forks.

On abrasive applications abrasion resistant materials and slow speed operation shall be utilised.

Susceptibility to fatigue failure shall be minimised by proper design and manufacturing procedures. In particular, changes in section shall be radiused and care must be taken to avoid the use of welded components in areas of fluctuating stress.

The locking of nuts and pins in position shall be done to the approval of the Engineer. Wearing parts shall be designed for interchangeability and ease of removal and replacement.

        - Arrangement and mounting

The arrangement and general design shall take the following requirements into consideration:

- Lifting eyes, lugs, hooks, etc., shall be provided on heavy or large items to facilitate handling.

- Castings or fabrications shall have machined pads for seating and be mounted on either soleplates or baseplates as appropriate.

- Where accurate alignment is required, positioning pins and/or jacking screws shall be provided.

- The needs of operation and maintenance including neatness, access, working space, safety, cleaning, adjustment, handling, assembly, alignment, disassembly, removal, etc.

- With plant and equipment to be mounted on or against concrete or brick structures, provision shall be made for adjustment in the mechanical design. Any special accuracy requirements must be specified on the Contractor's Drawings.

        - Installation

The Works shall comply with the following:

- When erected and installed, the plant and equipment shall be of neat and workmanlike appearance, solidly and evenly supported, true to line, level, plumb and in proper working order.

- The Contractor shall provide all foundation bolts, supports, hangers, brackets, etc. required for the support and fixing of his equipment.

- The Contractor is responsible for all grouting of puddle pipes which pass through liquid retaining walls or slabs.

- The use of more than three shims in the alignment of equipment will not be permitted. Machined spacers shall be prepared where necessary. Shims and spacers shall be of a corrosion resistant material such as stainless steel.

- Corrosion protection requirements shall be carefully attended to.

- Fastener threads must be coated with a nickel-based, anti-seize compound before assembly.

- Crevices which are formed between two surfaces shall be filled, prior to final fastening, with a suitable formable packing, Denso tape or equivalent. This applies particularly to stainless steel.

- Shafts for drives, such as motors, with an output above 150 kW shall be aligned to the driven shaft as follows:

- Final alignment shall be done after installation and before commissioning, shall be checked in the presence of the Engineer and shall be to his approval. Alignment shall be sufficiently accurate to ensure that no initial pre-load is placed on the shaft coupling.

- Each motor shall be aligned to its pump using laser aligning equipment.

- The use of pourable epoxy resin chocks shall be acceptable. If pourable chocks are used, the baseplate feet do not have to be machined but each machine foot shall be provided with a screw for vertical alignment. The chock thickness shall not be less than 20 mm.

- A Viking Johnson Flange Adaptor is to accompany all pipe manifolds for the removal of equipment for maintenance.

- All valves are to be suitable installed to allow easy removal for maintenance. Where applicable a Viking Johnson Flange Adaptor is to be used.

- Machines with vibrating components are to be coupled to their respective pipe manifolds with an approved flexible coupling.

- The lowest points on pipe lines are to have a drain.

- The highest point on all pipe lines is to have an air release valve to be vented to the atmosphere.

- Pressure gauges are to be supplied on suction and delivery pipe work for pumps and compressors.

        - Materials

All materials used in the manufacture and construction of plant and equipment shall be new, unused and shall be the best of their respective kinds. The Contractor shall ensure that the materials are selected in accordance with the best engineering practice to suit the working conditions and the extremely corrosive environment.

Particular attention shall be paid to cleanliness, soundness and neat fettling and dressing of castings. Surfaces shall be smooth and irregularities caused by mould wash-aways, and the presence of porosity and sand and slag inclusions will not be tolerated. Areas under bolt heads, nuts and washers, shall be machined or spot faced to ensure a flat and smooth pressure bearing area, and sufficient space shall be provided for the use of ring or socket spanners.

All pressure retaining castings shall be hydrostatically tested to not less than 1,5 times the maximum working pressure after machining and shall be pressure tight.

No repairs shall be undertaken to castings without the written permission of the Engineer and welding will not be permitted on cast iron castings.

Castings shall be heat treated to provide optimum corrosion resistance and toughness combined with reasonable machinability. In particular stainless steel castings shall be heat treated so as to ensure that all carbides are in solution, to ensure optimum grain size, and to provide maximum corrosion resistance.

The Contractor shall provide a test certificate for each casting or batch of castings giving details of the material analysis, the heat treatment and any mechanical tests carried out.

        - Welding

Standards complying with good modern practice, and acceptable to the Engineer, shall be adopted. All welding shall be continuous on all sides of any joint unless otherwise approved in writing by the Engineer. No crevices will be permitted and where stitch welding has been approved by the Engineer, the crevices so left shall be sealed with an approved filling compound after priming but before further painting.

Welding shall be free of blowholes and all welding flux shall be removed. All weld spatter and other sharp imperfections shall be removed prior to abrasive blasting. Prior to painting, weld beads with a surface irregularity exceeding 3 mm or with sharp crests having a radius less than 2 mm shall be ground. Weld grinding must not be performed on 304L or 316L stainless steel, however, unless unavoidable. Site welding shall be kept to a minimum and shall only be undertaken with the approval of the Engineer.

All possible steps shall be taken to ensure maximum corrosion resistance and strength of the welds and welded material. Special care shall be taken to avoid prolonged heating. Welds shall be passivated. Discolouration and steel contamination must be removed by pickling or electro-cleaning as approved by the Engineer but should rather be avoided by taking the appropriate measures.

Welding of pipelines and related facilities shall meet the requirements of the American Petroleum Institute 1104 (API Standard 1104), (Pipelaying) and American Petroleum Institute 5L (API 5L Standard) (Manufacturing), the American Society of Mechanical Engineers (ASME B31) or the British Standards (BS 4515).

All certified welders and certified welding inspectors must be in possession of a current and relevant internationally recognized welder or welding inspector certificate as issued by the American Welding Society (AWS) or the Southern African Institute of Welding (SAIW).

All certified welders and certified welding inspectors must be in possession of a current and relevant internationally recognized welder or welding inspector certificate as issued by the American Welding Society (AWS) or the Southern African Institute of Welding (SAIW).

        - Lubrication

Equipment shall be adequately lubricated by systems that require attention no more frequently than monthly during continuous operation. Lubrication systems shall not require attention during start-up or shutdown and shall not waste lubricants. Lubricants of the type recommended by the equipment manufacturer shall be provided in sufficient quantity to fill all lubricant reservoirs and to replace all consumption during testing, start- up, and operation prior to acceptance of equipment and one year of operation after Final Acceptance. The use of synthetic lubricants will not be acceptable.

Lubrication facilities shall be convenient and accessible. Lubrication of equipment shall not require removal of the equipment from its installed position or any dismantling of subassemblies. Oil drains and fill openings shall be at least 300 mm above working area and shall be easily accessible from the normal operating area or platform. Drains shall be extended from the equipment served where necessary to prevent leakage or spillage during oil changes, and shall allow for convenient collection of waste oil in containers from the normal operating area or platform without removing the unit from its normal installed position.

Lubrication fittings for underwater bearings shall be routed above the surface of the water with at least 8 mm diameter 316 L stainless steel tubing and mounted on the edge of the structure above. Fittings shall be compression type. Lubrication fittings shall be mounted together wherever possible using factory-mounted multiple fitting assemblies.

Grease lubrication is preferred and all greasing points must be easily accessible. Equipment with multiple greasing points shall be provided with grease lines which are piped, separately, to a single easily accessible position. In cases in which motorised lubrication is provided to more than one destination, a distributor shall be provided. The distributor shall be a positive displacement device which ensures equal, successive lubrication to all destinations. Pipework for grease distribution shall be of stainless steel or non-ferrous metal.

In the case of oil lubrication level indicators shall be fitted for visual checking. Drain cocks, including 316 SS fittings where necessary to permit convenient draining, and plugged at the end, shall be provided for oil reservoirs exceeding 1,5 litre capacity. Drains shall be from the lowest point and siphon type drains are unacceptable. Lubrication systems shall be designed to exclude dirt and moisture. Air vents on the oil reservoir shall contain an air filter.

        - Fasteners

Bolts and nuts shall be hexagon head type complying with SANS 1700 with threads of the coarse pitch series.	Allen head screws of any type shall not be used. All fasteners M12 and smaller shall be manufactured of grade 316 stainless steel. All fasteners in corrosive areas shall be manufactured of 316 SS. Corrosive areas shall be taken to include any moist or wet area such as in and above settling tanks, in or in the vicinity of open channels, where a continuous spray can be expected and all internal and external areas in the vicinity of the inlet works of a wastewater treatment works. All fasteners embedded in brick, concrete or soil shall also be of 316 SS. Fasteners larger than M12 which are in non-corrosive areas shall, except when specified otherwise, be hot-dip galvanized. Where high tensile bolts are required by the design, they shall be hot-dip galvanized and painted. The bolt holes and crevices shall be filled and sealed prior to painting. Fastener material shall always be of equal or better corrosion resistance than the items being fastened, e.g. 316 stainless steel bolts must be used to fasten together 316 stainless steel fabrications or flanges. Washers of similar material to the bolts shall be provided under each nut and setscrew head. Multiple washers or shims shall not be used. Spring washers or other approved locking arrangement shall be used on all fasteners subject to vibration. Before assembly, threads shall be treated with a nickel based, anti-seize/corrosion protection compound. The thread shall be treated in the area under the final position of the nut. Compound on the exposed thread shall be cleaned off after installation. If it is found during inspection that compound has not been applied, the Contractor shall disassemble all fasteners and comply with this requirement.

Bolt threads shall project between 1 and 6 mm from the head of the nuts when fixed. Longer projections will only be allowed if the Contractor can show that bolts of a more suitable length are not manufactured. After installation the exposed surfaces of bolts not made of 316 stainless steel shall be coated as for the items being fastened.

All anchor fasteners shall be of grade 316 stainless steel. Anchor fasteners for water retaining structures and for brickwork shall be of the chemical anchor fastening type. Anchor fasteners for other applications may be of the expanding type or chemical anchor type.

Grade 316 stainless steel stud bolts shall be supplied and grouted into pockets in the concrete structure. A suitable epoxy anchor grout for use in submerged conditions is to be used and pre-approved by the engineer.

Where machinery is anchored by studs or bolts which extend through the supporting structure and is therefore fastened down with the use of nuts from both sides, these, together with associated washers and brackets, shall also be of grade 316 stainless steel. All threads shall be coated with an approved nickel-based, anti-seize/corrosion protection compound before assembly.

Both direct-coupled and belt-driven machines shall be mounted with their drivers on common cast iron or fabricated steel baseplates of rigid construction. Steel baseplates shall be hot-dip galvanized. The baseplate shall incorporate machined mounting pads at the support and fixing positions of each item of plant and equipment to be mounted on the baseplate. On fabricated baseplates this machining shall be done after fabrication, stress relieving (if applicable) and hot-dip galvanizing are complete. The thickness of the solid pads shall be not less than 1,25 times the diameter of the holding down bolts. The pads shall not be provided with threaded holes for machine screws but shall be drilled for inserting through-bolts and adequate provision shall made for reaching the nut with a suitable spanner. In the period between machining and installation of the equipment, the machined surface shall be protected against corrosion by a removable coating. After installation, a non-hardening compound shall be applied to exposed machined surfaces and to the crevice formed at the foot of the equipment.

Anchor fasteners shall be of grade 316 stainless steel with threads coated with a nickel-based, anti-seize compound before assembly. Preliminary alignment shall be done at the factory to ensure that the baseplate has been correctly manufactured, but final alignment shall always be done on site after installation and grouting has been completed. Alignment shall be accurate and a final alignment check must be carried out prior to start up. Not more than three shims may be used at any point and these must be made of a corrosion resistant material. At least two diagonally opposed jacking screws shall be provided for belt tensioning in the case of belt-driven units. Direct-coupled motors below 5 kW shall be provided with jacking screws for horizontal and vertical alignment. Jacking screws shall be of grade 316 stainless steel. Baseplates shall be so designed and grouted as to eliminate collection points for water or dirt. All baseplates on concrete plinths shall be fully grouted in. Grouting holes must be provided on baseplates having a continuous top plate. Tapped holes and fixing setscrew protrusions shall be suitably protected. The material used for grouting shall be a non-shrink, cementitious grout.

In applications where baseplates are not practical, machined soleplates, suitably fixed and grouted to the concrete plinths, shall be provided. No machine may be mounted directly onto a concrete base without the use of either a baseplate or soleplate.

In applications where baseplates are not practical, machined soleplates, suitably fixed and grouted to the concrete plinths, shall be provided. No machine may be mounted directly onto a concrete base without the use of either a baseplate or soleplate.

        - Guards

Guards shall comply in all respects with the Occupational Health and Safety Regulations and the following points shall also be noted:

Guards are required to cover all moving or revolving components of machinery. Guards which do not adequately cover moving protrusions such as keys, lock-nuts, lockwashers, setscrews, etc., or irregularities such as keyways, will under no circumstances be accepted.

Guards shall be neatly and rigidly constructed and fixed and shall not vibrate or cause noise during operation.

Where expanded metal or similar mesh is used, the mesh opening shall not permit a circular object 10 mm or larger to penetrate.

Mesh shall not be used for chain guards but on belt drives the side of the guard most conveniently sited for inspection shall be constructed of expanded metal or similar. Mesh should similarly be used in other situations where inspection or ventilation is required.

Guards shall completely enclose drives and shall entirely prevent a person from touching any moving protrusion.

Allowance must be made for adjustment on belt guards or where adjustment will be required. It shall be possible to remove the guard easily for maintenance purposes.

Guards shall preferably be fabricated of 316 stainless steel (uncoated) but may also be hot-dip galvanized, zinc-sprayed or aluminium-sprayed carbon steel, coated to specification in all these cases. Fasteners shall be M10 or larger and shall be of 316 stainless steel.

        - Bearings

Bearing systems shall be designed to provide safe shut down without damage under normal stoppages as well as electrical supply failure. To assure satisfactory bearing application, fitting practice, mounting, lubrication, sealing, static rating, housing strength, and lubrication shall be considered in bearing selection.

Re-lubricatable type bearings shall be equipped with an hydraulic grease fitting in an accessible location and shall have sufficient grease capacity in the bearing chamber. Lubricated-for-life bearings shall be factory- lubricated with the manufacturer's recommended grease to insure maximum bearing life and best performance.

Anti-friction type bearings shall have a minimum L-10 life expectancy of 5 years or 20,000 hours, whichever occurs first, or per the equipment specifications where more stringent. Where so indicated, bearings shall have a minimum rated L-10 life expectancy corresponding to the type of service, as follows:

Bearing life expectancy

| Type of Service | Design Life (years) | L-10 Design Life (hours) |
| --- | --- | --- |
|  | (Whichever comes first) |  |
| 8-hour shift | 10 | 20,000 |
| 16-hour shift | 10 | 40,000 |
| Continuous | 10 | 100,000 |

Bearing housings shall be of cast iron or steel and bearing mounting arrangement shall be as indicated or as recommended in the published standards of the manufacturer. Split-type housings may be used to facilitate installation, inspection, and disassembly.

Sleeve-type bearings shall have a cast iron or ductile iron housing and Babbitt or bronze liner. Bearing housing shall be bolted and doweled to the lower casing half. These housings shall be provided with cast iron caps bolted in place and the bearing end caps shall be bored to receive the bearing shells. Sleeve bearings shall be designed on the basis of the maximum allowable load permitted by the bearing manufacturer. If the sleeve bearing is connected to an equipment shaft with a coupling, the coupling transmitted thrust will be assumed to be the maximum motor or equipment thrust. Lubricant, lubrication system, and cooling system shall be as recommended by the bearing manufacturer.

Thrust bearings shall be designed and manufactured to maintain the shaft in the fixed axial position without undue heating or the necessity of adjustment or attention. Bearings shall be oil lubricated to suit the manufacturer's standard method of lubrication for the specific bearing. If bearing cooling is required, manufacturer shall provide necessary piping, filters, and valves.

        - Couplings

Mechanical couplings shall be provided, unless otherwise called for, between all drivers and the equipment for equipment rated at above 5 kW. Flexible couplings shall be provided between the driver and the driven equipment to accommodate slight angular misalignment, parallel misalignment, end float, and to cushion shock loads. Each coupling size shall be determined based on the rated horsepower of the motor, speed of the shaft, and the load classification service factor. The Contractor shall have the equipment manufacturer select or recommend the size and type of coupling required to suit each specific application. Where differential settlement between the driver and the driven equipment may occur, 2 sets of universal type couplings shall be provided.

Taper-Lock or equal bushings may be used to provide for easy installation and removal of shafts of various diameters.

        - Shafting

Shafting shall be continuous between bearings and shall be sized to transmit the power required. Keyways shall be accurately cut in line. Shafting shall not be turned down at the ends to accommodate bearings or sprockets whose bore is less than the diameter of the shaft. Shafts shall rotate in the end bearings and shall be turned and polished, straight and true.

All shafts shall be designed to carry the steady state and transient loads suitable for unlimited number of load applications. Where shafts are subjected to fatigue stresses, such as frequent start and stop cycles, the mean stress shall be determined by using the modified Goodman Diagram. The maximum torsional stress shall not exceed the endurance limit of the shaft after application of the factor of safety of 2 in the endurance limit and the stress concentration factor of the fillets in the shaft and keyway. Stress concentration factor shall be in accordance with ASME Standard B17.1 - Keys and Keyseats.

In every case where a drive motor is connected to a driven piece of equipment by a flexible coupling, the coupling halves shall be disconnected and the alignment between the motor and the equipment checked and corrected after the complete unit has been levelled on its foundation and again after grout has set and foundation bolts have been tightened.

In general, checking and correcting the alignment shall follow the procedures set up in the Standards of the Hydraulic Institute, Instructions for Installation, Operation, and Maintenance of Centrifugal Pumps. Shafting materials shall be appropriate for the type of service and torque transmitted. Environmental elements such as corrosive gases, moisture, and fluids shall be taken into consideration.

        - Nameplates

A stainless steel name plate is to be provided on all mechanical equipment with at least the following information:

- Manufacturer’s name

- Supplier’s name

- Equipment’s serial number

- Size and type of equipment

- Equipment duty

- Rated motor

- Speed

        - Centrifugal pumps

All centrifugal pump sets (including end suction, horizontal split casing, multi-stage, submersible, self-priming and vertical axial flow turbine pumps) shall be designed and supplied in accordance with ISO 9908 – Technical specification for centrifugal pumps - Class III.

The manufacturer/supplier shall review the rated (guarantee) duties and offer his best technical and financial solution at the highest operational efficiency based on the type, size and arrangement of pumpsets suited to the application.

The pump selected shall be sized such that the rated (guarantee) duty is positioned as close as possible to the Best Efficiency Point (BEP) of the pumps hydraulic and shall be capable of at least 125% of the rated duty flow. The rated (guarantee) duty flow must be pitched within no less than 80% and no greater that 110

% of the BEP flow. The pumps are to be selected so as to have stable, non-overloading characteristic curves.

Pump characteristic curves shall show head, efficiency, power demand and NPSH required, plotted against discharge flow rate in metric units at the rated impeller diameter and speed required to satisfy the rated (guarantee) duty.

Required pump characteristics

| Measurement | Preferred Unit | Symbol |
| --- | --- | --- |
| Total Dynamic Head (TDH) | meters | (m) |
| Discharge flow | litres per second | (l/s) |
| Efficiency | percent | (%) |
| Power absorbed | kilowatt | (kW) |
| NPSHr | meters | (m) |
| Impeller diameter | millimetres | (mm) |
| Speed | revolutions per minute | (rpm) |

The performance curves shall indicate pump performance characteristics at maximum, minimum and rated impeller diameters.

Where two or more pumps are required to operate in parallel, care shall be taken to ensure that one pump can operate in isolation on the system without risk of damage to the pump itself or system within which it operates. This operating point shall be referred to as the “runout duty point”. Details of the hydraulic performances expected under these conditions shall be verified by superimposing the rated characteristics curve of the pumps offered onto the system curve (where) provided. This graphical data as well the runout hydraulic conditions shall be submitted with the tender.

The Net Positive Suction Head Required (NPSHR) shall be based on coldwater as specified in ISO 2548 and ISO 3555. The Net Positive Suction Head Available (NPSHA) must exceed NPSHR by a margin of at least 30% or 0,5 m, whichever is the greatest, at the rated (guarantee) point specified. The basis for use in performance curves is that NPSH corresponding to a drop of 3% of the total head of the first stage of the pump (NPSH3). Where a pump may be subjected to operating under a runout duty point condition, the NPSHA must exceed NPSHR by a margin of at least 15% under this scenario.

Although all pumps shall be installed within an enclosed installation they must be designed and supplied such that they are able to operate under normal Southern African outdoor environmental conditions. The manufacturer/supplier shall ensure that the combination of materials proposed for the construction of pumpsets shall not be subject to undue wear, abrasion, corrosion (galvanic etc.), stress, strain or otherwise, as brought about by this medium. The materials of construction proposed shall be clearly indicated in the Technical Bid. Any specialised coatings or other means determined to be necessary or recommended to prolong the service life of the pumpsets, must be clearly indicated.

As a minimum, the materials of combination shall consist of:

- S.G. iron casings, end covers, and bearing bracket.

- S.G iron, zinc free bronze or stainless steel impellers.

- High tensile steel shafts.

- Non metallic shaft flinger.

Rotating elements shall be statically and dynamically balanced according to ISO 1940-1:2003 to a balance quality grade of G2.5. Balancing certificates shall be submitted where specified, in an approved format.

The rated impeller diameter shall not exceed 95% of full diameter. Similarly the rated impeller diameter shall not be less than 105% of the minimum diameter.

Supplier/Manufacturer shall specify and offer the recommended shaft mechanical seal.

Baseplates are to be rigidly designed such that the combined unit (uncoupled pump, motor and baseplate) may be transported as a single item without any excess deflections or strains applied to any of these items. Suitable lifting lugs shall be provided on the baseplate design for transportation and lifting purposes. Lifting of the combined unit must not be carried out by slinging from the pump or motor. Baseplates shall be supplied complete with holding-down bolts and sufficient steel packers to allow shimming for alignment and grouting. All shims are to be neatly cut so as not to protrude beyond the baseplate or motor‘s base/feet. Jacking bolts shall be included in the baseplate design to aid in the alignment of rotating equipment.

The maximum working pressure that the pumpsets will be subjected to, will be under closed valve conditions. All pumpset flanges shall as a minimum be pressure rated and drilled in accordance with SANS 1123 Table 1600/3. Should the casing design pressure exceed this pressure rating then the flange drilling requirements shall be upgraded accordingly. All pumpsets shall be safeguarded from excessive surge pressure by suitable surge protection equipment.

The prime mover for all pumpsets shall be an electrical induction motor driven via a suitably rated flexible coupling. The operating speed of all pumps should preferably be less that 1 500 rpm but must not exceed 3 000 rpm. The prime movers power output rating shall equal or exceed at least the following margins according to the pump's absorbed power demand at the rated (guarantee) point.

Power output rating requirements

| Margin | Description | Value |
| --- | --- | --- |
| 50% | For pumps requiring up to | 2 kW |
| 40% | For pumps requiring from | 2 to 5 kW |
| 30% | For pumps requiring from | 5 to 10 kW |
| 20% | For pumps requiring from | 10 to 30 kW |
| 15% | For pumps requiring from | 30 to 100 kW |
| 10% | For pumps requiring | Over 100 kW |

Where a unit may be subjected to operating at a runout duty point condition, the power output rating of the prime mover shall be at least 5% greater than the power absorbed by the pump at this point. Contractors must ensure that their selection of motors is correctly sized to handle the start up torques brought about by the abovementioned start up procedures.

A hydrostatic test shall be performed for pressure-containing parts of a pump at a test pressure of at least 1,5 times the basic design pressure. This pressure shall be maintained for a period of at least 10 minutes.

The Client or his representative shall be entitled to witness the pressure tests and at least two (2) weeks’ notice shall be provided before such testing takes place. A test certificate shall be issued after the successful completion of such tests, in an approved format.

Pumps greater than 100 kW in size shall furthermore be subject to a hydraulic performance and NPSH test in accordance with ISO 9906, Class I or II, at an approved test facility. The Purchaser or his representative shall reserve the right to witness all tests (as required and indicated on the data sheets provided with this tender) and shall be granted full and complete access to all test data taken during the course of the test. They shall furthermore, be provided with copies of all test sheets, calibration certificates etc. upon completion of the tests. At least two (2) weeks’ notice shall be provided before such tests are undertaken.

Where pumps are supplied as complete pumpsets, these shall preferably be tested as such and shall be complete with own job motors. In addition to the test point required to establish the guaranteed performance, a sufficient number of test points shall be measured so as to establish the shape of the full performance curve as presented in the Tender. During the execution of the performance test, the mechanical operation of the pump shall be monitored with particular reference to abnormal temperature, noise, vibration and leaks. Failure to achieve the rated (guarantee) point may render the equipment liable for rejection. Should this occur the manufacturer/supplier shall then be responsible to rectify the equipment to achieve such guarantees at own expense.

Pumps greater than 185 kW shall have bearing vibration monitoring as stipulated in ISO 2372:1974. An alarm is to be sounded if the vibration reaches the upper limit requirements.

Other standard specifications applicable to centrifugal pumpsets shall be:

| Specification Number | Specification Title |
| --- | --- |
| ISO 9905:1994 | Technical specifications for centrifugal pumps – Class I |
| ISO 5199:2002 | Technical specifications for centrifugal pumps – Class II |
| ISO 9908:1993 | Technical specifications for centrifugal pumps – Class III |
| ISO 76:1987 | Rolling bearings – Static load ratings |
| ISO 281:1990 | Rolling bearings – Dynamic load ratings and rating life |
| ISO 2372:1974 | Mechanical vibration of machines with operating speeds from 10 to 200 rev/s – Basis for specifying evaluation standards |
| ISO 3069:1974 | End suction centrifugal pumps – Dimensions of cavities for mechanical seals and for soft packing |
| SANS 1123:2000 | Pipe Flanges |
| ISO 7005-1:1992 | Metallic flanges – Part 1: Steel flanges |
| ISO 7005-2:1988 | Metallic flanges – Part 2: Cast Iron |
| ISO 7005-3:1988 | Metallic flanges – Part 1: Copper alloy and composite flanges |
| ISO 1940-1:2003 | Mechanical vibration - Balance quality requirements for rotors in a constant (rigid) state - Part 1: Specification and verification of balance tolerances |
| ISO 9906 | Rotordynamic pumps – Hydraulic performance acceptance tests – Grades 1 and 2 *(ISO 9906 replaces ISO 3555 and ISO 2548) |
| ISO 3555:1977 | Centrifugal, mixed flow and axial flow pumps – Code for acceptance tests – Class B |
| ISO 2548:1973 | Centrifugal, mixed flow and axial flow pumps – Code for acceptance tests – Class C |

        - Positive displacement pumps

Positive displacement pumps refer to progressing cavity pumps and diaphragm pumps. Construction materials shall be selected according to the medium to be transferred and the pump size shall be conservatively selected to ensure a very low rotational speed (preferably not exceeding 300 rpm). All universals, pins, bushes and so forth operating in the pumped liquid shall be properly lubricated and must be fully sealed.

Each pump shall be direct coupled to a motor/gearbox unit to suit the range of pump duties. The complete drive unit shall have an ingress protection rating of IP 55 or higher. The pump and drive unit shall be mounted on a common fabricated steel baseplate complete with all necessary guards.

All components shall be conservatively selected to suit the specified type of duty with continuous 24 hour per day operation. The continuously rated output of the motor shall exceed the power required at maximum duty and at the worst operating condition by not less than 30 %. The gear unit shall be selected using a service factor of not less than 2, based on the installed motor power.

Chemical dosing pumps in variable speed applications shall have their drive motors controlled by electronic variable frequency converters which are suitably rated for the torque required by the application. The converter shall be housed in a cubicle in the electrical control panel which is normally in a separate room. The motor shall be inverter duty and VFC shall be of suitable design and shall be adequately sized to provide the high torque requirements of the pumps under all operating conditions,

When pumping sludge, it is possible for the pumps to block or seize or have abnormally high starting torque requirements, particularly when operating on a duty/standby rotation basis. The complete installation shall be designed to cope with such operating conditions without damage to equipment.

The drive unit shall be rated to withstand such shock overloads at any torque produced by the motor between full speed and shock stall without any damage. If any part of the unit could be damaged under such conditions, suitable safeguards shall be incorporated. Thermal overloads on the motor shall not be regarded as adequate in such a case.

If an overload safeguard system is necessary to protect against overload damage, the system used shall disconnect the load immediately an overload occurs, switch off the unit, activate an alarm indication on the control system and initiate the shutdown of other equipment if this is necessary. A sealed, adjustable and re- settable torque limiting coupling, between the pump and drive unit would be acceptable. The coupling must be set for the maximum torque which the drive unit can safely handle.

A 50 mm NB (Nominal Bore) connection shall be provided downstream of a check valve on the delivery line of all pumps. A 50 mm NB flushing line from the domestic water supply, or the service effluent water system (if applicable), shall be connected to this. On each branch a solenoid valve, isolating valve, by-pass with isolating valve and check valve shall be fitted. This system shall automatically flush the pump before each start up and shut down. Manual flushing shall also be possible using the by-pass.

Where a system such as that described above is not possible on, for example, a direct feed hopper system, then an alternative flushing system such as a hopper flushing system shall be devised.

Pressure switches shall be mounted on the inlet and the outlet connections of all pumps to protect the pumps against closed or blocked lines by interrupting the supply to the motor.

These switches shall be protected by a diaphragm type, liquid filled chemical seal. The portion of the seal in contact with the process liquid shall be suitably corrosion resistant and, when solids are handled, shall have a large threaded socket connection not smaller than 1" BSP.

The switch and its seal shall be mounted on the top leg of a cross with two plugged connections. The cross shall be mounted on the side of the pipe and the bottom and second side connection of the cross shall be plugged, but arranged so that effective cleaning or flushing of connections can be done. An isolating valve shall be provided to permit isolation of the cross from the pipe.

The layout of progressing cavity type screw pumps shall be such that the glands are under the lowest of suction or discharge pressure.

        - Valves

Valves shall be designed and constructed to ensure reliable operation after long periods of non-operation.

All valves shall be double-flanged and their method of actuation shall be designed to provide operation under the full pressure rating of the valve. The handwheel, lever, etc. on valves, valve actuators and valve gearboxes shall be clockwise closing unless otherwise specified.

For detailed specification on valves refer to Specification number RW/0310/AS0460

All valves interfacing with Rand Water main pipelines shall be designed to have metal-to-metal seats and shall be electrically operated.

        - Corrosion protection

The cleaning and corrosion protection of valves must be carried out at the factory prior to despatch to the Site. Non-ferrous metal or stainless steel surfaces must not be painted. The protection to be applied must comply with one internal and one external system from the following alternatives:

System 1 (Epoxy resin paint) - All cast iron surfaces of every valve, other than RSV's, must be prepared for painting to a thoroughly clean condition free of all grease and deleterious matter. Ferrous surfaces must be prepared in accordance with ISO 8501 to a Sa 3 finish. Surfaces must then be coated with a non-toxic epoxy resin paint to give a total minimum dry film thickness of 250 mm to be pinhole free over the entire painted surface.

System 2 (Epoxy powder coating) - Electrostatically applied epoxy powder coating (ESPC), of the fully disassembled valves shall be carried out in accordance with SANS 1217 as may be modified by this specification. All RSV's are to be treated with this system.

All surfaces of the fully disassembled valve shall be blast cleaned to Sa 3 of ISO 8501-1 and having an angular profile of 40 µm to 60 µm.

The coating medium shall be an exterior grade, tinted, non-toxic and non-tainting, suitable for use with potable water and applied strictly in accordance with the manufacturer's instructions in a single application to a minimum film thickness of 300 µm. The coated surface shall be subjected to a standard MEK 50 double rub test. Particular attention shall be given to the thickness and integrity of the coating in the areas where the gate of the RSV is to operate. Low voltage, wet sponge EID detection of pinholes is to be conducted on all surfaces of the valve. A visual inspection, to be carried out by an experienced observer, shall reveal the finished coating to be smooth and glossy, free from excessive runs, sags, "orange peel" finish, occlusions and other visible defects. The coating shall be subjected to a "hot water soak" adhesive test at the inspector's discretion, and no more than 15 mm disbondment from the point of the "V" (cut at a 30 degree angle) shall be permitted after immersing in water at 78°C for 48 hours, and testing adhesion after cooling to 25°C. Repairs shall be carried out using an approved repair system.

System 3 (external only) - Apply multi coats of an approved epoxy coal tar paint to give a minimum total dry film thickness of 240 µm. The paint shall be applied in accordance with the paint supplier's recommendation.

System 4 (external only) - Apply one coat of zinc chromate primer followed by one coat of undercoat tinted where necessary, and a final coat of best quality gloss enamel. The total dry film thickness of the system must be not less than 200 µm.

After erection on site all valves must be cleaned and the paintwork refurbished where necessary to restore the condition to that pertaining at the time of leaving the factory.

        - Lifting equipment

All aspects of lifting equipment, including design, fabrication and installation work shall be in full accordance with the relevant aspects of the relevant safety codes. Contractor shall specify and supply all lifting devices where deemed necessary throughout the plant to aid in the handling and operation of equipment. Appropriate space shall be provided throughout the plant for the use of such lifting devices and equipment being handled.

Lifting equipment shall be designed and constructed in accordance with at least the following technical guidelines:

The safe working load (SWL) shall be marked clearly on all items.

The complete installation shall be inspected and shall be tested over its complete lifting range using a load which is at least 125 % of the safe working load and appropriate impact factor for supporting elements during the load test.

High-tensile or alloy steel chains shall have a factor of safety of at least four. Chains shall have a factor of safety of at least five. Steel-wire ropes shall have a factor of safety of at least six.

No man-made fibre ropes, woven webbing or natural fibre ropes shall be acceptable.

Hoists shall be provided with a slipping clutch, or equivalent, which shall ensure that it is not possible to overload the hoist. Powered hoists shall hold the load upon power failure; i.e. shall feature fail-to-safe braking.

Crawl beams shall be hot-dip galvanised after all fabrication. If the beam is drilled or welded or the zinc coating is damaged by any other fabrication technique, the complete beam shall have the zinc removed by abrasive blasting and it shall be returned to the galvanisers for hot-dip galvanising. Repair using cold-applied zinc products will not be acceptable.  Crawl beams shall be anchored to concrete using grade 316 stainless steel anchor bolts. The anchor bolts shall, preferably, be through-bolted. If chemical anchors are used, every anchor shall be load-tested prior to installation of the beam. A nickel-based anti-seize compound shall be applied to bolt threads prior to fastening of the nut and galled fasteners shall be removed and replaced.

Crawl beams shall be fastened to hot-dip galvanised steel support structures using hot-dip galvanised fasteners.

The design, fabrication and installation of overhead travelling cranes required in the high-lift pump stations shall comply with the following:

- Construction of the crane shall be in accordance with BS EN 13001-1 and -2 as applicable.

- All welding of steelwork shall be carried out in accordance with BS 5135 by competent artisans meeting the requirements of BS 4872.

- The Contractor may use a crane during the installation of other equipment on condition that all testing and certification for the complete lifting installation, including supporting structure, has been successfully completed.

- The hoist shall be supported on and travel along a fabricated steel crane beam structure.

- The crane beam shall be supported on and travel along crane rails.

- The rails shall be supported along their full length, either on a concrete ring beam or on additional hot-dip galvanised steel beams.

The crane long travel, cross travel and hoist shall be electrically powered or manually operated as deemed necessary for the application at hand. Unless otherwise stated, the lowest hook level shall be room floor level and all operating chains shall fall to one metre above this level.

All materials shall be new and unused and suited to the application. Structural steelwork shall comply with the requirements of SANS 1431 and the grade used for structural members shall be 300 C. Site welding will not be acceptable.

The crane beam and end carriages shall be designed with suitable dimensions, wheel spacing and gusset plates or diagonal bracing to prevent cross-whipping. End stops with rubber buffers shall be fitted to prevent the hoist from moving off the travelling beam and to limit the long travel along the rails.

Lubrication systems shall be designed to exclude dirt and moisture and all gear wheels shall be fully enclosed. Bearings shall be mounted in properly sealed Plummer blocks or in totally enclosed and sealed housings, grease-lubricated and provided with grease nipples in both cases. The open type bearing units with exposed "lubricated for life" bearings will not be acceptable. The safe working load shall be permanently marked on the crane hook and on both sides of the girder. An overload prevention device, such as a clutch which slips upon overloading, shall be incorporated.

The bottom hook shall swivel on a ball or roller bearing through 360º and shall be fitted with a safety latch. The bearing shall have a protective skirt. Lifting chain is preferred, but corrosion-protected steel wire rope is acceptable for higher loads. A chain box for the unloaded length of lifting chain shall be provided.

The crane rails shall be supported on and secured to the concrete or steel gantry beams and shall be installed true to span, level, aligned, and shall be straight to within the permissible deviations given in BS EN 13598-1 over their entire length. The crane rails shall be made from standard rail sections. Rails manufactured from square section steel bar will not be acceptable. Rails shall be joined using fish-plates, with at least four fasteners, to provide a continuous path for the travel of the crane wheels. The rails shall be hot-dip galvanized after all fabrication work.

The distance between rail supports shall not exceed 1 000 mm and supports shall be anchored using grade 316 stainless steel bolts. Where it is deemed necessary, a personnel platform for two people shall be provided on the crane structure. The platform shall be bolted to the crane beam structure and shall be removable. The steel sections which form the crane beam shall be provided with welded lugs to which the platform shall be bolted. The complete platform and all guard-railing shall be hot-dip galvanised after fabrication. The platform itself shall be designed so that a person standing on it will be able to replace the electric lamps. A hot-dip galvanised steel ladder shall be provided for accessing the platform. The platform floor shall have a minimum width of 500 mm.

Crane rail anchor bolts shall be M16 or larger and shall be of grade 316 stainless steel. Fasteners smaller than 12 mm shall be of grade 316 stainless steel. All other fasteners, including high-tensile fasteners, shall be of stainless steel or shall be hot-dip galvanized. Before assembly, the threads of all bolts and studs shall be coated with an approved nickel-based, anti-seize corrosion protection compound.

The crane beam and end carriages shall be zinc-sprayed and sealed. Smaller items, such as cable brackets and protective covers, shall be hot-dip galvanized. The crane and rails, when erected and installed, shall be of neat and workmanlike appearance, solidly and evenly supported, true to line, level, plumb and in proper working order.

In the alignment of equipment or structures, the use of multiple shims will not be permitted. All shimmed feet shall be neatly grouted to provide corrosion protection. The full length of the rails shall be grouted in cases in which the rails rest on a concrete ring beam. A suitable gap between the rails and the beam shall be provided for application of the grout. The grout shall be applied strictly in accordance with the manufacturer's instructions. The grout shall be neatly finished with a 45º chamfer.

The Contractor shall supply a certificate from the manufacturer which:

- certifies that the crane has been manufactured in accordance with the requirements of the safety codes;

- specifies the design standards used, and;

- states the safe working load and the test load.

This certificate shall be provided prior to delivery of the crane to Site.

Hand cranked winches shall be rated for a safe working load at least 100 % in excess of the calculated load. All gears, clutches, etc., shall be enclosed in a robust cast iron or cast steel casing which shall be grease filled and sealed against ingress of dirt and moisture. The winch shall be designed to hold the load stationary when the hand crank is released during raising or lowering. In addition, a locking arrangement to lock the position of the load shall be provided.

The force required to operate the winch at its maximum rated load shall not exceed 100 N. The radius at which the handle operates shall preferably be adjustable. A double handled crank or two opposing cranks shall be provided when necessary to ensure easy operation in all positions possible with the mounting arrangement provided.

The wire rope and all attachments shall be of grade 316 stainless steel with a safety factor of at least 6. The wire rope shall be long enough to reach the lowest required position with at least 3 turns left on the drum. The drum size shall easily store the full rope length. The inside diameter of the drum shall suit the rope diameter in accordance with good engineering practice approved by the wire rope manufacturer.

The maximum safe working load shall be clearly and permanently marked on the winch. The drum support brackets, all exposed fasteners, shafts, handles, pins, etc., shall be grade 316 stainless steel and the casing shall be hot-dip galvanized or zinc-sprayed (to a thickness of 150 µm) and then painted.

        - Fall Arrest System:

The Fall Arrest System shall be designed, supplied and installed. The Fall Arrest system shall be used when carrying maintenance on a Crane. The system shall be in accordance with the following standards:

SANS 50353-2: Personal protective equipment against falls from a height - Guided type fall arresters including a flexible anchor line

SANS 50354 Personal protective equipment against falls from a height – Lanyards

SANS 50361 Personal protective equipment against falls from a height - Full body harnesses

SANS 50364 Personal protective equipment against falls from a height - Test methods

        - Surge protection

A surge tank pressure vessel may be supplied on systems to counteract undue excessive transient pressures from shock waves due to pump start-up, shutdown, and valve shut-off or power failures.

The work shall consist of the furnishing of all labour, materials, equipment and Appurtenances for surge protection at the discharge side of each pump/turbine system to prevent column separation and/or to limit surge upon pump shutdown including a power failure situation.

The surge arrestor shall consist of a cylindrical pressure tank for surge control, including: shell assembly, pressure gauge, isolation valves, safety valve, NRVs and other miscellaneous appurtenances, constructed in accordance with A.S.M.E. Section VIII Pressure Vessel Code Division. The surge arrestor shall be constructed on a reinforced concrete foundation with steel supports. The vessel shall be fitted with a ½” cross connection on the top of the vessel into which the pressure gauge and all necessary fittings and valves will be fitted.

The connecting pipework from the vessel to the pipeline must be allowed for and must be at least the same size as the vessel outlet and manufactured and designed to ASME B31.3 up to the first isolating valve from the vessel. The piping, fittings, flanges and jointing material from the vessel up to the first isolating valve are considered part of the pressure vessel and will be subject to the same design, inspection, material and quality requirements as the pressure vessel. The piping must also allow for flanges and/or stubs (flanged) to fit the valves.

The material of construction of the pressure vessel must be as a minimum SA516 Grade 60. The interior paint finish must be solvent-free chemicall cured Epoxy to a minimum 600µm dry film thickness. The exterior paint finish must be an Epoxy to a minimum 600µm dry film thickness.

Each Pressure Vessel must be fitted with the following valves as a minimum:-

- Carbon steel gate valve for isolation and must be the size of the vessel outlet, fitted with gearbox and handwheel.

- 1 off flanged two piece stainless steel ball valves, flanged for drainage purposes.

- A safety relief valve complete with dome cap and lockable, carbon steel body, carbon steel spring and stainless steel trim.

The design pressure shall be determined by means of an acceptable and recognised surge analysis software tool showing: input data for the piping system, initial flow rate, initial and maximum expanded air volume and envelope of maximum and minimum line pressure throughout the pipe system.

In addition, a predicted pressure-time history at the pump station/ System  and at other critical points in the pipe system will also be required. The hydro-pneumatic surge control system shall include a surge tank, valves, instruments and other miscellaneous appurtenances as is deemed necessary by the Contractor. The operation, control and type of non-return valves installed on these systems shall also be subject to the findings of the surges analysis. The surge tank must be designed to match the dynamics of the pumping system. The surge tank supplier shall indicate the percent of fluid in the tank.

        - Heating, ventilation and air conditioning

- supply and installation of units for the plant where required;

- training of staff to operate plant;

- maintenance manuals, maintenance program, warranties etc.;

- painting of all equipment with corrosion protection painting.

- mounting brackets, supports, plinths, bracings and other fixing material;

- commissioning and handing over to client in full operational status; and

- guarantee and maintenance.

- Energy efficient units to be considered.

- Built in intelligent sensor to detect movement of people to automatically switch between normal operation and energy saving operation.

- HVAC Control strategies.

- List of any specialist tools.

AC units can be either Heat Pump type or Heat Recovery System.

AC Heat Pump type units shall be equipped with frost protection and defrost control. The following installation requirements are applicable:

- the indoor units shall be mounted on robust galvanized and painted wall brackets

- the condensers shall be mounted on robust heavy duty galvanized and painted wall brackets

- Refrigerant charge to be R410A

- Pipework to be properly fixed and supported where required shall be run on galvanized trays

- the bottom of the condenser units shall not be lower than 2200mm from the finished floor level

- the indoor units shall be generally be with the top of unit 150mm below the ceiling

- where natural fall is not possible on drain piping, the units shall be equipped with heavy duty continuous duty in-line condensing water pumps

- gas lines, cables and drains shall run inside PVC trunking from the inside units up to the condenser units

- all gas line shall be Armaflex insulated. Drains shall be insulated for the first 2 meters from indoor units

- the trunking shall be large enough to house the gas lines, cables and drains comfortably without bulging or damaging the trunking and lid. If required, additional trunking will be added to house all lines.

- drains shall be extended to the nearest gulley

- drain pipes shall be minimum 25mm diameter

- gas lines shall be sized according to the manufacturer’s specifications. Cognisance shall be taken of lengths of piping and pipe diameters shall be increased where necessary to keep the operating parameters within the specified capacities

- both suction lines and liquid lines shall be insulated with minimum 8mm wall thickness insulation material

- all drain pipes shall be uPVC class 3

- fittings shall be properly glued on, to prevent any leaks

- the first 2 meters of drain lines will be insulated with minimum 8mm wall thickness insulation material to prevent condensation.

- one power point must be provided within 1,5 m from the outdoor unit, in the form of a weather proof 60A (3ph or 1 ph as required) isolator

- cable and wiring sizes to this point will be able to handle the total load of each unit with a minimum voltage drop of 5% from point of source

- all wiring from the outdoor units to the indoor units will conform to the suppliers specifications

- medium duty galvanized wire mesh trays must be provided to house all cable, gas lines and drains between indoor and outdoor units

- sizes may vary from 100 mm wide to 300 mm wide as applicable

- additional hangers must be provided were fixing points are more that 2m apart

- cable, gas lines and drains outside buildings will be housed in large enough PVC trunking with lids

- final wire mesh trays and trunking routes shall be discussed and pointed out on site

- Fans and other associated HVAC equipment, shall be adequately sized and designed to run under specified site conditions and shall be suitable for indoor and outdoor application. The fan motor closure rating shall be of IP68 and shall be capable of operating for long periods.

The designer shall take all other precautions to eliminating high noise levels and shall minimize vibrations in all mechanical and electrical components. All noise levels relative to the installation shall be in accordance with SANS10103 requirements or equivalent standard.

The applicable standards for HVAC are given below.

SANS SPECIFICATIONS

- SANS 1200	Standardized Specifications for Civil Engineering Construction

- SANS 10064	The preparation of steel surfaces for coating

- SANS 10400	The application of the National Building Regulations

- SANS 1200 HC	Corrosion protection of structural steelwork

- SANS 1091	National colour standards for paint

- SANS 460	Plain-ended solid drawn copper tubes for potable water

- SANS 455	Covered electrodes for the manual arc welding of carbon and carbon manganese steels

- SANS 966-1	Components of pressure pipe systems Part 1: Unplasticized poly(vinyl chloride) (PVC-U) pressure pipe systems

- SANS 967	Unplasticized poly(vinyl chloride) (PVC-U) soil, waste and vent pipes and pipe fittings

- SANS 10044	Welding : Parts I to VII

- SANS 10238	Welding and thermal cutting processes – Health and safety

- SABS EN 10240	Internal and/or external protective coatings for steel tubes – Specification for hot- dip galvanized coatings applied in automatic plants.

- SANS 121	Hot-dip galvanized coatings on fabricated iron and steel articles – Specification and test methods.

- SANS 1019	Determination of sound power levels of noise sources – Guidelines for the use of basic standards for the reparation of noise test codes

- SANS 10064	The preparation of steel surfaces for coating

- SANS 10103		The measurement and rating of environmental noise with respect to annoyance and to speech communication.

- SANS 10021	Waterproofing of Buildings

- SANS 204	Energy Efficiency in Buildings

- SANS ISO 3575	Continuous hot-dip zinc-coated carbon steel sheet of commercial, lock forming and drawing qualities

- SANS 10214	The design, fabrication and inspection of articles for hot-dip galvanising

- SANS 1186-1	Symbolic Safety Signs Part I : Standard signs and general requirements.

- SANS 62	Steel Pipes Part 1 : Steel pipes of NB not exceeding 200 mm.

- Steel Pipes Part 2 : Pipes and pipe fittings of nominal bore not exceeding 150 mm, made from steel pipe.

- SANS 0147	Refrigerating System including Plants associated with air-conditioning systems.

- SANS 1125	Room air conditioners and heat pumps

- SANS 719	Electric welded low carbon steel pipes for aqueous fluids (ordinary duties)

- SANS 193	Fire Dampers

- SABS 10173	The installation, testing and balancing of air-conditioning duct work

- SANS 10103	The measurement and rating of environmental noise with respect to annoyance and speech communication

- SANS 10140	Identification colour marking

- SANS 630	Decorative high-gloss enamel paint for interior and exterior

- SANS 1238	HVAC duct construction standards - air conditioning ductwork

- SANS 1062	Pressure and vacuum gauges

- SANS 10227-2	Pressure vessels, inspectorates, certification (approval), modified or repaired pressure vessels.

- SANS 1424	Filters for use in air-conditioning and general ventilation Machines for miscellaneous applications.

Applicable HVAC standards

BS SPECIFICATIONS

BS 10	Specification for flanges and bolting for piping, valves and fittings.

BS EN 10216-1

BS EN 10217-1 Specification for carbon steel pipes and tubes with specified room temperature properties for pressure purposes

BS 4504	Circular flanges for pipes, valves and fittings (PN designated)

3.1	Specification for steel flanges

3.3	Specification for copper alloy and composite flanges.

BS 13001-1

BS 13001-2

# Hydro-Mechanical

      - Bronberg Reservoir

        - Scope

This Schedule sets out the design, manufacture, supply, delivery and installation requirements for hydro-mechanical infrastructure at including but not limited to.

- Inlet Valve

- Outlet Valve

- Flow straightener

- Turbine

- Gearbox

- Generator

- Cooling system

- Bypass Valve

        - Inlet valve

Each turbine shall be provided with a main inlet valve capable of closing without an external power source under maximum flow.

The rate of closure of the main inlet valve shall be controlled so as to limit the transient pressures in the pipeline within the maximum pressure limits given in Part 4: Site Information.

The main inlet valve shall be a double flanged and capable of use as a termination valve when the turbine is removed.

The valve shall include auxiliary contacts to show the current position of the valve and provide for future remote indication of the valve position.

The turbine contractor shall ensure that the supplied equipment is installed correctly and datum levels for the equipment is correct.

The mating surfaces between the turbine and the pipe shall be identical in dimension and profile and no abrupt dimension changes shall be accepted.

Take offs for the cooling water turbine shall be from this pipe.

        - Outlet valve

Each turbine shall be provided with an outlet valve capable of closing without an external power source under maximum flow. The outlet valve shall be capable of isolating the turbine for dismantling.

The valve shall be manually operated and designed to open and close under balance, no flow conditions.

The discharge outlet valve shall be a double flanged and capable of use as a termination valve when the turbine is removed.

The valve shall include auxiliary contacts to show the current position of the valve and provide for future remote indication of the valve position.

        - Flow straightener

The flow straightener shall minimize turbulence to ensure optimum inlet conditions throughout the operating range of the turbine.

The flow straightener shall be designed, supplied and installed by the turbine contractor in the inlet and intermediate pipework.

The turbine contractor shall ensure that the supplied equipment is installed correctly and datum levels for the equipment are correct.

The turbine contractor shall supply a 100 mm drain point with a 100 mm sluice drain valve. The drainpipe shall be at the bottom of the pipe and the valve shall be installed vertically. The drainage water shall be piped to the sump.

        - Turbine

The turbine shall be designed such that on load rejection the transient pressure in the pipeline is within the maximum pressure limits given in Part 4: Site Information. If necessary this may be achieved by the addition of a suitably sized pressure relief valves, incorporation of a flywheel or mechanical braking system.

The rate of movement of the wicket gates or needle valves shall be controlled so as to limit the transient pressures in the pipeline within the maximum pressures limits given in Site Information.

The turbine shall be designed to withstand runaway speed for the time required for the controlled closing of the main inlet valve.

All turbine parts shall have good resistance to fatigue, cavitation, erosion and corrosion. All bushing shall be of a self-lubricated type if possible.

The turbine and governing system shall be provided with sufficient monitoring and protection devices for the safe operation of the Generating Plant. As a minimum this shall include:

- Turbine overspeed protection

- Bearing oil level monitoring

- Bearing temperature monitoring

- Governor system oil level monitoring

- Governor system oil pressure monitoring

- Cooling water circulation monitoring

        - Gearbox

The gearbox shall be designed and installed by the contractor to suit the individual requirements of each turbine design and running conditions.

        - Generator

The generator shall be a synchronous generator with a static or brushless excitation system.

The generator and bearings shall be designed to withstand runaway speed of the turbine for the time required for the controlled closing of the main inlet valve.

The generator and excitation system shall be provided with sufficient monitoring and protection devices for the safe operation of the Generating Plant. As a minimum this shall include:

- Stator temperature monitoring

- Bearing oil level monitoring

- Bearing temperature monitoring

- Cooling water circulation monitoring

- Overcurrent protection (stator and rotor)

- Earth fault protection (stator and rotor).

- Under and over voltage protection

- Under and over frequency protection

- Reverse Power protection

- Generator differential protection

        - Cooling system

Where possible, air cooling of the generator and bearings is preferred.

Where water cooling is necessary, the design must include means to ensure there is no possibility of contamination of the discharged cooling water. The tender shall provide information on the design methods employed.

        - Flowmeter

The flowmeter shall be purchased by the contractor from a flowmeter supplier and installed by the contractor.

The flowmeter shall be of the full bore flanged electromagnetic induction type to be installed in a pipeline the same diameter as the turbine inlet pipe.

The flowmeter shall be installed in the hydropower building and shall therefore comply with IP68 requirements.

The accuracy of the flowmeter shall equal or better that specified in the applicable Rand Water specification.

The flowmeters shall be supplied, calibrated, tested and delivered with two sets of calibration certificates, installation, and service and maintenance manuals for each meter. The meters shall be flanged and the quote shall include for locally manufactured carbon steel mating plate flanges, bolts and nuts. An electrical isolation kit shall be supplied with each meter. Calibration and testing shall be carried out as stipulated. The Contractor shall guarantee each of the material items against defects in manufacture and errors or omissions in assembly, calibration and inspection.

The flowmeter shall be able to operate from a 24 VDC power supply. The power supply shall be supplied with the flowmeter. The power supply shall operate from a 231 VAC single phase supply. The basic accuracy and function of the meter shall not be effected by voltage variations of 15% of the nominal supply value. The electronic converter shall be clearly marked with the power supply requirements.

It shall be possible to communicate with the PLC in order to monitor the flow rate and the status of the flowmeter as defined in the applicable Rand Water specification.

General specification:

        - Each meter shall be of the flanged type.

        - The meters shall be suitable for measuring the flow of potable water normally at a temperature between 10C and 25C and has a conductivity within the range 20 to 150 mS/m.

        - The specific design criteria of internal diameter, power supply, working and test pressure, maximum flow rate, tag numbers and quantity shall be as stipulated in the relevant schedule.

        - The meters shall be manufactured to the same general design and basic model number. The designed maximum uncertainty factor shall be better than 0,25% of the actual flow rate for both  the displayed reading and the transmitted signals. The basic accuracy of the meter shall be maintained between fluid velocities of 300 to 10 000 mm per second. The long-term stability of the electronic components and the flow head assembly shall be better than 0,05% of the flow rate at three meters per second over a period of 12 (twelve) months. There shall be no requirement to adjust the calibration factors or zero setting after testing and calibration

        - It is essential that the complete flowmeter shall be designed, manufactured, calibrated and delivered such that the original calibration parameters can easily be reconfirmed while the meter remains installed (in situ) in the service pipeline. It shall be possible to print out a confirmation calibration certificate with a full traceable accuracy to 1% of the original factory calibration certificate.

Flow tube assembly

        - Each flow tube shall be rated for a working pressure as listed in the relevant schedule. This pressure includes for the normal head and additional expected system generated surge pressures. The meter tube shall be designed to withstand at least 150% of the rated working pressure without permanent deformation.

        - The nominal bore diameter of the flow tube extensions are listed in the relevant schedule. The combined inaccuracy of the diameter and the ovality of the flow tube extensions shall be within 10 mm or 1% of the specified value whichever is the lesser. The diameter shall be determined by the average of four measurements at each end of the stainless steel tube extensions of the meter body.

        - All electrical wiring on the flow tube, sensors and coils, shall be designed to withstand a voltage impulse with respect to the steel pressure tube of 5 000 Volts for 1,5 seconds.

        - The signal cable connection shall be sealed against the ingress of moisture to IP 68 to withstand a permanent water head of at least four meters above the centre line of the flow tube consequent to installation.

        - Each flow tube shall be supplied with a separate electronic flow transmitter and screened signal cable of length as stipulated in Table 1 for magnetic coil power and sensor signals. The cable length ends shall be sealed against the ingress of water for transportation and storage purposes.

        - The environmental protection requirement for the complete flow tube shall be IP 68 with four meters of water above the centre line of the meter tube and shall be suitable for installation in a chamber.

        - An engraved identification plate manufactured from a corrosion resistant material such as aluminum or 316 stainless steel shall be permanently fixed within 100 mm of the cable connection box. The size of the numbers/letters shall be at least 5 mm and clearly show the following information:

          - Diameter.

          - Calibration factors.

          - Serial and tag numbers.

          - The working pressure rating of the flow tube.

          - Electronic flow transmitter

        - The electronic flow transmitter (EFT) enclosure shall be suitable for the protection of the electronic components from exposure to ambient conditions associated with temperature variations from minus 10C to plus 40C with relative humidity from 20% to 95% condensing. The environmental dust factor is normally very high therefore the environmental protection for the electronic converter module shall not be less than be IP 65.

        - The EFT shall be microprocessor based, re-programmable, rugged and have an assessed meantime between failure in excess of 25 000 hours. The unit shall incorporate an illuminated digital display that is readable in low light conditions.

        - The digital display shall be capable of displaying the forward and reverse flow rate as well as the totalised values for both directions in the engineering units of M/d. The display shall have a minimum of eight digits to display the totalised flow values. The totalised values shall NOT be able to be reset at any time nor during power failures. The totalised values shall continue in increment until a maximum displayable value is reached upon which it shall reset to zero.

        - The EFT shall provide galvanically isolated dual analogue current output signals directly proportional to the flow rate for the forward and reverse flow values respectively. The signal output range shall be 4 to 20 mA, each capable of feeding into a load of 750 Ohms. Volt free pulsed contacts suitable for triggering remote forward and reverse totalised counters shall be provided. The frequency output pulses shall be in direct proportion to the respective flow rate and the contacts rated at 25 Volts and 250 mA DC

        - A data communication port shall be provided with either RS-422/485/232 serial communications or a HART interface that can be permanently connected to a local IO device or computer. Software required to access the flow rate, totalised values both forward and reverse, alarm and status information from the EFT shall be included for the portable programmer. The communication protocol shall be made available to Rand Water for RTU and telemetry interfacing.

Portable Programmer

        - The parameters associated with physical constants, flow rate, integration period and output signals shall all be set within the memory by the use of a removable portable programmer. The programmer shall incorporate a user-selected access code to prevent unauthorised changes to the programmable variables. The programmer shall be easily connected to the EFT via a plug- in connector for the upload and download of parameters to and from the EFT.

Detail requirements are given in the applicable Rand Water specification listed in Chapter 2 of this Specification.

        - Bypass valve

Bypass valves shall be designed and installed by the contractor with reference to valve specification RW/0310/AS0460 Rev 3.

      - Brakfontein Reservoir

        - Scope

This Schedule sets out the design, manufacture, supply, delivery and installation requirements for hydro-mechanical infrastructure including but not limited to.

- Inlet Valve

- Outlet Valve

- Flow straightener

- Turbine

- Gearbox

- Generator

- Cooling system

- Bypass Valve

        - Inlet valve

Each turbine shall be provided with a main inlet valve capable of closing without an external power source under maximum flow.

The rate of closure of the main inlet valve shall be controlled so as to limit the transient pressures in the pipeline within the maximum pressure limits given in Part 4: Site Information.

The main inlet valve shall be a double flanged and capable of use as a termination valve when the turbine is removed.

The valve shall include auxiliary contacts to show the current position of the valve and provide for future remote indication of the valve position.

The turbine contractor shall ensure that the supplied equipment is installed correctly and datum levels for the equipment is correct.

The mating surfaces between the turbine and the pipe shall be identical in dimension and profile and no abrupt dimension changes shall be accepted.

Take offs for the cooling water turbine shall be from this pipe.

        - Outlet valve

Each turbine shall be provided with an outlet valve capable of closing without an external power source under maximum flow. The outlet valve shall be capable of isolating the turbine for dismantling.

The valve shall be manually operated and designed to open and close under balance, no flow conditions.

The discharge outlet valve shall be a double flanged and capable of use as a termination valve when the turbine is removed.

The valve shall include auxiliary contacts to show the current position of the valve and provide for future remote indication of the valve position.

        - Flow straightener

The flow straightener shall minimize turbulence to ensure optimum inlet conditions throughout the operating range of the turbine.

The flow straightener shall be designed, supplied and installed by the turbine contractor in the inlet and intermediate pipework.

The turbine contractor shall ensure that the supplied equipment is installed correctly and datum levels for the equipment are correct.

The turbine contractor shall supply a 100 mm drain point with a 100 mm sluice drain valve. The drainpipe shall be at the bottom of the pipe and the valve shall be installed vertically. The drainage water shall be piped to the sump.

        - Turbine

The turbine shall be designed such that on load rejection the transient pressure in the pipeline is within the maximum pressure limits given in Part 4: Site Information. If necessary this may be achieved by the addition of a suitably sized pressure relief valves, incorporation of a flywheel or mechanical braking system.

The rate of movement of the wicket gates or needle valves shall be controlled so as to limit the transient pressures in the pipeline within the maximum pressures limits given in Site Information.

The turbine shall be designed to withstand runaway speed for the time required for the controlled closing of the main inlet valve.

All turbine parts shall have good resistance to fatigue, cavitation, erosion and corrosion. All bushing shall be of a self-lubricated type if possible.

The turbine and governing system shall be provided with sufficient monitoring and protection devices for the safe operation of the Generating Plant. As a minimum this shall include:

- Turbine overspeed protection

- Bearing oil level monitoring

- Bearing temperature monitoring

- Governor system oil level monitoring

- Governor system oil pressure monitoring

- Cooling water circulation monitoring

        - Gearbox

The gearbox shall be designed and installed by the contractor to suit the individual requirements of each turbine design and running conditions.

        - Generator

The generator shall be a synchronous generator with a static or brushless excitation system.

The generator and bearings shall be designed to withstand runaway speed of the turbine for the time required for the controlled closing of the main inlet valve.

The generator and excitation system shall be provided with sufficient monitoring and protection devices for the safe operation of the Generating Plant. As a minimum this shall include:

- Stator temperature monitoring

- Bearing oil level monitoring

- Bearing temperature monitoring

- Cooling water circulation monitoring

- Overcurrent protection (stator and rotor)

- Earth fault protection (stator and rotor).

- Under and over voltage protection

- Under and over frequency protection

- Reverse Power protection

- Generator differential protection

        - Cooling system

Where possible, air cooling of the generator and bearings is preferred.

Where water cooling is necessary, the design must include means to ensure there is no possibility of contamination of the discharged cooling water. The tender shall provide information on the design methods employed.

        - Flowmeter

The flowmeter shall be purchased by the contractor from a flowmeter supplier and installed by the contractor.

The flowmeter shall be of the full bore flanged electromagnetic induction type to be installed in a pipeline the same diameter as the turbine inlet pipe.

The flowmeter shall be installed in the hydropower building and shall therefore comply with IP68 requirements.

The accuracy of the flowmeter shall equal or better that specified in the applicable Rand Water specification.

The flowmeters shall be supplied, calibrated, tested and delivered with two sets of calibration certificates, installation, and service and maintenance manuals for each meter. The meters shall be flanged and the quote shall include for locally manufactured carbon steel mating plate flanges, bolts and nuts. An electrical isolation kit shall be supplied with each meter. Calibration and testing shall be carried out as stipulated. The Contractor shall guarantee each of the material items against defects in manufacture and errors or omissions in assembly, calibration and inspection.

The flowmeter shall be able to operate from a 24 VDC power supply. The power supply shall be supplied with the flowmeter. The power supply shall operate from a 231 VAC single phase supply. The basic accuracy and function of the meter shall not be effected by voltage variations of 15% of the nominal supply value. The electronic converter shall be clearly marked with the power supply requirements.

It shall be possible to communicate with the PLC in order to monitor the flow rate and the status of the flowmeter as defined in the applicable Rand Water specification.

General specification:

        - Each meter shall be of the flanged type.

        - The meters shall be suitable for measuring the flow of potable water normally at a temperature between 10C and 25C and has a conductivity within the range 20 to 150 mS/m.

        - The specific design criteria of internal diameter, power supply, working and test pressure, maximum flow rate, tag numbers and quantity shall be as stipulated in the relevant schedule.

        - The meters shall be manufactured to the same general design and basic model number. The designed maximum uncertainty factor shall be better than 0,25% of the actual flow rate for both the displayed reading and the transmitted signals. The basic accuracy of the meter shall be maintained between fluid velocities of 300 to 10 000 mm per second. The long-term stability of the electronic components and the flow head assembly shall be better than 0,05% of the flow rate at three meters per second over a period of 12 (twelve) months. There shall be no requirement to adjust the calibration factors or zero setting after testing and calibration

        - It is essential that the complete flowmeter shall be designed, manufactured, calibrated and delivered such that the original calibration parameters can easily be reconfirmed while the meter remains installed (in situ) in the service pipeline. It shall be possible to print out a confirmation calibration certificate with a full traceable accuracy to 1% of the original factory calibration certificate.

Flow tube assembly

        - Each flow tube shall be rated for a working pressure as listed in the relevant schedule. This pressure includes for the normal head and additional expected system generated surge pressures. The meter tube shall be designed to withstand at least 150% of the rated working pressure without permanent deformation.

        - The nominal bore diameter of the flow tube extensions are listed in the relevant schedule. The combined inaccuracy of the diameter and the ovality of the flow tube extensions shall be within 10 mm or 1% of the specified value whichever is the lesser. The diameter shall be determined by the average of four measurements at each end of the stainless steel tube extensions of the meter body.

        - All electrical wiring on the flow tube, sensors and coils, shall be designed to withstand a voltage impulse with respect to the steel pressure tube of 5 000 Volts for 1,5 seconds.

        - The signal cable connection shall be sealed against the ingress of moisture to IP 68 to withstand a permanent water head of at least four meters above the centre line of the flow tube consequent to installation.

        - Each flow tube shall be supplied with a separate electronic flow transmitter and screened signal cable of length as stipulated in Table 1 for magnetic coil power and sensor signals. The cable length ends shall be sealed against the ingress of water for transportation and storage purposes.

        - The environmental protection requirement for the complete flow tube shall be  IP 68  with four meters of water above the centre line of the meter tube and shall be suitable for installation in a chamber.

        - An engraved identification plate manufactured from a corrosion resistant material such as aluminum or 316 stainless steel shall be permanently fixed within 100 mm of the cable connection box. The size of the numbers/letters shall be at least 5 mm and clearly show the following information:

          - Diameter.

          - Calibration factors.

          - Serial and tag numbers.

          - The working pressure rating of the flow tube.

          - Electronic flow transmitter

        - The electronic flow transmitter (EFT) enclosure shall be suitable for the protection of the electronic components from exposure to ambient conditions associated with temperature variations from minus 10C to plus 40C with relative humidity from 20% to 95% condensing. The environmental dust factor is normally very high therefore the environmental protection for the electronic converter module shall not be less than be IP 65.

        - The EFT shall be microprocessor based, re-programmable, rugged and have an assessed meantime between failure in excess of 25 000 hours. The unit shall incorporate an illuminated digital display that is readable in low light conditions.

        - The digital display shall be capable of displaying the forward and reverse flow rate as well as the totalised values for both directions in the engineering units of M/d. The display shall have a minimum of eight digits to display the totalised flow values. The totalised values shall NOT be able to be reset at any time nor during power failures. The totalised values shall continue in increment until a maximum displayable value is reached upon which it shall reset to zero.

        - The EFT shall provide galvanically isolated dual analogue current output signals directly proportional to the flow rate for the forward and reverse flow values respectively. The signal output range shall be 4 to 20 mA, each capable of feeding into a load of 750 Ohms. Volt free pulsed contacts suitable for triggering remote forward and reverse totalised counters shall be provided. The frequency output pulses shall be in direct proportion to the respective flow rate and the contacts rated at 25 Volts and 250 mA DC

        - A data communication port shall be provided with either RS-422/485/232 serial communications or a HART interface that can be permanently connected to a local IO device or computer. Software required to access the flow rate, totalised values both forward and reverse, alarm and status information from the EFT shall be included for the portable programmer. The communication protocol shall be made available to Rand Water for RTU and telemetry interfacing.

Portable Programmer

        - The parameters associated with physical constants, flow rate, integration period and output signals shall all be set within the memory by the use of a removable portable programmer. The programmer shall incorporate a user-selected access code to prevent unauthorised changes to the programmable variables. The programmer shall be easily connected to the EFT via a plug- in connector for the upload and download of parameters to and from the EFT.

Detail requirements are given in the applicable Rand Water specification listed in Chapter 2 of this Specification.

        - Bypass valve

Bypass valves shall be designed and installed by the contractor with reference to valve specification RW/0310/AS0460 Rev 3.

      - Klipfontein Reservoir

        - Scope

This Schedule sets out the design, manufacture, supply, delivery and installation requirements for hydro-mechanical infrastructure including but not limited to.

- Inlet Valve

- Outlet Valve

- Flow straightener

- Turbine

- Gearbox

- Generator

- Cooling system

- Bypass Valve

        - Inlet valve

Each turbine shall be provided with a main inlet valve capable of closing without an external power source under maximum flow.

The rate of closure of the main inlet valve shall be controlled so as to limit the transient pressures in the pipeline within the maximum pressure limits given in Part 4: Site Information.

The main inlet valve shall be a double flanged and capable of use as a termination valve when the turbine is removed.

The valve shall include auxiliary contacts to show the current position of the valve and provide for future remote indication of the valve position.

The turbine contractor shall ensure that the supplied equipment is installed correctly and datum levels for the equipment is correct.

The mating surfaces between the turbine and the pipe shall be identical in dimension and profile and no abrupt dimension changes shall be accepted.

Take offs for the cooling water turbine shall be from this pipe.

        - Outlet valve

Each turbine shall be provided with an outlet valve capable of closing without an external power source under maximum flow. The outlet valve shall be capable of isolating the turbine for dismantling.

The valve shall be manually operated and designed to open and close under balance, no flow conditions.

The discharge outlet valve shall be a double flanged and capable of use as a termination valve when the turbine is removed.

The valve shall include auxiliary contacts to show the current position of the valve and provide for future remote indication of the valve position.

        - Flow straightener

The flow straightener shall minimize turbulence to ensure optimum inlet conditions throughout the operating range of the turbine.

The flow straightener shall be designed, supplied and installed by the turbine contractor in the inlet and intermediate pipework.

The turbine contractor shall ensure that the supplied equipment is installed correctly and datum levels for the equipment are correct.

The turbine contractor shall supply a 100 mm drain point with a 100 mm sluice drain valve. The drainpipe shall be at the bottom of the pipe and the valve shall be installed vertically. The drainage water shall be piped to the sump.

        - Turbine

The turbine shall be designed such that on load rejection the transient pressure in the pipeline is within the maximum pressure limits given in Part 4: Site Information. If necessary this may be achieved by the addition of a suitably sized pressure relief valves, incorporation of a flywheel or mechanical braking system.

The rate of movement of the wicket gates or needle valves shall be controlled so as to limit the transient pressures in the pipeline within the maximum pressures limits given in Site Information.

The turbine shall be designed to withstand runaway speed for the time required for the controlled closing of the main inlet valve.

All turbine parts shall have good resistance to fatigue, cavitation, erosion and corrosion. All bushing shall be of a self-lubricated type if possible.

The turbine and governing system shall be provided with sufficient monitoring and protection devices for the safe operation of the Generating Plant. As a minimum this shall include:

- Turbine overspeed protection

- Bearing oil level monitoring

- Bearing temperature monitoring

- Governor system oil level monitoring

- Governor system oil pressure monitoring

- Cooling water circulation monitoring

        - Gearbox

The gearbox shall be designed and installed by the contractor to suit the individual requirements of each turbine design and running conditions.

        - Generator

The generator shall be a synchronous generator with a static or brushless excitation system.

The generator and bearings shall be designed to withstand runaway speed of the turbine for the time required for the controlled closing of the main inlet valve.

The generator and excitation system shall be provided with sufficient monitoring and protection devices for the safe operation of the Generating Plant. As a minimum this shall include:

- Stator temperature monitoring

- Bearing oil level monitoring

- Bearing temperature monitoring

- Cooling water circulation monitoring

- Overcurrent protection (stator and rotor)

- Earth fault protection (stator and rotor).

- Under and over voltage protection

- Under and over frequency protection

- Reverse Power protection

- Generator differential protection

        - Cooling system

Where possible, air cooling of the generator and bearings is preferred.

Where water cooling is necessary, the design must include means to ensure there is no possibility of contamination of the discharged cooling water. The tender shall provide information on the design methods employed.

        - Flowmeter

The flowmeter shall be purchased by the contractor from a flowmeter supplier and installed by the contractor.

The flowmeter shall be of the full bore flanged electromagnetic induction type to be installed in a pipeline the same diameter as the turbine inlet pipe.

The flowmeter shall be installed in the hydropower building and shall therefore comply with IP68 requirements.

The accuracy of the flowmeter shall equal or better that specified in the applicable Rand Water specification.

The flowmeters shall be supplied, calibrated, tested and delivered with two sets of calibration certificates, installation, and service and maintenance manuals for each meter. The meters shall be flanged and the quote shall include for locally manufactured carbon steel mating plate flanges, bolts and nuts. An electrical isolation kit shall be supplied with each meter. Calibration and testing shall be carried out as stipulated. The Contractor shall guarantee each of the material items against defects in manufacture and errors or omissions in assembly, calibration and inspection.

The flowmeter shall be able to operate from a 24 VDC power supply. The power supply shall be supplied with the flowmeter. The power supply shall operate from a 231 VAC single phase supply. The basic accuracy and function of the meter shall not be effected by voltage variations of 15% of the nominal supply value. The electronic converter shall be clearly marked with the power supply requirements.

It shall be possible to communicate with the PLC in order to monitor the flow rate and the status of the flowmeter as defined in the applicable Rand Water specification.

General specification:

        - Each meter shall be of the flanged type.

        - The meters shall be suitable for measuring the flow of potable water normally at a temperature between 10C and 25C and has a conductivity within the range 20 to 150 mS/m.

        - The specific design criteria of internal diameter, power supply, working and test pressure, maximum flow rate, tag numbers and quantity shall be as stipulated in the relevant schedule.

        - The meters shall be manufactured to the same general design and basic model number. The designed maximum uncertainty factor shall be better than 0,25% of the actual flow rate for both the displayed reading and the transmitted signals. The basic accuracy of the meter shall be maintained between fluid velocities of 300 to 10 000 mm per second. The long-term stability of the electronic components and the flow head assembly shall be better than 0,05% of the flow rate at three meters per second over a period of 12 (twelve) months. There shall be no requirement to adjust the calibration factors or zero setting after testing and calibration

        - It is essential that the complete flowmeter shall be designed, manufactured, calibrated and delivered such that the original calibration parameters can easily be reconfirmed while the meter remains installed (in situ) in the service pipeline. It shall be possible to print out a confirmation calibration certificate with a full traceable accuracy to 1% of the original factory calibration certificate.

Flow tube assembly

        - Each flow tube shall be rated for a working pressure as listed in the relevant schedule. This pressure includes for the normal head and additional expected system generated surge pressures. The meter tube shall be designed to withstand at least 150% of the rated working pressure without permanent deformation.

        - The nominal bore diameter of the flow tube extensions are listed in the relevant schedule. The combined inaccuracy of the diameter and the ovality of the flow tube extensions shall be within 10 mm or 1% of the specified value whichever is the lesser. The diameter shall be determined by the average of four measurements at each end of the stainless steel tube extensions of the meter body.

        - All electrical wiring on the flow tube, sensors and coils, shall be designed to withstand a voltage impulse with respect to the steel pressure tube of 5 000 Volts for 1,5 seconds.

        - The signal cable connection shall be sealed against the ingress of moisture to IP 68 to withstand a permanent water head of at least four meters above the centre line of the flow tube consequent to installation.

        - Each flow tube shall be supplied with a separate electronic flow transmitter and screened signal cable of length as stipulated in Table 1 for magnetic coil power and sensor signals. The cable length ends shall be sealed against the ingress of water for transportation and storage purposes.

        - The environmental protection requirement for the complete flow tube shall be  IP 68  with four meters of water above the centre line of the meter tube and shall be suitable for installation in a chamber.

        - An engraved identification plate manufactured from a corrosion resistant material such as aluminum or 316 stainless steel shall be permanently fixed within 100 mm of the cable connection box. The size of the numbers/letters shall be at least 5 mm and clearly show the following information:

          - Diameter.

          - Calibration factors.

          - Serial and tag numbers.

          - The working pressure rating of the flow tube.

          - Electronic flow transmitter

        - The electronic flow transmitter (EFT) enclosure shall be suitable for the protection of the electronic components from exposure to ambient conditions associated with temperature variations from minus 10C to plus 40C with relative humidity from 20% to 95% condensing. The environmental dust factor is normally very high therefore the environmental protection for the electronic converter module shall not be less than be IP 65.

        - The EFT shall be microprocessor based, re-programmable, rugged and have an assessed meantime between failure in excess of 25 000 hours. The unit shall incorporate an illuminated digital display that is readable in low light conditions.

        - The digital display shall be capable of displaying the forward and reverse flow rate as well as the totalised values for both directions in the engineering units of M/d. The display shall have a minimum of eight digits to display the totalised flow values. The totalised values shall NOT be able to be reset at any time nor during power failures. The totalised values shall continue in increment until a maximum displayable value is reached upon which it shall reset to zero.

        - The EFT shall provide galvanically isolated dual analogue current output signals directly proportional to the flow rate for the forward and reverse flow values respectively. The signal output range shall be 4 to 20 mA, each capable of feeding into a load of 750 Ohms. Volt free pulsed contacts suitable for triggering remote forward and reverse totalised counters shall be provided. The frequency output pulses shall be in direct proportion to the respective flow rate and the contacts rated at 25 Volts and 250 mA DC

        - A data communication port shall be provided with either RS-422/485/232 serial communications or a HART interface that can be permanently connected to a local IO device or computer. Software required to access the flow rate, totalised values both forward and reverse, alarm and status information from the EFT shall be included for the portable programmer. The communication protocol shall be made available to Rand Water for RTU and telemetry interfacing.

Portable Programmer

        - The parameters associated with physical constants, flow rate, integration period and output signals shall all be set within the memory by the use of a removable portable programmer. The programmer shall incorporate a user-selected access code to prevent unauthorised changes to the programmable variables. The programmer shall be easily connected to the EFT via a plug- in connector for the upload and download of parameters to and from the EFT.

Detail requirements are given in the applicable Rand Water specification listed in Chapter 2 of this Specification.

        - Bypass valve

Bypass valves shall be designed and installed by the contractor with reference to valve specification RW/0310/AS0460 Rev 3.

      - Hartebeeshoek Reservoir

        - Scope

This Schedule sets out the design, manufacture, supply, delivery and installation requirements for hydro-mechanical infrastructure including but not limited to.

- Inlet Valve

- Outlet Valve

- Flow straightener

- Turbine

- Gearbox

- Generator

- Cooling system

- Bypass Valve

        - Inlet valve

Each turbine shall be provided with a main inlet valve capable of closing without an external power source under maximum flow.

The rate of closure of the main inlet valve shall be controlled so as to limit the transient pressures in the pipeline within the maximum pressure limits given in Part 4: Site Information.

The main inlet valve shall be a double flanged and capable of use as a termination valve when the turbine is removed.

The valve shall include auxiliary contacts to show the current position of the valve and provide for future remote indication of the valve position.

The turbine contractor shall ensure that the supplied equipment is installed correctly and datum levels for the equipment is correct.

The mating surfaces between the turbine and the pipe shall be identical in dimension and profile and no abrupt dimension changes shall be accepted.

Take offs for the cooling water turbine shall be from this pipe.

        - Outlet valve

Each turbine shall be provided with an outlet valve capable of closing without an external power source under maximum flow. The outlet valve shall be capable of isolating the turbine for dismantling.

The valve shall be manually operated and designed to open and close under balance, no flow conditions.

The discharge outlet valve shall be a double flanged and capable of use as a termination valve when the turbine is removed.

The valve shall include auxiliary contacts to show the current position of the valve and provide for future remote indication of the valve position.

        - Flow straightener

The flow straightener shall minimize turbulence to ensure optimum inlet conditions throughout the operating range of the turbine.

The flow straightener shall be designed, supplied and installed by the turbine contractor in the inlet and intermediate pipework.

The turbine contractor shall ensure that the supplied equipment is installed correctly and datum levels for the equipment are correct.

The turbine contractor shall supply a 100 mm drain point with a 100 mm sluice drain valve. The drainpipe shall be at the bottom of the pipe and the valve shall be installed vertically. The drainage water shall be piped to the sump.

        - Turbine

The turbine shall be designed such that on load rejection the transient pressure in the pipeline is within the maximum pressure limits given in Part 4: Site Information. If necessary this may be achieved by the addition of a suitably sized pressure relief valves, incorporation of a flywheel or mechanical braking system.

The rate of movement of the wicket gates or needle valves shall be controlled so as to limit the transient pressures in the pipeline within the maximum pressures limits given in Site Information.

The turbine shall be designed to withstand runaway speed for the time required for the controlled closing of the main inlet valve.

All turbine parts shall have good resistance to fatigue, cavitation, erosion and corrosion. All bushing shall be of a self-lubricated type if possible.

The turbine and governing system shall be provided with sufficient monitoring and protection devices for the safe operation of the Generating Plant. As a minimum this shall include:

- Turbine overspeed protection

- Bearing oil level monitoring

- Bearing temperature monitoring

- Governor system oil level monitoring

- Governor system oil pressure monitoring

- Cooling water circulation monitoring

        - Gearbox

The gearbox shall be designed and installed by the contractor to suit the individual requirements of each turbine design and running conditions.

        - Generator

The generator shall be a synchronous generator with a static or brushless excitation system.

The generator and bearings shall be designed to withstand runaway speed of the turbine for the time required for the controlled closing of the main inlet valve.

The generator and excitation system shall be provided with sufficient monitoring and protection devices for the safe operation of the Generating Plant. As a minimum this shall include:

- Stator temperature monitoring

- Bearing oil level monitoring

- Bearing temperature monitoring

- Cooling water circulation monitoring

- Overcurrent protection (stator and rotor)

- Earth fault protection (stator and rotor).

- Under and over voltage protection

- Under and over frequency protection

- Reverse Power protection

- Generator differential protection

        - Cooling system

Where possible, air cooling of the generator and bearings is preferred.

Where water cooling is necessary, the design must include means to ensure there is no possibility of contamination of the discharged cooling water. The tender shall provide information on the design methods employed.

        - Flowmeter

The flowmeter shall be purchased by the contractor from a flowmeter supplier and installed by the contractor.

The flowmeter shall be of the full bore flanged electromagnetic induction type to be installed in a pipeline the same diameter as the turbine inlet pipe.

The flowmeter shall be installed in the hydropower building and shall therefore comply with IP68 requirements.

The accuracy of the flowmeter shall equal or better that specified in the applicable Rand Water specification.

The flowmeters shall be supplied, calibrated, tested and delivered with two sets of calibration certificates, installation, and service and maintenance manuals for each meter. The meters shall be flanged and the quote shall include for locally manufactured carbon steel mating plate flanges, bolts and nuts. An electrical isolation kit shall be supplied with each meter. Calibration and testing shall be carried out as stipulated. The Contractor shall guarantee each of the material items against defects in manufacture and errors or omissions in assembly, calibration and inspection.

The flowmeter shall be able to operate from a 24 VDC power supply. The power supply shall be supplied with the flowmeter. The power supply shall operate from a 231 VAC single phase supply. The basic accuracy and function of the meter shall not be effected by voltage variations of 15% of the nominal supply value. The electronic converter shall be clearly marked with the power supply requirements.

It shall be possible to communicate with the PLC in order to monitor the flow rate and the status of the flowmeter as defined in the applicable Rand Water specification.

General specification:

        - Each meter shall be of the flanged type.

        - The meters shall be suitable for measuring the flow of potable water normally at a temperature between 10C and 25C and has a conductivity within the range 20 to 150 mS/m.

        - The specific design criteria of internal diameter, power supply, working and test pressure, maximum flow rate, tag numbers and quantity shall be as stipulated in the relevant schedule.

        - The meters shall be manufactured to the same general design and basic model number. The designed maximum uncertainty factor shall be better than 0,25% of the actual flow rate for both the displayed reading and the transmitted signals. The basic accuracy of the meter shall be maintained between fluid velocities of 300 to 10 000 mm per second. The long-term stability of the electronic components and the flow head assembly shall be better than 0,05% of the flow rate at three meters per second over a period of 12 (twelve) months. There shall be no requirement to adjust the calibration factors or zero setting after testing and calibration

        - It is essential that the complete flowmeter shall be designed, manufactured, calibrated and delivered such that the original calibration parameters can easily be reconfirmed while the meter remains installed (in situ) in the service pipeline. It shall be possible to print out a confirmation calibration certificate with a full traceable accuracy to 1% of the original factory calibration certificate.

Flow tube assembly

        - Each flow tube shall be rated for a working pressure as listed in the relevant schedule. This pressure includes for the normal head and additional expected system generated surge pressures. The meter tube shall be designed to withstand at least 150% of the rated working pressure without permanent deformation.

        - The nominal bore diameter of the flow tube extensions are listed in the relevant schedule. The combined inaccuracy of the diameter and the ovality of the flow tube extensions shall be within 10 mm or 1% of the specified value whichever is the lesser. The diameter shall be determined by the average of four measurements at each end of the stainless steel tube extensions of the meter body.

        - All electrical wiring on the flow tube, sensors and coils, shall be designed to withstand a voltage impulse with respect to the steel pressure tube of 5 000 Volts for 1,5 seconds.

        - The signal cable connection shall be sealed against the ingress of moisture to IP 68 to withstand a permanent water head of at least four meters above the centre line of the flow tube consequent to installation.

        - Each flow tube shall be supplied with a separate electronic flow transmitter and screened signal cable of length as stipulated in Table 1 for magnetic coil power and sensor signals. The cable length ends shall be sealed against the ingress of water for transportation and storage purposes.

        - The environmental protection requirement for the complete flow tube shall be  IP 68  with four meters of water above the centre line of the meter tube and shall be suitable for installation in a chamber.

        - An engraved identification plate manufactured from a corrosion resistant material such as aluminum or 316 stainless steel shall be permanently fixed within 100 mm of the cable connection box. The size of the numbers/letters shall be at least 5 mm and clearly show the following information:

          - Diameter.

          - Calibration factors.

          - Serial and tag numbers.

          - The working pressure rating of the flow tube.

          - Electronic flow transmitter

        - The electronic flow transmitter (EFT) enclosure shall be suitable for the protection of the electronic components from exposure to ambient conditions associated with temperature variations from minus 10C to plus 40C with relative humidity from 20% to 95% condensing. The environmental dust factor is normally very high therefore the environmental protection for the electronic converter module shall not be less than be IP 65.

        - The EFT shall be microprocessor based, re-programmable, rugged and have an assessed meantime between failure in excess of 25 000 hours. The unit shall incorporate an illuminated digital display that is readable in low light conditions.

        - The digital display shall be capable of displaying the forward and reverse flow rate as well as the totalised values for both directions in the engineering units of M/d. The display shall have a minimum of eight digits to display the totalised flow values. The totalised values shall NOT be able to be reset at any time nor during power failures. The totalised values shall continue in increment until a maximum displayable value is reached upon which it shall reset to zero.

        - The EFT shall provide galvanically isolated dual analogue current output signals directly proportional to the flow rate for the forward and reverse flow values respectively. The signal output range shall be 4 to 20 mA, each capable of feeding into a load of 750 Ohms. Volt free pulsed contacts suitable for triggering remote forward and reverse totalised counters shall be provided. The frequency output pulses shall be in direct proportion to the respective flow rate and the contacts rated at 25 Volts and 250 mA DC

        - A data communication port shall be provided with either RS-422/485/232 serial communications or a HART interface that can be permanently connected to a local IO device or computer. Software required to access the flow rate, totalised values both forward and reverse, alarm and status information from the EFT shall be included for the portable programmer. The communication protocol shall be made available to Rand Water for RTU and telemetry interfacing.

Portable Programmer

        - The parameters associated with physical constants, flow rate, integration period and output signals shall all be set within the memory by the use of a removable portable programmer. The programmer shall incorporate a user-selected access code to prevent unauthorised changes to the programmable variables. The programmer shall be easily connected to the EFT via a plug- in connector for the upload and download of parameters to and from the EFT.

Detail requirements are given in the applicable Rand Water specification listed in Chapter 2 of this Specification.

        - Bypass valve

Bypass valves shall be designed and installed by the contractor with reference to valve specification RW/0310/AS0460 Rev 3.

# Electrical Sub-Systems

      - Electrical Scope

The proposed scope of work entails the following as minimum:

- Turbine Generator

- Excitation and Synchronisation Systems for Generator

- Suitably Rated Medium Voltage Switchgear

- Suitably Rated Low Voltage Switchgear

- 110 VDC Batteries and Battery Chargers

- Low Voltage Distribution Boards

- Auxiliaries Distribution and Control Board for the turbine generator set

- Cooling Water Control Panel if required

- Valve Distribution Boards where required

- Valve and Motor Isolation Panels

- LCDs for Electrical System Reticulation Control and Monitoring

- Flood Alarm Panel if required.

- Sump Pump Control panels

- Energy Metering

- Suitably Rated Power Transformer(s)

- Suitably Rated Standby Generator

- Reticulation from the reservoir to the substations (Power Supply Utility) via underground cable and/or overhead line

- Neutral Earthing Compensator Resistive Transformer (NECRT)(s)

- Uninterruptable Power Supplies (UPS)

- Interface of electrical infrastructure to all buildings with regard room requirements, sizes, volumes, cable ducts, cable access etc

- Earthing and lightning protection for the whole system

- Fire detection, monitoring and protection where required

- Submit Electrical returnable schedule as indicated in the applicable Rand Water Standards, e.g. MV & LV switchgear, etc.

- Spares

- As built documentation

- Operating and Maintenance manuals

      - ELECTRICAL DESIGN

The Contractor shall execute the electrical design requirements as follows:

        - Preparation and compiling a design philosophy and calculations work package for main items as set out in the contractor’s Bill of Quantities, Detail Engineering Package Deliverables Document which re in line with Rand Water design criteria, Rand Water typical design drawings, Rand Water specifications, legal requirements and national and international specifications (SANS/IEC/IEEE). The contractor shall allow for integration with responsible Rand Water Design Office personnel and applicable vendors of equipment and submit a draft detail design. This design is to be presented to Rand Water before the final philosophy and design document is submitted for verification and record keeping, and before manufacturing by appointed vendors of the equipment can commence.

        - Preparation of compiling all required detail design drawings and schedules, suitable to be issued for the construction of equipment and installations as set out in the contractor’s Bill of Quantities, Detail Engineering Package Deliverables Document, in line with Rand Water design criteria, Rand Water typical design drawings, Rand Water specifications, legal requirements and national and international specifications (SANS/IEC/IEEE). The contractor shall allow for integration with responsible Rand Water Design Office personnel and applicable vendors of equipment and submit a draft detail design to be presented to Rand Water before the final philosophy and design document is submitted for verification and record keeping before manufacturing by appointed vendors of the equipment can commence.

        - Prepare a detailed drawing and schedule register indicating the drawing No., drawing title description and revision No. starting with Revision A and progressing alphabetically for subsequent submissions.

        - Select vendors and manufacturers to finalise detail designs for construction. Update typical design documents and generate new design documents where required to incorporate vendor specific details in these documents. Vendor selected equipment shall comply with Rand Water design criteria, Rand Water generic design drawings, Rand Water specifications, legal requirements and national and international specifications (SANS/IEC/IEEE).

        - Design drawings shall be in the Rand Water approved drawing templates for the drawing size. Design drawings shall incorporate the following on the template of the drawing as a minimum:

- Rand Water Drawing No which shall be different to any tender drawing No. New drawing Nos to be obtained from the Rand Water drawing office or Technical Information Centre.

- Station Name and Plant: Rand Water Bulk Water Services “XXXX XXX” Reservoir.

- Rand Water Contract No.

- Project SAP No and Network No

- Contractors Logo

- Contractors Name and Address, Company Registration No

- Contractors Contract No.

- Contractors Drawing No.

- Name and ECSA Registration No of the Company’s design engineer who will approve the drawings. The full name and ECSA No of the engineer shall be clearly legible on each drawing.

        - Submit design documents in pdf and Autocad drawing format to Rand Water for verification together with the drawing and schedule register, and a transmittal note for signature by the Rand Water project manager, clearly indicating the documents submitted. The Rand Water Lead Design Engineer shall also receive the electronic versions of the above documents at the same time as submission to the Project Manager. Any submissions without an official transmittal note and an update drawing and schedule register and the correct updated Revision number will not be accepted.

        - Receive comments or acceptance of design documents from Rand Water.

        - Update design documents as required by Rand Water.

        - Drawings or schedules accepted by Rand Water will be returned to the Rand Water Project Manager together with the Rand Water Design Review Comments Document.

        - Re submit documents updated complete with new Revision No e g B as required. Documents that are not rigorously checked and with repeat errors will be referred back in totality to the Contractor for proper checking. This will not be accepted as a delay in the project as far as design approval is concerned or for extensions of time.

        - Accepted drawings and schedules will be taken to Revision 0 status, printed in hard copy, stamped “For Construction”, signed by the Contractors ECSA registered design engineer and signed as accepted by the Rand Water Lead Engineer.

        - Revisions during construction will be taken to the next revision e g Revision 0A together with revision comments and follow the same process as in Clause 3.7.7.2.11 above.

        - A detailed CV of the Contractors’ ECSA registered design engineer together with his/her registration certificate shall be submitted at the time of tendering

        - Detail Electrical Engineering Design Package Deliverables.

The Contractor shall provide the following design deliverables as a minimum, which include reports, calculations, drawings and schedules:

|  | Medium Voltage Switchgear |
| --- | --- |
|  | Final MV Switchgear design basis, requirements and equipment specification as per SANS IEC 62271 |
|  | Power system desktop study on proprietary software to determine the switchboard short circuit and service ratings. A final report with calculation results and the actual model in the primary software shall be submitted. The ETAP software package is preferred. |
|  | Recommended protection settings for overcurrent, earth fault, over and under voltage and negative sequence current for each distribution and motor feeder |
|  | Final MV Switchgear interface with PLC and SCADA system |
|  | Final MV Switchgear interface with the Rand Water on-line billing metering and power quality systems |
|  | Final MV Switchgear Single Line Diagrams |
|  | Final MV Switchgear Parts List and Full Construction Schedule e g paint colours, specification, wiring, lamp colours etc |
|  | Final MV Switchgear General Arrangements showing all compartment, foot prints |
|  | Final MV Switchgear Schematic and Wiring Diagrams of each circuit including detailed PLC/SCADA Interface |
|  | Final MV Switchgear Individual Tier LV Door Layout |
|  | Final MV Switchgear Individual Tier LV Chassis Layout |
|  | Final MV Switchgear Individual Rear Layout showing full details of cable and current transformer chambers, gland plate, core balance current transformers, cable clamping and terminal strip arrangements |
|  | Final MV Switchgear Cross Sectional Layout showing full details of cable and current transformer, bus bar, instrument and circuit breaker chambers, including MV connections to Voltage Transformers |
|  | Final MV Switchgear Detailed Internal Arc Detection System Layout showing full details of detectors in cable and current transformer, bus bar, voltage transformer and circuit breaker chambers |
|  | Final MV Switchgear Tier dimensioned footprint showing power and control cable entry points |
|  | Final MV Switchgear Tier mounting and installation detail requirements |
|  | Final MV Switchgear Schematic and Wiring Diagrams of each circuit including detailed PLC/SCADA Interface |
|  | Final MV Switchgear detailed Connection Diagram to each protection relay with relay terminal numbers and wire numbers connected to the terminals |
|  | Final MV Switchgear Protection Relay Configuration and Settings Files including ladder logic programs for each relay in hard copy and electronic copy format |
|  | Final MV Switchgear Wiring Diagrams of each circuit breaker truck |
|  | MV Switchgear Schematic and Wiring Diagrams of bus wiring for 110 V AC and DC circuits |
|  | Final Terminal strip layouts complete with wire numbers and terminal numbers for all terminal strips |
|  | MV Switchgear Diagrams showing the final relay front panel annunciation in hard copy and electronic copy format |
|  | MV Switchgear WKS numbering details |
|  | MV Switchgear labels per circuit |
|  | Stationary Battery Charger and Battery Systems |
|  | Battery capacity sizing complete with design calculations and assumptions |
|  | Battery charger sizing and specification complete with design calculations and assumptions |
|  | Battery data sheet with technical data and performance data (constant current discharge from 1 minute to 24 hour duration) |
|  | Battery installation drawing (racks, interconnection between battery/cells etc) |
|  | Battery Charger General Arrangement drawing |
|  | Battery Charger Schematic Diagrams |
|  | Battery Charger Configuration Data |
|  | Battery Room Requirements (Maintainability, Ventilation, Operating Temperature, OHS Act requirements) |
|  | Low Voltage Switchboard |
|  | Low Voltage Load Flow analysis (Kilowatts, Kilovars, Voltage levels, Current flows) |
|  | Low Voltage Load List complete with diversities applied and spare capacity allowed |
|  | Low Voltage Short Circuit Analysis (Fault levels: Three phase symmetrical, Asymmetrical, Asymmetrical peak, Single phase to earth) |
|  | Final LV system operating basis/philosophy. (Example: dual supply, paralleling, diversity etc) |
|  | Final LV system future expansion requirements and allowance thereof |
|  | Final LV MCC/Switchgear design basis, requirements and equipment specification as per SANS IEC 61439 and 60947 |
|  | Final LV MCC/Switchgear interface with PLC and SCADA system |
|  | Final LV MCC/Switchgear Single Line Diagrams |
|  | Final LV MCC/Switchgear External General Arrangement |
|  | Final LV MCC/Switchgear Individual Tier Door Layout |
|  | Final LV MCC/Switchgear Individual Tier Chassis Layout |
|  | Final LV MCC/Switchgear Individual Rear Layout showing full details of busbar droppers and terminal strip arrangements(where applicable) |
|  | Final LV MCC/Switchgear Individual Incomer Circuit side view complete with dimensions of the Air Circuit Breaker and all busbar dimensions, together with the gland plate position and height of gland plate to the main busbar connection, where applicable. |
|  | Final LV MCC/Switchgear Busbar Layout/Specification with full details of main busbars including dimensions and all busbar droppers. Provision for maintenance of busbars to be taken into account |
|  | Final LV MCC/Switchgear Schematic and Wiring Diagrams of each circuit including detailed PLC/SCADA Interface |
|  | Standby Generator Changeover and Control Schematic diagrams |
|  | Final LV MCC/Switchgear Label Design and Nameplate in compliance with SANS 1973 |
|  | Low Voltage Distribution Boards |
|  | LV Load Flow analysis (Current flows) |
|  | LV Short Circuit Analysis (Fault levels: Three phase symmetrical, Single phase to earth) |
|  | Final LV system operating basis/philosophy. (Example: paralleling, diversity etc) |
|  | Final LV system future expansion requirements and allowance thereof |
|  | Final LV Distribution Board design basis, requirements and equipment specification as per SANS IEC 60439 and 60947 |
|  | Final LV Distribution Board General Arrangement, Exterior and Interior |
|  | Final LV Distribution Board Single Line Diagram |
|  | Final LV Distribution Board Schematic and Wiring Diagrams of each circuit |
|  | Power Transformers (Depending on make) |
|  | Final Transformer Sizing |
|  | Detailed Transformer specification |
|  | Transformer Fittings and Accessories |
|  | Detailed dimensioned General Arrangement drawings, showing plans and elevations |
|  | Detailed Transformer enclosure design including ventilation, dust deposit limitation, clearances and maintainability considerations |
|  | Details of thermal and fault protection devices, surge arrestors fault signals and wiring diagrams to terminal boxes |
|  | Forced cooling fan details, mounting arrangements, maintainability considerations |
|  | Full dimensioned details of Terminal Boxes both Low and Medium Voltage |
|  | Surge arrestors specifications, construction details and maintainability considerations |
|  | Earthing of the transformer |
|  | Nameplate details including tappings and impedance values |
|  | Specific supplier drawings are required |
|  | Fire Detection &/or protection philosophy |
|  | Adherence to Local Fire Regulations and OHS Act |
|  | Control Panel Design with zone design |
|  | Fire Detection Equipment Layout Drawings (Plan, Sections, Elevations) |
|  | Fire Detection Conduiting Layout, Cable Access Requirements (Plan, Sections, Elevations) |
|  | Interface to SCADA systems |
|  | Fire Detection Equipment Network Drawings |
|  | Fire protection equipment (refer to Mechanical Design) |
|  | Diesel Standby Generator |
|  | Load Flow analysis (Kilowatts, Current flows, Diversity) |
|  | Motor starting requirements of essential power supplies (sump pumps, valves) and diversity between standing and starting loads |
|  | Future load requirements and allowance thereof |
|  | Generator and Diesel Engine Ratings |
|  | Optimising Generator Load Rating to prevent operation outside optimal load |
|  | Generator Control Philosophy and Controller Configuration |
|  | Generator Outline and General Arrangement Drawings |
|  | Generator Bunding requirements and design, including level sensors, valves, PLC interface etc |
|  | Generator Changeover and Control Schematic diagrams |
|  | Generator Controller Configuration and Settings |
|  | Final Generator Label Design and Nameplate in compliance with SANS 1973 |
|  | Earthing and Lightning Protection |
|  | Plant earthing and lightning protection philosophy and tie-in with existing system where applicable |
|  | Soil resistivity surveys |
|  | Design using proprietary software in accordance with SANS, IEC and IEEE criteria |
|  | Development of earth mat designs including electrodes, conductors etc in accordance with the software output above and detail documentation of the designs |
|  | Compliance with step and touch potentials limitations in terms of SANS, IEC and IEEE standards where there is human presence |
|  | Detail drawings of earth mat design connection points of components of the system and test points |
|  | Lightning protection requirements, risk assessments and design in accordance with SANS and IEC standards |
|  | Detail lightning protection layout (Plan, Elevations), conductor sizing, routing and layout, tie in to building reinforcing bars where required, down conductors etc |
|  | Earthing and lightning protection layout (Plan, Elevations) |
|  | Building Small Power and Lighting System |
|  | Requirements (Socket Outlets, Water Heaters, HVAC isolators, Surface/Built in installation) |
|  | Lighting philosophy: Final design including lux calculation (Daylight switching, selection of fitting type per application) |
|  | Emergency lighting (Operational and OHS Act requirements) |
|  | Conduiting requirements (Built-in/Surface mount) |
|  | Standby power requirements (UPS and /or generator backup) |
|  | Exterior Building Lighting |
|  | Interface to data, communication, access control and fire detection systems, where applicable |
|  | Fault Level Requirements |
|  | Conductor Design and Specification |
|  | Small Power and Lighting Layout (Plan and Elevation, Interior and Exterior) |
|  | Small Power and Lighting Conduiting Layout (Plan and Elevation), Cable Access Requirements |
|  | Distribution Board Design (Rating, Fault Level, Circuits, Balancing of Loads, Sections (Raw/Standby/UPS) |
|  | Interface to HVAC systems where required |
|  | Cable reticulation and plant cabling |
|  | Normal and essential service supply points from within the existing reticulation in the plant |
|  | Service detection along anticipated cable routes |
|  | MV and LV cable reticulation design |
|  | Cable installation philosophy (ducts, trenches, sleeves, protection from other services, cable transit system, road crossings) |
|  | Interface to other services (buildings, pipes, roads, valve chambers, sewerage lines, telecommunications and data) |
|  | Cable support system philosophy and specification (Cable Basement, where applicable and plant cable support systems, including valve chambers, where required) |
|  | Cable racking system design calculations (mechanical loading) |
|  | Detailed layout of all cables at all sections of the cable support system |
|  | Requirements for ancillary equipment (Pushbutton stations, junction boxes, welding plugs, isolator panels) |
|  | Cable Design Schedules for MV and LV Power Cables (Voltage, Size, de-rating for non-standard installation conditions, Volt Drop, Fault Withstand etc) |
|  | Cable Schedules (Detailed Design with full cable termination details of each core of the cable for both power and control cables) |
|  | Cable Route Drawings for all cables |
|  | Cable Support System Drawings (Cable Basement, where applicable, Valve Chambers, Switchgear Rooms) |
|  | Reticulation Cable Access into buildings, structures (Ducts, cable racking, slots, sleeves including casting into concrete structures at right position and height during chamber construction, cable transit systems etc) |
|  | Schedule and full details of all cable transit systems in and out of the building and valve chambers |
|  | Schedule of any core drilling requirements through reinforced concrete slabs and interface with the structural engineer in this regard |
|  | Cabling sealing systems, where cables enter and exit buildings |
|  | Electrical interface with Civil, Architectural, Mechanical, Process, Pipelines and Automation Requirements (where required and applicable) |
|  | Switchgear Room Philosophy (number of rooms, separation of equipment, sizing, clearances to all walls, ceilings, doors etc) |
|  | Switchgear Room Heights and Ceiling requirements (Internal Arc, IEC 62271, arc ducting) |
|  | Switchgear Room Lighting philosophy (natural and artificial lighting, emergency lighting) |
|  | Switchgear Room HVAC philosophy (natural ventilation, A/C, emergency ventilation) |
|  | Switchgear Room Access Control (Doors, emergency exits, type of door mechanisms) |
|  | Switchgear Room Cable Ducts and Access (Cable duct requirements, Slots, sleeves, cable transit systems, water ingress control) |
|  | Switchgear Room Materials Handling Requirements (Crawl Beam) |
|  | Switchgear Room Architectural/Structural Drawings (Plan, Elevation and Sections) |
|  | Diesel Standby Generator Bay Requirements (Size, Noise Control, Exhaust Ducting, Bunding, Fuel Storage, environmental and safety requirements) |
|  | Diesel Standby Generator Bay Equipment Handling (Crawl Beam) |
|  | Diesel Standby Generator Bay Cable Ducts (Slots, sleeves, water ingress control, cable transit systems) |
|  | Diesel Standby Generator Bay Lighting (natural and artificial lighting, emergency lighting) |
|  | Diesel Standby Generator Bay Ventilation requirements (Forced/Natural ventilation) |
|  | Diesel Standby Generator Bay/Room Layout Drawings (Plan, Elevations, Sections) |
|  | Transformer Room Requirements (Sizing, Bunding, Plinth details, cable ducts, explosion separation) |
|  | Transformer Bay Cable Access (cable transit systems, final finish of transformer bay, chipped stone etc) |
|  | Transformer Bay Equipment Handling (Crawl beam etc) |
|  | Transformer Bay Lighting (natural and artificial lighting, emergency lighting) |
|  | Transformer Bay Ventilation requirements (Dry type transformers) (Forced/Natural ventilation) |
|  | Transformer Bay Layout Drawings (Plan, Elevations, Sections) |
|  | UPS and Battery Rooms Sizing |
|  | UPS and Battery Room Lighting philosophy (natural and artificial lighting, emergency lighting) |
|  | UPS and Battery Room HVAC philosophy (natural ventilation, A/C, emergency ventilation, safety requirements w r t explosive gases) |
|  | UPS and Battery Room Cable Ducts and Access (Slots, sleeves, Water ingress control, cable transit systems) |
|  | UPS and Battery Room Layout Drawings (Plan, Elevations, Sections) |
|  | Mimic positioning in Control Room |
|  | Control Room Cable Ducts and Access (Slots, sleeves, Water ingress control, cable transit systems) for mimic cables |
|  | Control Room Lighting philosophy (natural and artificial lighting, emergency lighting) |
|  | Control Room HVAC philosophy (natural ventilation, A/C, emergency ventilation) |
|  | Control Room Cable Ducts and Access (Slots, sleeves, Water ingress control, cable transit systems) for mimic cables |
|  | Control Room Layout Drawings (Plan, Elevations, Sections) |

      - CONSTRUCTION SUPERVISION

After acceptance of all designs the Contractors’ design engineer shall be responsible for supervision of the entire electrical installation during construction as follows:

        - The Contractors’ design engineer shall fulfil the duties of the electrical design engineer under Section 6 of the Construction Regulations and shall conduct design compliance inspections at all relevant milestone points in the project. At the completion of the project the design engineer shall declare the installation safe and issue a completion certificate.

        - Obtaining a proposed quality control plan from every manufacturer of equipment and in consultation with the Rand Water Lead Engineer enter witness and hold points for each construction milestone of the manufactured equipment.

        - Inform the Rand Water Lead Engineer of each construction milestone inspection required as per the quality control plan. Attend each construction milestone inspection and generate documentary evidence of the inspection in the form of a completed and signed attendance of all present at the inspection, sign off of the milestone if accepted or generate a punch list of items to be corrected, with actions required by each party and agreed completion dates, signed by the design engineer and the manufacturers’ representative. Records shall be kept of each such visit for submission in a monthly report to the Rand Water Lead Engineer.

        - Once the manufactured equipment is ready for a Factory Acceptance Test the Contractors’ design engineer shall carry out the Acceptance Test with the minimum of the following tests:

- Specifying witness and hold points on the QCP documents from each manufacturer during manufacture.

- Management of the QCP documents and witnessing at hold points, including sign off.

- Generation of defects lists and management of clearance of defects.

- Construction quality checks for compliance with the requirements of the specifications.

- Point to point wiring checks of all wiring and agreement with the schematic diagrams.

- Injection tests on current transformers where required.

- Pressure and Insulation Resistance Tests.

- Functional tests including closing, tripping and indication from all possible operational modes

- Labelling

- Protection settings, Configuration where requires and adjustments.

- Functionality of metering equipment.

- Relevant photographic evidence.

        - A signed attendance register for each day of a test shall be kept.

        - A master set of approved construction documents shall be kept by the Contractors’ design engineer and the manufacturer on which tested and completed circuits shall be marked up. Any modifications that may be required shall also be recorded on the documents, together with the date(s).

        - Once construction impacting any electrical part of the installation commences on site as follows:

- Attend site once a week or when a significant construction milestone such as lift in concrete pouring, finalisation of concrete ducts, cable racking, casting in of cable transit system boxes etc is reached. A record of progress or events witnessed shall be kept in a site diary, together with dated photographic evidence. Where site instructions are issued these shall be communicated to the Rand Water Project Manager and Lead Engineer. Compliance to the Contractors’ approved design shall be checked and any deviations recorded as a site instruction. Every calendar month the Contractors’ design engineer shall submit a concise report containing all items above to the Lead Engineer and Rand Water Project Manager.

- Attend all scheduled project and technical meetings on site.

- Once the electrical installation commences on site the as follows:

- Attend site twice or more frequently a week or when a significant construction milestone such as delivery of a distribution board etc is reached. The Contractors’ design engineer shall check that the installation on site such as cable racking, cable installation, installation of other equipment such as control panels etc proceeds in accordance with the approved design. A record of progress or events witnessed shall be kept in a site diary, together with dated photographic evidence. Where site instructions are issued these shall be communicated to the Rand Water Project Manager and Lead Engineer. Compliance to the Contractors’ approved design shall be checked and any deviations recorded as a site instruction. Every calendar month until final handover of the completed installation the Contractors’ design engineer shall submit a concise report containing all items above to the Lead Engineer and Rand Water Project Manager.

        - Once the completed installation or a logical part thereof e g a turbine set is completed the Contractors’ design engineer shall carry out the commissioning and Site Acceptance Test on the completed installation with the minimum of the following tests:

- Construction quality checks for compliance with the requirements of the specifications.

- Checking the cable installation is as per the approved design.

- Cable trench inspections.

- Inspection of cable transit points e g into valve chambers where required.

- Cable supports are as per specification or best practice.

- Point to point wiring checks of all wiring between connected equipment and agreement with the schematic diagrams and cable schedules.

- Pressure and Insulation tests.

- Functional tests including closing, tripping and indication from all possible operational modes.

- Labelling especially cable numbers

- Configuration and protection settings and adjustments.

- Functionality of metering.

- Relevant photographic evidence.

- A signed attendance register for each day of the Test shall be kept.

        - A master set of approved construction documents shall be kept by the Contractors’ design engineer and the manufacturer on which tested and completed circuits shall be marked up. Any modifications that may be required shall also be recorded on the documents, together with the date(s). Close out of the implemented modifications shall also be recorded on the documents complete with dates.

        - A commissioning report of the completed installation addressing all the results of testing and checking in Clause 3.7.7.3.8 shall be submitted to the Rand Water Project Manager and Lead Engineer.

      - MEDIUM VOLTAGE SWITCHGEAR

        - All switchboards shall be front and rear access.

        - Control, Protection and metering designs shall be completed with reference to the Rand Water Electrical Standard Specifications.

        - Separate panels shall be provided for each type of circuit e.g. generator feeder, transformer feeder etc. Where there is provision for two generators both shall feed onto the same bus. One or more bus-section circuit breakers shall be provided to enable flexibility of operations and maintenance.

          - General requirements for medium voltage switchgear panels are as follows:

| Circuit Description | Generator Feeder | Distribution Transformer Feeder | Bus- Section | Auxiliary Transformer Feeder |
| --- | --- | --- | --- | --- |
| Busbars |  |  |  |  |
| Rated normal current Ir (A) | TBA | TBA | TBA | TBA |
| Rated short-time withstand current Ik (kA) | TBA | TBA | TBA | TBA |
| Rated peak withstand current Ip (kA) | TBA | TBA | TBA | TBA |
| Rated duration of short circuit tk (secs) | TBA | TBA | TBA | TBA |
| Power Frequency Voltage Withstand (kV) | TBA | TBA | TBA | TBA |
| Impulse Withstand Voltage (kV) | TBA | TBA | TBA | TBA |
| Impulse Rating (kV) | TBA | TBA | TBA | TBA |
| Internal Arc Classification | IAC Classified | IAC Classified | IAC Classified | IAC Classified |
| Internal Arc Withstand (kA) | TBA | TBA | TBA | TBA |
| Internal Arc Withstand Time (secs) | 0.50 | 0.50 | 0.50 | 0.50 |
| Accessibility | AFLR | AFLR | AFLR | AFLR |
| Level of Service Continuity | LSC2A | LSC2A | LSC2A | LSC2A |
| Partition Class | PM | PM | PM | PM |
| Circuit Rating (A) | TBA | TBA | TBA | TBA |
| Circuit Breaker Switching Medium | TBA | TBA | TBA | TBA |
| Circuit Breaker Rated normal current Ir (A) | TBA | TBA | TBA | TBA |
| Cicruit Breaker Rated short-time withstand current Ik (kA) | TBA | TBA | TBA | TBA |
| Circuit Breaker Rated peak withstand current Ip | TBA | TBA | TBA | TBA |

| Circuit Description | Generator Feeder | Distribution Transformer Feeder | Bus- Section | Transformer Feeder |
| --- | --- | --- | --- | --- |
| (kA) |  |  |  |  |
| Cicruit Breaker Rated duration of short circuit tk (kA) | TBA | TBA | TBA | TBA |
| Circuit Breaker Configuration | Withdrawable | Withdrawable | Withdrawable | Withdrawable |
| Circuit Breaker Tripping | Shunt Trip | Shunt Trip | Shunt Trip | Shunt Trip |
| Circuit Breaker 110 V dc Undervoltage Release | Yes | Yes | Yes | Yes |
| Circuit Breaker Closing | Solenoid | Solenoid | Solenoid | Solenoid |
| Tripping, Closing, Undervoltage, indication operating voltage | 110 V dc | 110 V dc | 110 V dc | 110 V dc |
| Racked In Service Position Signal | Yes | Yes | Yes | Yes |
| Racked In Test Position Signal | Yes | Yes | Yes | Yes |
| Breaker Latched Signal | Yes | Yes | Yes | Yes |
| Protection C T Ratio | XXX/1 | XXX/1 | - | XXX/1 |
| Protection C T Rating | XX VA | XX VA | - | XX VA |
| Protection C T | 5P20 rating | 5P20 rating | - | 5P20 rating |
| Protection C T Quantity | Three | Three | - | Three |
| Protection C T Residual Connection | Yes | Yes | - | Yes |
| Protection Test Blocks | Yes | Yes | - | Yes |
| Differential Protection C T | Class X | Class X | - | - |
| Differential Protection Test Blocks | Yes | Yes | - | - |
| Metering C T Ratio | XXX/1 | XXX/1 | - | XXX/1 |
| Metering C T | Class 0.5 | Class 0.5 | - | Class 0.5 |
| Metering C T Rating | 10 VA | 10 VA | - | 10 VA |
| Metering C T Quantity | Two | Two | - | Two |
| Metering Test Blocks | Yes | Yes | - | Yes |
| Power Quality Monitor to NRS 048 |  | Yes |  |  |

| Circuit Description | Generator Feeder | Distribution Transformer Feeder | Bus- Section | Transformer Feeder |
| --- | --- | --- | --- | --- |
| Core Balance C T | Yes | Yes | - | Yes |
| Core Balance C T Ratio | XXX/1 | XXX/1 | - | XXX/1 |
| Core Balance C T Rating | XX VA | XX VA | - | XX VA |
| Voltage Transformer | XX kV/110 V ac | - | - | - |
| Voltage Transformer Vector Group | Yyn | - | - | - |
| Voltage Transformer Class | Class 0.5 | - | - | - |
| Voltage Transformer Rating | TBA | - | - | - |
| Voltage Transformer Connections | Cable | - | - | - |
| Voltage Transformer Configuration | Withdrawable | - | - | - |
| Protection Relay 1 | Generator | Overcurrent/Earth Fault | - | Overcurrent/E arth Fault |
| Protection Relay 2 | Differential | Transformer Differential | - | - |
| Internal Arc Protection | Yes | Yes | - | - |
| Differential Protection | Yes | Yes | - | - |
| Synchronising | Yes | Yes | - | - |
| Metering | Combination Metering | Billing Class Elster Kent | - | Combination Metering |
| Metering Interface | No | GPRS | No | No |
| Open Indication | Yes | Yes | Yes | Yes |
| Closed Indication | Yes | Yes | Yes | Yes |
| Tripped Indication | Yes | Yes | Yes | Yes |
| Interlocks Correct/Ready to Close Indication | Yes | Yes | Yes | Yes |
| Indication Lamp Type | Cluster LED | Cluster LED | Cluster LED | Cluster LED |
| Indication Lamp Voltage | 110V dc | 110V dc | 110V dc | 110V dc |

| Circuit Description | Generator Feeder | Distribution Transformer Feeder | Bus- Section | Transformer Feeder |
| --- | --- | --- | --- | --- |
| Maintenance/Service Selector switch | Yes | Yes | Yes | Yes |
| Emergency Stop | Yes | Yes | Yes | Yes |
| 110 V dc Inputs to Remote PLC |  |  |  |  |
| Output Relay Signals from PLC to switch 110 V dc |  |  |  |  |
| Interface to SCADA | Ethernet | Ethernet | Ethernet | Ethernet |

        - The structural stability of the switch room (floor,walls and roof) shall be designed for a catastrophic failure of the switchgear as a result of any venting of gases due to a full prospective short circuit occurring on any circuit of the switchboard. Pressure relief measures shall be built into the room with no compromise on safety of personnel or an arc venting duct installed

        - The clearances around each switchboard shall be as follows:

- Rear- Not less than 1500 mm but not exceeding 1800 mm at every point of the switch room.

- Front- Double the depth of the switchboard at every point along the length of the switchboard to allow for the withdrawal and handling of circuit breakers.

- Sides- 2500 mm on each side of the switchboard.

        - Heating, Ventilation and Air Conditioning (Part. 2 of IEC 62271-1)

- The ambient air temperature shall not exceed 35°C and its average value, measured over 24 hours, must not exceed 30°C.  The minimum ambient air temperature will be -5°C

- The average relative humidity measured over 24 hours must not exceed 95%; average water vapour pressure measured over 24 hours must not exceed 2,2 kPa; average relative humidity over one month must not exceed 90% and average water vapour pressure measured over one month must not exceed 1,8 kPa.

        - The correct positioning of control, communications and power cable entries to the switchgear from either a cable basement or cable duct below shall be specifically determined. The switchgear placement taking into account the switchgear clearances required in Rand Water Standard Specification..

        - Purpose formed cable ducts or an entry into a cable basement shall be provided below the switchgear to meet amongst other the following requirements:

- The depth of the cable duct shall be such that cables below the switchgear shall be installed vertically against the cable duct wall.

- The minimum bending radii requirement for all cables installed in the cable duct shall be met.

- Suitable chamfering of 90° bends in the cable ducts shall be provided to cater for cable bending radii.

- The separation requirements to any communication cables to prevent EMC interference shall be complied with.

- Wherever possible the cable duct width shall be such that no additional supports for the switchgear straddling the duct shall be required. If additional support is required it shall be horizontal across the duct and not to the duct floor.

        - Where required the switchgear supplier and installer will install custom manufactured frames for the mounting of switchgear tiers. Where frames are to be cast into the floor this shall be co-ordinated with the casting of concrete and shall meet the switchgear suppliers’ requirements and specification. The required tolerances in levels by the switchgear supplier in all directions shall be met. A certificate with specific level measurements and tolerances shall be signed off by the switchgear supplier.

        - The switchgear rooms shall be equipped with a double door with sufficient dimensions (width and especially height) to enable the switchgear to be installed into the room. Particular attention shall be paid to the landing area outside the doors, preferably a concrete base to enable the switchgear tier sections to be placed comfortably and safely for further installation into the switchgear room.

        - Each switchgear room shall be provided with two doors preferably at opposite ends of the room for access by operating and maintenance personnel and providing an escape route out of the room. The doors shall be provided with panic bar ironmongery to facilitate the easy egress from the room.

        - The switchgear installer shall install one lockable steel enclosure correctly dimensioned for the secure and lockable storage of one spare circuit breaker truck which shall be supplied for each switchboard. In the same vicinity the switchgear installer will install a wall mounted cabinet of approximately 1600 wide and 1600 high for any switchgear operating tools. A storage space shall be allowed for any trolley to facilitate the withdrawal and insertion of switchgear trucks

        - The roof or ceiling height of the switch room shall be minimum 3 000 from finished floor level to meet the switchgear arc venting requirements, but shall be determined by the final fault rating of the switchgear and the switchgear suppliers arc venting design including possible arc vent ducting, plasma deflectors and absorbers.

        - The contractor shall interface with the switchgear supplier for the installation of possible arc vent ducting above the switchgear and to exit ducts. The roof and wall designs shall accommodate these requirements.

        - The effect of possible solar radiation and heating on the switchgear shall be taken into account.

        - The contractor shall take measures to prevent the ingress of dust into the switchgear room.

        - No PLC panel, Battery Charger, Batteries and UPS’s shall be housed in the any medium voltage switch room.

      - TURBINE GENERATOR, EXCITATION AND SYCHRONISATION SYSTEMS

        - The generator shall be a synchronous generator with a static or brushless excitation system.

        - The generator and bearings shall be designed to withstand the runaway speed of the turbine for the time required for the controlled closing of the main inlet valve.

        - The generator shall comply with the applicable sections of the SANS/IEC 60034 standard.

        - The generator stator insulation system shall be Class F with a Class B temperature rise.

        - The generator and excitation system shall be provided with sufficient monitoring and protection devices for the safe operation of the Generating Plant.

        - As a minimum this shall include:

- Stator temperature monitoring

- Bearing oil level monitoring

- Bearing temperature monitoring

- Cooling water circulation monitoring

- Overcurrent protection (stator and rotor)

- Earth fault protection (stator and rotor).

- Under and over voltage protection

- Under and over frequency protection

- Reverse Power protection

- Generator differential protection

        - Cooling system

          - Where possible, air cooling of the generator and bearings is preferred.

          - Where water cooling is necessary, the design must include means to ensure there is no possibility of contamination of the discharged cooling water. The tender shall provide information on the design methods employed.

      - 110 V DC BATTERY CHARGERS AND STATIONARY BATTERIES

        - Battery and Charger Design Criteria

          - Battery System

- The battery system shall be sized and designed for the following worst case load profile which is in the event of a total power failure of 8 hours.

- At the start of the power failure the number of circuit breakers indicated shall be tripped within one minute of each other.

- Thereafter the standing DC load shall be supplied by the battery until 8 hours have elapsed.

- After eight hours the number of circuit breakers indicated shall be closed within one minute of each other.

- The battery system cell voltage shall not be lower than 1,75 V/cell at the end of the eight hour period.

- The maximum system DC voltage shall be 125 V DC.

- The minimum system DC voltage shall be 95 V DC.

- The following design factors shall be used in sizing the battery:

- Temperature De-Rating	1.00.

- Design Margin		1.15.

- Ageing Factor			1.25.

- The batteries shall have a 10/12 year design life when operated within the expected float charge voltage range and at 20ºC ambient temperature. Long life and high reliability are particular requirements.

- Valve regulated lead acid batteries shall have a Standard Flammability rating of FV1 as per IEC 60707.

- The continuous and momentary DC loads per switchboard shall be determined once the switchgear design has been finalised.

          - Battery Charger

- The Ampere Hours removed from the battery in the load calculated shall be used in sizing the battery charger.

- A recharge factor of 1,15 shall be used.

- The battery charger shall recharge the battery in 8 hours.

- A design margin of 10% shall be used in the sizing calculations.

- Temperature and altitude correction shall be taken into account in determining the battery charger rating.

- The charger output current shall not exceed 25% of the final battery rated Ampere Hour capacity.

- The continuous available current limit rating of the battery charger may be taken into account in sizing the battery charger, where the calculated rating required exceeds the next lowest standard rating, e g a with a calculated rating of 26,5 A a 25 A battery charger with a 110% continuous current limit can be used as its output will be 27,5 A.

          - The battery charger and battery shall comply with Rand Water standard specification RC   01475- STANDARD FOR 110VDC AUXILIARY AND BATTERY CHARGING SYSTEMS

      - Power Transformer

        - The Power Transformer to supply power to the supply authority shall comply to the following requirements:

| Requirement | Power Transformer |
| --- | --- |
| Rating (MVA) | 20% above calculated max load rating |
| Primary Voltage (kV) | As per Generator Voltage |
| Secondary Voltage (kV) | As per distribution system |
| Vector Group | TBA |
| Insulation Grading | Uniform |
| Insulation Class | F |
| Conductors | Copper |
| Power frequency withstand voltages (kV) | As per SANS |
| Breakdown insulation level (kV) | As per SANS |
| Cooling | ONAN |
| Impedance voltage | Standard |
| Type | Free breathing |
| Tappings (Off Load) | ± 5%, ±2,5%, 0 |
| Tapped winding | Primary |
| Conservator | Yes |
| Dehydrating breather | Yes |
| Gas and oil actuated relay | Yes |
| On line gas analyser | Yes |
| On line gas analyser type | TBA |
| On line gas analyser data interface | TBA |
| Indicating thermometer with trip and alarm relay | Yes |
| Thermometer pocket | Yes |
| Skid underbase | Yes |
| Drain valve | Yes |
| Power cables- Primary | Type A, XLPE, TBA |
| Power cables- Secondary | Type A, XLPE, TBA |
| Primary Neutral Current Transformer for Backup earth fault protection | TBA |
| Primary Current Transformers for Restricted Earth Fault Protection | TBA |
| Primary Current Transformers for Differential Protection | TBA |
| Secondary Neutral Current Transformer for Backup earth fault protection | TBA |
| Secondary Current Transformers for Restricted Earth Fault Protection | TBA |
| Secondary Current Transformers for Differential Protection | TBA |

      - Auxiliaries Power Transformer (If required)

        - One auxiliary transformer is required to supply the 400 Volt DB which in turn supplies the building and plant auxiliaries.

        - Transformer requirements:

| Requirement | Auxiliary Transformer |
| --- | --- |
| Rating (kVA) | TBA |
| Primary Voltage (kV) | As per Generator Voltage |
| Secondary Voltage (V) | 400V, RWBN |
| Vector Group | Dyn 11 |
| Insulation Grading | Uniform |
| Insulation Class | F |
| Conductors | Copper |
| Power frequency withstand voltages (kV) | As per SANS |
| Breakdown insulation level (kV) | As per SANS |
| Cooling | ONAN |
| Impedance voltage | Standard |
| Type | Sealed category 1 |
| Tappings (Off Load) | ± 5%, ±2,5%, 0 |
| Tapped winding | Primary |
| Conservator | N/A |
| Dehydrating breather | N/A |
| Gas and oil actuated relay | N/A |
| Indicating thermometer with trip and alarm relay | Yes |
| Thermometer pocket | Yes |
| Skid underbase | Yes |
| Drain valve | Yes |
| Power cables- Primary | TBA |
| Power cables- Secondary | TBA |
| Neutral Current Transformer for Backup earth fault protection | TBA |
| Current Transformers for Restricted Earth Fault Protection | Not Required |

      - Revenue metering

        - The Metering accuracy shall meet the Eskom or local municipality requirements.

        - Energy meters shall meet the functionality required from Time of Use meters as far as tariff structures, seasonal variations etc and shall be certified for billing purposes.

        - Metering data shall be transmitted in a wireless format, to the required data transfer rate, to a metering database meeting all Eskom’s and local municipality requirements. Rand Water shall also have full access to all data on a web based data server currently administered by Power Meter Technics.

        - The CT/VT unit shall be pole mounted.

        - The VT primary and secondary fuses shall be accessible for maintenance purposes. The CT rating shall not be less than 10 VA.

        - The CT secondary current shall be 1 A.

        - Main circuit isolators on either side of the CT/VT unit shall be provided.

      - Surge arrestors

        - Surge arrestors shall be installed to protect transformers, instrument transformers and downstream equipment.

        - Surge arrestors shall be suitably rated for maximum continuous overvoltage, discharge current, maximum residual voltage and minimum creepage distances.

        - Heavy duty station class arrestors are preferred. Ground line disconnectors shall be supplied on all surge arrestor installations.

        - Critical surge arrestors shall be fitted with a surge counter with an interface to the SCADA system.

      - NECRT

        - The requirement for a NECRT on the generator bus or on the Distribution system shall be considered by the Contractor.

        - Type

          - The units shall be oil filled, naturally cooled, free breathing, zig-zag connected three phase 50 Hz NEC combined with current limitation resistor NER.

          - The windings shall be of high conductivity copper.

          - The core and winding assembly shall be correctly located on the tank bottom and adequately braced.

          - The current limiting resistor shall be suitably insulated to withstand full line voltage and securely located in the same oil filled tank as the NEC.

          - The resistor shall be of stainless steel (or similar) material.

          - Where the resistor is built from a large number of series connected grids, the welding method of connecting these grids is preferred.

          - Electrical stresses on resistor insulation shall be defined, ie: no construction metal pieces may be at "floating" potential.

          - To prevent entry of gas developed during normal NER operation into gas and oil operated relay, a suitable gas trap shall be provided above the NER only. This trap shall be vented to the conservator by-passing the relay. Reaction of the relay to the NEC winding faults may not be affected.

        - Main terminals

          - The NER to earth connection shall be brought out of the tank through an outdoor bushing complying with SANS 833.

          - The supply terminals shall be brought out through bushings into an air filled cable box having a removable gland plate suitable for XLPE cable heatshrink termination

        - Current transformers

          - The NEC/NER shall be fitted with two 300/1 ratio current transformers in the neutral connection on the earthed end.

          - Both CT's shall be Class X 15 VA. Their knee point voltage shall be 30 volts and they shall be compatible with the protection relays installed on the MV switchgear.

          - The NEC/NER shall be fitted with:

- Oil conservator with oil level indicator;

- Gas and oil actuated relay;

- Dehydrating breather;

- Dial type top oil thermometer having alarm and trip contacts;

- Check thermometer pocket;

- Rating and diagram plate;

- Drain valves;

- Skid underbase;

- Tank earth stud.

        - Painting

          - Painting to coastal area standards. Auxiliary cable box

          - An auxiliary cable box with terminals and removable gland plate for PVC cable compression glands is to be fitted for all small wiring on the NEC/NER.

        - Ratings

          - It is required that the NEC/NER combination shall limit earth fault currents to the order of 300 to 355 amps taking into account manufacturing tolerances and system parameters.

          - The maximum continuous neutral current shall be taken as 15 amperes.

        - Overfluxing

          - The NEC/NER must be suitable of withstanding 1,15 times the relevant system nominal voltage on the main transformer terminals and the NEC/NER shall be designed to operate continuously at this level.

        - Short-Time Currents

          - The NEC and NER shall be capable of withstanding 355 amps in the neutral connection and 118 amps in each phase of the NEC for 10 seconds without exceeding the temperature rise limits below

        - Temperature rise limits

          - The temperature rise limits shall not exceed: Top oil temperature rise resulting from the magnetisation losses plus the losses due to the maximum continuous neutral current shall be 55°C.Temperature rise of the metallic resistor resulting from the load described in 5.8.1 above shall be 60°C.Average NEC winding temperature rise resulting from the load described in 5.8.1 above shall be 65°C.

        - Distribution Circuit Breaker

          - An outgoing distribution circuit breaker shall be supplied and meet national standards.

          - The breaker shall be fitted with electrical closing, tripping and no-volt release features. Synchronising facilities and a protection scheme for the breaker shall be provided.

      - Earthing and Lightning Protection

        - A specialist earthing contractor shall design, supply and install a lightning protection  system and earth mat comprising of a trenched/rod system for the Resevour Installation and all ancillary structures and equipment supplied under this contract.

        - The installation shall meet the requirements of SANS 10313, SANS 62305 Parts 1 to 4 and SANS 62561 Parts 1 to 7 and where applicable IEEE 80.

        - The Contractor shall ensure that all electrical items including but not limited to MV and 400V switchgear, transformers, auxiliary panels, flood alarm panels, valve isolating panels, PLC panels, cable racking, generators, motors and ancillary equipment etc, are adequately earthed. All electrical equipment shall be earthed utilizing black insulated copper wire or copper coated steel conductor. No bare copper earth wire will be accepted

        - Earthing

          - Earthing shall generally be done in accordance to SANS 10142-1, SANS 10199, SANS 10292 and SANS 1063 and where applicable IEEE 80.

          - The contractor shall utilise a recognised proprietary software package to design the earthing and lightning protection systems to SANS, IEC and where applicable IEEE standards, also based on soil resistivity data. Attention shall also be given to allowable step and touch potentials as per SANS and IEC standards. The output of design calculations and its traceability to the final designs shall be provided in the design deliverables and the final documentation.

          - All electrical equipment shall be earthed utilizing anti-theft type copper cladded steel wire. No bare copper earth wire will be accepted, except for the underground earthing system.

        - Lightning Protection

          - The installation shall be done in accordance with SANS 10313, SANS 62305 Parts 1 to 4, SANS 10199, SANS 1063 and SANS 62561 Parts 1 to 7 and.

          - A specialist service provider registered with ELPA (Earthing And Lightning Protection Association) shall design, supply and install a lightning protection system for all buildings and structures.

          - The designs shall be provided in PDF and Auto Cad formats on Rand Water drawing templates to be approved by Rand Water prior to construction.

          - The Soil Resistivity testing shall be done at every installation where a lightning protection system shall be installed and these results shall be used to base the designs on. Provide for complete reports on findings.

          - The contractor shall allow for a complete and full installation of the lightning protection including design, supply, delivery, installing in terms of the standards and strapping and supporting as necessary.

          - The specialist shall supply test certificates and documentation verifying the installation and readings obtained for the lightning protection.

      - LV Switchgear

        - A free standing 400VAC three phase and neutral switchboard shall be supplied. The Switchgear shall have the following sections:

  - Normal

  - Emergency

  - UPS.

The requirements are:

| 400V SWITCHGEAR |  |  |
| --- | --- | --- |
| POWER SUPPLY TO LV DISTRIBUTION BOARD |  |  |
| Supply details: | 400 | V ac |
| Supply voltage variations | -15% and +10% |  |
| Supply Frequency Variations | ± 2.5 | % |
| Total Harmonic Content | < 3% up to 25th harmonic |  |
| Supply Transformers (three off) | TBA kVA |  |
| Ratio | 11/0.4 kV |  |
| Impedance | TBA% |  |
| Vector Group | Dyn11 |  |
| CURRENT RATINGS |  |  |
| Rated Operational Current In | TBA | A continuous |
| Complete Busbar System Derating Factor | 0.85 |  |
| Short Circuit Rating Icw | 50 | kA for 1 second |
| Operating configuration | The short circuit rating of the switchboard shall be suitable for paralleling of two incoming transformers even though this will not be the normal operating mode |  |
| Rated Peak Withstand Ipk | TBA | kA |
| Internal arc rating | TBA | kA |
| VOLTAGE RATINGS & INSULATION SYSTEM REQUIREMENTS |  |  |
| Rated voltage Ue | 400 | V |
| Insulation Ui | 1 000 | V |
| Impulse Withstand Level | 6 | kV peak |
| BUSBAR SYSTEM |  |  |
| Busbars: |  |  |
| Busbar Material | High Conductivity Copper |  |
| Busbar Nominal Rating | TBA | A |
| Rated Diversity Factor | 1 |  |
| Busbar Maximum Current Density | 1,55 | A/mm2 |
| Neutral Busbar Rating | >=500 | A |
| System of Earthing | TNCS |  |
| TEMPERATURE RISE SPECIFICATION |  |  |
| Assembly Temperature Rise Limit |  | °C above ……°C |
| Busbar Support Temperature Rise |  | °C above ……°C |
| Maximum Busbar Temperature Rise | 50 | °C above 40°C |
| OTHER |  |  |
| Place of Installation | Indoor Closed Room |  |
| Form | 2b & 3b |  |
| IP rating | 55 |  |
| Type of access: | Front and Rear |  |
| Type of entry: | Bottom Cable Entry |  |
| Type of mounting: | Solid floor |  |
| Enclosure materials: | Mild Steel |  |
| Door Thickness: | 1,6 | mm minimum |
| Chassis Plate Thickness: | 1,6 | mm minimum |
| Finish | Powder Coated Structured |  |
| Colour: | B26 to SANS 1091 | Normal Section |
|  | A11 to SANS 1091 | Emergency Section |
|  | F01 to SANS 1091 | UPS Distribution |
|  | G12 to SANS 1091 | 110 V DC Distribution |
| Certification required | Approved performance to SANS 1973-1 |  |
| Special environmental conditions: | None |  |
| Humidity | 80 | % |
| Maximum Ambient Temperature | 40 | °C |
| Minimum Ambient Temperature | -5 | °C |
| Altitude | 1590 m | aMSL |
| Rapid temperature variations | No |  |
| Pollution level: | Dust |  |
| Exposure to magnetic fields | Site Specific |  |
| Direct radiation from the sun/furnaces | No |  |
| Attacks by fungi /Small creatures | Yes |  |
| Fire / Explosive environment | No |  |
| EMC environmental requirements | No |  |
| Fixed DISTRIBUTION BOARDBs | Yes |  |
| SCPD / Motor starter coordination | Type II Coordination |  |
| EQUIPMENT SPECIFICATIONS: |  |  |
| INCOMER AND BUS-SECTION MOULDED CASE CIRCUIT BREAKERS: |  |  |
| RATINGS AND CONFIGURATION |  |  |
| Rated Operational Voltage (Ue) | 690 V |  |
| Rated Insulation Voltage (Ui) | 800 V |  |
| Rated Impulse Withstand Voltage (Ue) | 12 kV |  |
| Rated Uninterrupted Current (Iu) at 40˚C | TBA A |  |
| Rated Ultimate Short Circuit Breaking Capacity (Icu) | TBA kA |  |
| Rated Service Short Circuit Breaking Capacity (Ics) | 100% of Icu |  |
| Rated Short Time Withstand Current (Icw) (1 sec) | TBA kA |  |
| Poles | Four |  |
| Neutral Pole Current Carrying Capacity (%Icu) | 100 |  |
| Mounting configuration | Horizontal Drawout |  |
| SAFETY FEATURES |  |  |
| All poles shall operate simultaneously for circuit breaker opening, closing and tripping. | Yes |  |
| MCCBs shall be actuated by a toggle or handle that clearly indicates the three positions: ON, OFF and TRIPPED. | Yes |  |
| Suitability for isolation complying with SANS/IEC 60947-2 | Yes |  |
| The operating mechanism shall be such that the toggle or handle can only be in OFF position (O) if the power contacts are all actually separated, in OFF position, the toggle or handle shall indicate the isolation position. | Yes |  |
| Isolation shall be provided by a double break on the main circuit. | Yes |  |
| MCCB shall be able to receive a device for locking in the “isolated” position, with up to 3 padlocks. | Yes |  |
| MCCBs shall be designed to prevent access to live parts when the cover is removed. | Yes |  |
| MCCBs shall be equipped with a “push to trip” button in front to test operation and the opening of the poles. | Yes |  |
| MCCB rating, “push to trip” button, performances and contact position indication must be clearly visible and accessible from the front, through the front panel or the door of the switchboard. | Yes |  |
| ACCESSORIES |  |  |
| Motor mechanism | Yes 110 V DC |  |
| An “auto/manual” switch in front shall, when set to the “manual” position, lock out electrical control; when set to “auto”, lock out the manual control; remote indication of “manual” or “auto” mode shall be possible. It shall also be possible to control the access to the “auto” control. | Yes |  |
| Closing shall take place in less than 80 ms. | Yes |  |
| The operating mechanism shall be of the stored-energy type only | Yes |  |
| The addition of a motor mechanism or a rotary handle shall in no way affect circuit breaker characteristics | Yes |  |
| Electronic Trip Module | Yes 110 V DC |  |
| Residual Current Module | Yes 110 V DC |  |
| Shunt Trip | Yes 110 V DC |  |
| Undervoltage Release | Yes 110 V DC |  |
| Auxiliary Contacts | Two NO and NC each One “TRIPPED” Position Carriage Inserted Changeover Contact Carriage Withdrawn Changeover Contact |  |
| Mechanical Operations Counter | Yes |  |
| Lockout key provision | Yes |  |
| PROTECTION UNIT FUNCTIONALITY |  |  |
| Electronic Protection Unit Protection: | Yes |  |
| Power for protection shall be from current transformers and shall operate at currents as low as 5% of the nominal rating | Yes |  |
| Overload Protection (L) adjustable for current and time | Yes |  |
| Thermal memory for overload protection | Yes |  |
| IDMT Short Circuit Protection (S)adjustable for time and current | Yes |  |
| Instantaneous Short Circuit Protection (I) adjustable in several thresholds | Yes |  |
| Ground Fault Protection Module adjustable for time and current up to 1000mA | Yes |  |
| Programming of protection unit | Keypad or RS232 or USB interface |  |
| Measurement: |  |  |
| Power for protection shall be from current transformers and shall operate at currents as low as 5% of the nominal rating | Yes |  |
| Parameters to be measured: |  |  |
| All three phase currents and neutral current | Yes |  |
| All three phase voltages and phase to neutral voltages | Yes |  |
| Indication of all measured parameters | Yes |  |
| Visual Indication |  |  |
| Trip indication of L, S and I breaker trips | Yes |  |
| Trip indication of RCD device | Yes |  |
| Communication: |  |  |
| Facility to communicate on Ethernet IP and Profibus | Yes |  |
| MULTI FUNCTION METER SPECIFICATION |  |  |
| CT input: 1A or 5A Primary current up to 1 250 A | Yes |  |
| VT input: 3 phase star connection 400/231 V | Yes |  |
| Control power: 110 V DC or 231 AC UPS | Yes |  |
| Instantaneous rms values: |  |  |
| Current per phase, neutral and ground | Yes |  |
| Voltage Total, per phase , phase to phase and phase to neutral | Yes |  |
| Frequency | Yes |  |
| Real, reactive, and apparent power total and per phase Signed, Four Quadrant | Yes |  |
| True Power Factor Total and per phase Signed, Four Quadrant | Yes |  |
| Displacement PF Total and per phase Signed, Four Quadrant | Yes |  |
| % Unbalanced I per phase and total, | Yes |  |
| % Unbalanced Voltage phase to neutral, phase to phase | Yes |  |
| Energy values: |  |  |
| Accumulated Active, Reactive and Apparent Energy Received/Delivered; Net and absolute | Yes |  |
|  | Yes |  |
| Demand values: | Yes |  |
| Current average Present, Last, Predicted, Peak, and Peak Date Time | Yes |  |
| Active power Present, Last, Predicted, Peak, and Peak Date Time | Yes |  |
| Reactive power Present, Last, Predicted, Peak, and Peak Date Time | Yes |  |
| Apparent power Present, Last, Predicted, Peak, and Peak Date Time | Yes |  |
| Peak demand with time stamping D/T for current and powers | Yes |  |
| Power quality measurements |  |  |
| Total Harmonic Distortion, Current per phase and Total, Voltage Total, phase to phase and phase to neutral | Yes |  |
| Individual harmonics (odds) up to the 15th Current per phase and Total, Voltage Total, phase to phase and phase to neutral | Yes |  |
| True rms sampling rate: 64 samples per cycle | Yes |  |
| EMC compatibility: IEC 61000 | Yes |  |
| Display: Minimum of four parameters at a time | Yes |  |
| Keypad: Navigate instantaneous and cumulative/minimum/maximum values | Yes |  |
| Alarm log with date and time stamping | Yes |  |
| Compliance: IEC 61557-12 Class 0,5 | Yes |  |
| MoDBus TCP/IP Interface | Yes |  |

        - In the event of a 400V supply failure, the normal section will not be live and the emergency section will be supplied from the emergency generator. Sump pumps, emergency lighting and the UPS shall be supplied from the emergency section as a minimum.

        - The PLC control panel shall supplied from the UPS section as a minimum. The PLC, instrumentation, telemetry, HMI, telemetry, Ethernet switch, etc will then be supplied from the PLC control panel.

        - Five spare circuits rated from 20 to 60 A three phase shall be supplied for each of the normal and emergency sections.

      - TURBINE AND GENERATOR AUXILIARIES PANEL

Function:  To supply power and local controls to pump set associated equipment.

        - Specific requirements:

| Description | RW Requirement |
| --- | --- |
| Panel supply voltage | 400VAC |
| Panel control voltage | 231VAC |
| Panel current rating | TBA A |
| Panel IP rating | IP65 |
| Panel material | Mild Steel |
| Panel painting system details. | Powdercoated B26,structured. As per the RW specifications. (min 70µm paint thickness) |
| Panel form classification | 3b |
| Panel short circuit rating (3 sec) kA | TBA |
| Panel location | Pump Pit Walk ways |
| Panel access | Front |
| Panel mounting location | Floor standing against the wall in the turbine chamber walkway |
| Cable entry location | Bottom |
| Certification required | Assembly assessors certification |
| Power supply fed from | 400V Distribution board |

        - There shall be a 400V Turbine Auxiliary Panel per turbine. The panel shall supply power and controls to turbine associated equipment such as:

          - Cooling water pump panels,

          - Lubrication oil pumps (where required),

          - Generator Space Heaters,

          - Isolation Valves associated with the turbine

          - PLC panel (if required)

          - One Spare Circuit

        - The incomer circuit shall consist of a suitably rated ammeter and moulded case circuit-breaker, with door interlocked handle, rated to the maximum demand of the panel.

        - All circuit breakers statuses shall be monitored by a potential free auxiliary contact of the applicable circuit breaker. All contacts shall be marshalled to a common terminal strip for connection by multicore cable to the PLC panel.

        - The 400V auxiliary supply shall be installed on the walkway directly in front of the corresponding turbine set. The contractor shall ensure that all the turbine auxiliary supplies have been included in the design of the panel.

      - CONTROL PANELS

        - General requirements:

| Description | Preferred |
| --- | --- |
| Panel supply voltage | 400VAC |
| Panel control voltage | 231VAC |
| Panel current rating | TBA A |
| Panel IP rating | IP65 |
| Panel material | 3CR12 |
| Panel painting system details. | Powdercoated B26,structured to SANS 1091 |
| Panel form classification | 1 |
| Panel short circuit rating (3 sec) kA | TBA |
| Panel location | At cooling water pump |
| Panel access | Front |
| Panel mounting location | Installed on a unistrut support complete with cable racking |
| Cable entry location | Bottom |
| Certification required | Assembly assessors certification |
| Power supply fed from | Pump Set Auxiliary Distribution Board |

        - The panels shall be installed as close as possible to the controlled load/equipment eg. Sump pumps, cooling water pumps…)

        - The panel shall be equipped, as a minimum, with a suitably rated circuit breaker, isolator, contactor, overload protection, pushbuttons, trunking, terminals, pad lockable door interlock handle, selector switch, square key door catches, LEDs and labels.

        - The stop pushbutton shall be red in color, of the lock with twist release type and shall be capable of being padlocked in the stopped position.

      - VALVE AND MOTOR ISOLATING PANELS

        - Specific requirements:

| Description | Preferred |
| --- | --- |
| Panel supply voltage | 400VAC |
| Panel control voltage | As per drawing |
| Panel current rating | TBA A |
| Panel IP rating | IP65 |
| Panel material | 3CR12 |
| Panel painting system details. | Powdercoated B26 to SANS 1091 |
| Panel form classification | 1 |
| Panel short circuit rating (3 sec) kA | TBA |
| Panel location | Pedestal or wall mounted at valve or motor with cable racking |
| Panel access | Front |
| Cable entry location | Bottom |
| Power supply fed from | Distribution Board |

        - Every motorised device (less than 35kW) or motorised valve shall have an isolating panel which allows for the local isolation of the motor or valve actuator.

        - The panels shall be equipped, as a minimum, with a suitably rated isolator, trunking, terminals, terminal numbers, wire numbers, pad lockable door interlock isolator handle, square key door catches, labels and support brackets.

        - If a 4-20mA signal is utilized to control the valve actuator then, in addition to the above, each VIP (Valve Isolating Panel) shall include additional terminals and two suitably rated surge arrestors.

        - The main isolator shall have a potential free auxiliary contact wired to terminals for indication or interlocking purposes.

      - FLOOD ALARM PANEL, SIREN AND LEVEL SWITCHES

        - Where there is a risk of flooding especially at the turbine hall suitably rated sump pumps shall be provided as determined by the mechanical engineer.

        - Specific requirements:

| Description | Preferred |
| --- | --- |
| Panel supply voltage | 24VDC |
| Panel control voltage | 24VDC |
| Panel current rating | TBA A |
| Panel IP rating | IP65 |
| Panel material | 3CR12 |
| Panel painting system details. | Powdercoated B26,structured to SANS 1091 |
| Panel form classification | 1 |
| Panel short circuit rating (3 sec) kA | TBA |
| Panel location | Indoors/Outdoors |
| Panel access | Front |
| Panel mounting location | Installed on a unistrut support complete with cable racking |
| Cable entry location | Bottom |
| Certification required | Assembly assessors certification |
| Power supply fed from | Control Room UPS or Common Services PLC |

        - The panel shall be equipped, as a minimum, with a suitably rated circuit breaker, isolator, contactor, overload protection, pushbuttons, trunking, terminals, pad lockable door interlock handle, selector switch, square key door catches, LEDs and labels.

        - An audible alarm, with a range of 1000m and rated for continuous operation, together with an orange flashing light shall be installed on top of each panel must be installed.

        - The contractor shall also include level switches for low and high level provided with suitably rated changeover contacts.

      - Standby diesel generator

The contractor shall design the emergency standby diesel generator to be rated as follows:

        - The final essential services load list of generator shall be verified and checked against the generator rating taking into account standing loads and switching loads from e g valve actuators

        - Black start load requirements for the turbines shall be taken into account

        - The generator shall operate at between 60 and 80% of its full load rating with design load connected. No spare capacity shall be allowed for as the remaining capacity will be considered spare.

        - If the design loading is significantly variable the requirement for any dummy loads shall be investigated and a designed for as, but this is not preferred.

        - The generator shall be designed for automatic changeover in the event of a power failure.

        - The generator shall be provided with a four pole changeover system.

        - The output of the generator shall be equipped with adjustable IDMT and instantaneous earth fault protection.

        - The emergency standby diesel generators shall be installed in the diesel generator rooms and shall supply power to the respective 400V distribution boards, essential services distribution section.

        - The generator unit shall have a Modbus TCP/IP communications port and software to allow for connection to a PLC and SCADA system. The generator unit status, alarms and metering values shall be communicated to the PLC via this communications link.

        - The contractor shall ensure that the power supplies to all essential equipment have been included, and that where possible starting loads such as those for valve actuators do not occur simultaneously.

        - A double skinned containment area for diesel and oil spillages shall be provided.

          - A level sensor for high levels in outer bund area shall be supplied.

          - Controlled drainage of spillage with a low level sump area suitable for a portable pump

          - Low level outlet with a drain plug to flush the bund area when required

        - Fuel management and Theft Prevention

          - Intelligent Monitoring of Fuel Intake and Consumption via Running Hours and alarming of discrepancies

          - Limit Switches on all enclosure doors and date and time stamped recording of opening and closing of doors

        - Generator Room Requirements

          - The generator orientation shall facilitate ease of removal of the set for maintenance and re-fuelling

          - Air flow arrangement to the engine shall be taken into account.

          - Exhaust ducting shall be taken overhead and out of the room with a proper design with compensation.

          - A minimum of 1000 mm shall be provided all around the generator for ease of access.

          - If a dummy load is required, this shall be placed taking into account safety and ease of heat dissipation from the room.

        - Specific requirements:

| NO | DESCRIPTION | REQUIREMENT |
| --- | --- | --- |
| 1 | GENERAL DATA |  |
|  | Continuous Rated Output Power At Sea Level (kW) |  |
|  | Continuous Rated Output Power At Sea Level (kVA) |  |
|  | Percentage De-Rating For Site Conditions, In Accordance With BS 551.4: - For Altitude - For Temperature - For Humidity - Total De-Rating |  |
|  | Continuous Rated Output Power At site (kW at 0.8 Power Factor) |  |
|  | Continuous Rated Output Power At site (kVA) | TBA kVA based on the loads to be supplied including sequential starting loads of valve actuators |
|  | Power Factor | 0.8 |
|  | Efficiency | Min. 90% @ 75% Load |
|  | AC Voltage | 380Vac/400Vac/230Vac |
|  | Frequency | 50 Hz |
|  | Number Of Phases | 3-Phase with Neutral |
|  | Connection Method | Star |
|  | Duty Type | Heavy Duty |
|  | Canopy Material (Indoor Installation) | 3CR12 and Powder Coated |
|  | Canopy Internal Material | Flameproof |
|  | Continuous Running Time @ Full Load | Min. 12 Hours |
|  | Insulating And Dielectric Materials | Fireproof, Non-Toxic And Environmental Friendly |
|  | Applicable Standards/Specification | European And South African |
|  | Type Of Technology | ATS & AMF |
|  | OTHERS |  |
| 2 | OPERATION MODE |  |
|  | Start/Shutdown Method | Auto Start (AMF&ATS) And Auto Shutdown |
|  | Operation Condition (Load Application) | Withstand Sudden Load Change And Maintain Stable Operation |
|  | Negative Phase Sequence Current | Up To 10% |
|  | Load Acceptance | As Soon As Reaching Rated Speed and Voltage |
|  | Effects Of Sudden Load Change | Insignificantly Small |
|  | Intervention Running At Less Than 60% Load |  |
|  | Overload Capability | 10% for 1 hour |
| 3 | NOISE LEVEL (DBA) SABS 0103 |  |
|  | Canopy (Indoor Installation) | Not Greater Than 65 DBA |
|  | Open Set (Indoor Installation) |  |
| 4 | ENGINE DATA (BS 5514 AND SANS 60034) |  |
|  | DC Voltage | 12Vdc/24Vdc |
|  | Exhaust System Material | 3CR12 Corrosion-Resistant Steel |
|  | Exhaust Cladding Material | Galvanized Mild Steel |
|  | Fuel Type | Diesel |
|  | Fuel Storage | Eight hours running at full connected load |
|  | Lubrication Oil Type | As per Engine Manufacturer Preference |
|  | AVR | Constant Voltage |
|  | Mounting | Heavy Duty Anti-Vibration |
|  | Type of base and Base Orientation |  |
|  | OTHERS | Engines to be supplied with replaceable elements for oil, fuel, air filter assemblies |
| 5 | ALTERNATOR DATA (BS 5000 Part 99 and BS 4999 Parts 20 and 32) |  |
|  | Manufacturer’s Name, Type Number (Model) and Year of Manufacturer |  |
|  | Terminal Voltage and Frequency | 380Vac/400Vac/230Vac @ 50Hz |
|  | Guaranteed Voltage Regulation From No-Load To Full-Load @ 0.8 PF | Within 1% of steady state in less than 300 ms |
|  | Transient Voltage Dip on Load Application | - 10% of rated voltage |
|  | Insulation Class | H |
|  | IP Protection | Minimum 22 |
| 6 | STARTING BATTERY (SANS 8528-4) |  |
|  | Manufacturer’s Name |  |
|  | Battery Type (Heavy Duty) | Lead-Acid Low Maintenance Type |
|  | Battery Voltage | 12Vdc/24Vdc |
|  | Battery Quantity | 1 |
|  | Battery Capacity (Ah) | 100 |
|  | Battery Starting Capacity | Six 10 Second Start Attempts |
|  | Boost Charge When The Battery Voltage Drops | Less Than 20% Of Battery Capacity |
|  | Battery Life Span | 5 years |
|  | OTHERS | Supply Battery Tray and Leads |
| 7 | CONTROL PANEL |  |
|  | Control Type/Technology | Microprocessor |
|  | Alarm and Fault Indication | Code and Description |
|  | Communication Protocol | Open Communication (Ethernet; Modbus; Profibus) |
|  | Ambient Temperature | 40°C |
|  | IP Protection | 55 |
|  | OTHERS |  |
| 8 | PROTECTION |  |
|  | Engine Oil Pressure | Remote Alarm & Shutdown |
|  | High Engine/Oil Temperature | Remote Alarm & Shutdown |
|  | High Water Temperature | Remote Alarm & Shutdown |
|  | Low Water Level | Remote Alarm & Shutdown |
|  | Battery Voltage | Remote Alarm |
|  | Under/Over Frequency Protection | Remote Alarm & Shutdown |
|  | Under/Over Voltage Protection | Remote Alarm & Shutdown |
|  | Overload Protection | Remote Alarm & Shutdown |
|  | Start Fault | Remote Alarm & Shutdown |
|  | Emergency Stop | Remote Alarm & Shutdown |
|  | Battery Charger Fault | Remote Alarm |
|  | Low Fuel Level (30%) | Remote Alarm |
|  | Loss Of Speed Signal | Remote Alarm & Shutdown |
|  | Under/Over Speed Protection | Remote Alarm & Shutdown |
|  | Electrical Phase Sequence | Remote Alarm & Shutdown |
|  | Earth Fault | Remote Alarm & Shutdown |
|  | Over-current | Remote Alarm & Shutdown |
|  | Auto Start Failure | Remote Alarm & Shutdown |
|  | Start Failure After 3 Attempts | Remote Alarm & Shutdown |
|  | Water Jacket Heater Failure | Remote Alarm & Shutdown |
| 9 | MONITORING |  |
|  | Generator Working Status and Alarms | Yes |
|  | Generic Sensors: - Smoke Detection - Humidity, etc. | Yes |

      - Uninterruptible Power Supply (UPS)

        - A UPS with a minimum rating of 10 kVA or 50% more than the connected total nominal load, whichever is the greater, at 231 V ac, shall be supplied.

        - The UPS system shall comply to Rand Water and national standards.

        - A UPS changeover circuit to supply raw mains to the connected load in the event of a total failure of the UPS shall be provided.

        - A UPS distribution board shall be provided with all individual circuits to each load and five additional spare circuits.

        - The colour of the UPS distribution board shall be F01 Royal Blue to SANS 1091.

      - Cabling

        - Cable selection, design and installation shall meet Rand Water and national standards.

      - Power Transmission

        - The power transmission to the Power Utility Sub-station shall conform to NRS, SANS standards and to all Eskom requirements.

      - Small Power and Lighting

        - The contractor shall design, supply and install a separate small power and lighting system, including emergency/escape lighting (the contractor shall as far as possible utilize approved LED type light fittings), distribution boards etc. for the entire installations per the supplied typical building layouts, relevant standards and Rand Water specifications.

        - Drawings shall be completed in the format and with the symbols as indicated in typical drawing RA 20941, including the distribution board arrangement of circuits.

        - The selection, design and installation shall meet the Rand Water and the National Standards.

        - Separate distribution boards shall be provided where required for Raw Power, Essential Services Power and UPS power painted as specified in this document complete and populated with all equipment.

        - The following powder coated colour finishes in accordance with SANS 1091 shall be applied on the relevant distribution boards:

          - “Raw” power – Orange B26

          - UPS power - Royal Blue F01

          - Emergency power – Signal Red A11

      - AREA LIGHTING

        - Area lighting shall be provided at each of the reservoir sites.

        - The contractor shall complete selection, design and installation shall meet the Rand Water and the National Standards

        - All area lighting masts shall be supplied from the Essential Services section of the 400 V Switchboard and provision shall be made for the required circuits in the switchboard.

        - The installation shall be so planned that maintenance can be carried out efficiently and safely on the installation.

      - SPARES

        - The contractors shall allow for spares of all major equipment and as detailed in the Rand Water Standard Specifications.

# Automation

      - Scope

The Automation Equipment shall control the Bronberg, Brakfontein Hartebeesthoek and Klipfontein   turbines according to the Electrical and Mechanical control philosophy. Each turbine shall be connected to dedicated PLC and HMI. There shall be a SCADA Application at the Central Depot, Benoni Depot, and Esselen Park Depot Control Room to monitor, control as well as produce reports on the Hydropower Plant Key Performance Indicators. The Bronberg Hydropower Plant shall be linked to Central Depot and Benoni Depot telemetry network for remote monitoring. The Brakfontein, Hartebeesthoek and Klipfontein Hydropower Plants shall be linked to Central Depot and Esselen Park Depot telemetry network for remote monitoring. The Contractor shall use the standards below for the design and construction requirements pertaining to the automation infrastructure, including but not limited to:

- Instrumentation

- Programmable Logic Controllers (PLC’s)

- PLC panels and Field Junction Boxes

- Human Machine Interface (HMI)

- Supervisory Control and Data Acquisition (SCADA)

- Profibus/Modbus Network

- Fibre Optic Network

- Ethernet

- Telemetry

- Telecommunication

- Reporting.

      - Design criteria

The following specifications form part of the Tender Document.

| Fibre Optic Standard Specification | SAM AAM 00001 Spec rev02 |
| --- | --- |
| Automation Asset Management Std Spec | SAM AAM 00003 Spec rev02 |
| Automation Panels Standard Specification | SAM AAM 00004 Spec |
| Temperature Measurement Sheet | SAM AAM 00006F |
| Temperature Measurement Std Spec | SAM AAM 00006 Spec |
| Pressure Measurement Sheet | SAM AAM 00017 F |
| Pressure Measurement Standard Specification | SAM AAM 00017 Spec |
| Industrial Ethernet | RW AAM 07000 Rev B |
| SCADA Standard Specification | RW AAM 06000 Rev A |
| Ultrasonic Clampon Flowmeter | RW AAM 02008 Rev B |
| Magnetic Flow Meter | RW AAM 02006 Rev B |
| Tagnaming Convention | RW AAM 00002 Rev C |

      - Bronberg Hydropower Plant

      - Design package

- The design drawings shall be generated according to RW_EES_002.

- The design pack shall be according to SAM AAM 00003 SPEC.

- The Profibus design shall be done by a Certified Profibus Engineer.

- The designs shall be approved by Pr.Eng/Pr.Tech Eng.

- The design pack shall consist of the following drawings:

- Network layout drawing

- PLC rack module wiring drawings

- Termination schedules

- Loop drawings

- Hookup drawings

- Panel General Arrangement Drawings

- Equipment schedules

- Cable schedules

- The Profibus network shall be able to handle minimum 1.5Mb/s baud rate.

- The following is applicable to Profibus design:

| SPECIFICATION | REQUIREMENT |
| --- | --- |
| Baud rate | 12Mb/s – 93.75kb/s; default 1.5Mb/s |
| Maximum segment length | 100m-1000m, default 200m |
| Maximum nodes per segment | 32 |
| Addressing structure | 0,1,2,3,126,127 are reserved for use by slave devies |
| Slave devices per segment | 29; preferred 10% spare capacity per segment |
| Number of segments in series | Maximum 8 segments in series, 9th segment shall be reserved as spare capacity |
| Spurs | No spurs allowed on Profibus DP |
| Termination | Active termination on segment with more than 3 devices. |

      - Instrumentation

- The Contractor shall put into operation the applicable instrumentation to fulfil the functional requirements of the system.

- The supply and installation shall be in accordance with applicable Instrumentation Standard Specifications and manufacture specifications.

      - PLC

- The Contractor shall put into operation PLC system with all modules and ancillary items for each turbine and one Common Services PLC system.

- The PLC shall monitor, control and communicate with applicable instrumentation, actuators, valves, motors, Ethernet switches, UPS, telemetry and any other equipment as required.

- The Functional Design Specification (FDS) shall be developed.

- The PLC software application shall be developed by a Certified System Integrator.

      - PLC Panels

- Each turbine shall have a dedicated PLC panel.

- One PLC panel shall be for the Common Services PLC.

- Each PLC panel shall be manufactures using 3CR12 stainless steel sheet metals or better.

- The thickness of the sheet metal shall be not less than 2mm.

- Each panel shall have heat extraction fan and filtered air inlet

- Each PLC panel shall be IP65 rated.

- Each PLC panel shall be Cornflower blue painted.

- Each PLC panel shall have 70µm paint thickness.

- Each PLC panel shall have a galvanized gland plate.

- Each PLC panel shall have smooth white chassis plate.

- Each PLC panel shall come with miniature circuit breakers.

- The PLC panel shall be manufactured according to RW 00320 AS 491.

- The PLC panel shall have LED type fuse terminals.

- Each PLC panel shall have a hard-wired mushroom emergency stop button.

- Each PLC panel shall have Red, Amber, Green and White stacker light and Siren combined.

- Each PLC panel shall have a fluorescent light with door limit switches.

      - Human Machine Interface (HMI)

- The Contractor shall put into operation one HMI for each hydropower turbine.

- The Contractor shall put into operation a panel to house each HMI.

- The Contractor shall develop an application for each HMI to monitor all respective system/site information including but not limited to equipment statuses and alarms and also to enable the operator to change operational modes.

- The HMI software shall be developed by a Certified System Integrator.

      - SCADA

- The Contractor shall develop, configure and supply SCADAs at Central Depot and Benoni Depot Control Room to provide an interface and communicate the full plant status including alarms.

- The Contractor shall ensure that information including but not limited to equipment statuses are also configured in the Historian data bases at Central Depot for historical data capture purposes.

- The Contractor shall put into operation at least two reports for each system/site (details to be defines later).

- The SCADA application shall be developed by a Certified System Integrator.

      - Communication network

- The Contractor shall put into operation a full communication network to communicate between instruments, actuators, PLC, HMI and Ethernet switches.

- The supply and installation shall be in accordance with applicable Standard Specifications which may be Profibus or Ethernet.

      - Fibre optic cabling

- The Contractor shall put into operation a fibre optic network.

- The supply and installation shall be in accordance with the Fiber Optic Standard Specification.

      - Ethernet switch

- The Contractor shall put into operation Ethernet switches at each turbine.

- The Ethernet design shall allow for full redundancy topology.

- The Ethernet design shall have minimum bandwidth of 1Gbps to cater for cctv video footage traffic.

- The Contractor shall put into operation the Ethernet network and connect all Ethernet compatible devices onto the Employer’s network.

- The supply and installation shall be in accordance with the Ethernet Standard Specification.

      - Telemetry

- The Contractor shall put into operation telemetry system linking Bronberg Hydropwer Plant with Central Depot and Benoni Depot Control Room.

- The wireless modem linking each site to Rand Water Central Depot shall be hybrid type consisting of license free radio, 3G/4G Access Point Name (APN) or 3G/4G Virtual Private Network (VPN) depending on results of each site survey conditions.

- APN telemetry shall utilize Rand Water issued APN.

- The wireless GPRS/GSM modem shall support Modbus TCP/IP communication protocol.

- The wireless GPRS/GSM modem shall have embedded data-logging functionality with expandable memory via SD card.

      - Brakfontein Hydropower Plant

      - Design package

- The design drawings shall be generated according to RW_EES_002.

- The design pack shall be according to SAM AAM 00003 SPEC.

- The Profibus design shall be done by a Certified Profibus Engineer.

- The designs shall be approved by Pr.Eng/Pr.Tech Eng.

- The design pack shall consist of the following drawings:

- Network layout drawing

- PLC rack module wiring drawings

- Termination schedules

- Loop drawings

- Hookup drawings

- Panel General Arrangement Drawings

- Equipment schedules

- Cable schedules

- The Profibus network shall be able to handle minimum 1.5Mb/s baud rate.

- The following is applicable to Profibus design:

| SPECIFICATION | REQUIREMENT |
| --- | --- |
| Baud rate | 12Mb/s – 93.75kb/s; default 1.5Mb/s |
| Maximum segment length | 100m-1000m, default 200m |
| Maximum nodes per segment | 32 |
| Addressing structure | 0,1,2,3,126,127 are reserved for use by slave devies |
| Slave devices per segment | 29; preferred 10% spare capacity per segment |
| Number of segments in series | Maximum 8 segments in series, 9th segment shall be reserved as spare capacity |
| Spurs | No spurs allowed on Profibus DP |
| Termination | Active termination on segment with more than 3 devices. |

      - Instrumentation

- The Contractor shall put into operation the applicable instrumentation to fulfil the functional requirements of the system.

- The supply and installation shall be in accordance with applicable Instrumentation Standard Specifications and manufacture specifications.

      - PLC

- The Contractor shall put into operation PLC system with all modules and ancillary items for each turbine and one Common Services PLC system.

- The PLC shall monitor, control and communicate with applicable instrumentation, actuators, valves, motors, Ethernet switches, UPS, telemetry and any other equipment as required.

- The Functional Design Specification (FDS) shall be developed.

- The PLC software application shall be developed by a Certified System Integrator.

      - PLC Panels

- Each turbine shall have a dedicated PLC panel.

- One PLC panel shall be for the Common Services PLC.

- Each PLC panel shall be manufactures using 3CR12 stainless steel sheet metals or better.

- The thickness of the sheet metal shall be not less than 2mm.

- Each panel shall have heat extraction fan and filtered air inlet

- Each PLC panel shall be IP65 rated.

- Each PLC panel shall be Cornflower blue painted.

- Each PLC panel shall have 70µm paint thickness.

- Each PLC panel shall have a galvanized gland plate.

- Each PLC panel shall have smooth white chassis plate.

- Each PLC panel shall come with miniature circuit breakers.

- The PLC panel shall be manufactured according to RW 00320 AS 491.

- The PLC panel shall have LED type fuse terminals.

- Each PLC panel shall have a hard-wired mushroom emergency stop button.

- Each PLC panel shall have Red, Amber, Green and White stacker light and Siren combined.

- Each PLC panel shall have a fluorescent light with door limit switches.

      - Human Machine Interface (HMI)

- The Contractor shall put into operation one HMI for each hydropower turbine.

- The Contractor shall put into operation a panel to house each HMI.

- The Contractor shall develop an application for each HMI to monitor all respective system/site information including but not limited to equipment statuses and alarms and also to enable the operator to change operational modes.

- The HMI software shall be developed by a Certified System Integrator.

      - SCADA

- The Contractor shall develop, configure and supply SCADAs at Central Depot and Esselen Park Depot to provide an interface and communicate the full plant status including alarms.

- The Contractor shall ensure that information including but not limited to equipment statuses are also configured in the Historian data bases at Central Depot for historical data capture purposes.

- The Contractor shall put into operation at least two reports for each system/site (details to be defines later).

- The SCADA application shall be developed by a Certified System Integrator.

      - Communication network

- The Contractor shall put into operation a full communication network to communicate between instruments, actuators, PLC, HMI and Ethernet switches.

- The supply and installation shall be in accordance with applicable Standard Specifications which may be Profibus or Ethernet.

      - Fibre optic cabling

- The Contractor shall put into operation a fibre optic network.

- The supply and installation shall be in accordance with the Fiber Optic Standard Specification.

      - Ethernet switch

- The Contractor shall put into operation Ethernet switches at each turbine.

- The Ethernet design shall allow for full redundancy topology.

- The Ethernet design shall have minimum bandwidth of 1Gbps to cater for cctv video footage traffic.

- The Contractor shall put into operation the Ethernet network and connect all Ethernet compatible devices onto the Employer’s network.

- The supply and installation shall be in accordance with the Ethernet Standard Specification.

      - Telemetry

- The Contractor shall put into operation telemetry system linking Brakfontein Hydropwer Plant with Central Depot and Benoni Depot Control Room.

- The wireless modem linking each site to Rand Water Central Depot shall be hybrid type consisting of license free radio, 3G/4G Access Point Name (APN) or 3G/4G Virtual Private Network (VPN) depending on results of each site survey conditions.

- APN telemetry shall utilize Rand Water issued APN.

- The wireless GPRS/GSM modem shall support Modbus TCP/IP communication protocol.

- The wireless GPRS/GSM modem shall have embedded data-logging functionality with expandable memory via SD card.

      - Hartebeesthoek Hydropower Plant

      - Design package

- The design drawings shall be generated according to RW_EES_002.

- The design pack shall be according to SAM AAM 00003 SPEC.

- The Profibus design shall be done by a Certified Profibus Engineer.

- The designs shall be approved by Pr.Eng/Pr.Tech Eng.

- The design pack shall consist of the following drawings:

- Network layout drawing

- PLC rack module wiring drawings

- Termination schedules

- Loop drawings

- Hookup drawings

- Panel General Arrangement Drawings

- Equipment schedules

- Cable schedules

- The Profibus network shall be able to handle minimum 1.5Mb/s baud rate.

- The following is applicable to Profibus design:

| SPECIFICATION | REQUIREMENT |
| --- | --- |
| Baud rate | 12Mb/s – 93.75kb/s; default 1.5Mb/s |
| Maximum segment length | 100m-1000m, default 200m |
| Maximum nodes per segment | 32 |
| Addressing structure | 0,1,2,3,126,127 are reserved for use by slave devies |
| Slave devices per segment | 29; preferred 10% spare capacity per segment |
| Number of segments in series | Maximum 8 segments in series, 9th segment shall be reserved as spare capacity |
| Spurs | No spurs allowed on Profibus DP |
| Termination | Active termination on segment with more than 3 devices. |

      - Instrumentation

- The Contractor shall put into operation the applicable instrumentation to fulfil the functional requirements of the system.

- The supply and installation shall be in accordance with applicable Instrumentation Standard Specifications and manufacture specifications.

      - PLC

- The Contractor shall put into operation PLC system with all modules and ancillary items for each turbine and one Common Services PLC system.

- The PLC shall monitor, control and communicate with applicable instrumentation, actuators, valves, motors, Ethernet switches, UPS, telemetry and any other equipment as required.

- The Functional Design Specification (FDS) shall be developed.

- The PLC software application shall be developed by a Certified System Integrator.

      - PLC Panels

- Each turbine shall have a dedicated PLC panel.

- One PLC panel shall be for the Common Services PLC.

- Each PLC panel shall be manufactures using 3CR12 stainless steel sheet metals or better.

- The thickness of the sheet metal shall be not less than 2mm.

- Each panel shall have heat extraction fan and filtered air inlet

- Each PLC panel shall be IP65 rated.

- Each PLC panel shall be Cornflower blue painted.

- Each PLC panel shall have 70µm paint thickness.

- Each PLC panel shall have a galvanized gland plate.

- Each PLC panel shall have smooth white chassis plate.

- Each PLC panel shall come with miniature circuit breakers.

- The PLC panel shall be manufactured according to RW 00320 AS 491.

- The PLC panel shall have LED type fuse terminals.

- Each PLC panel shall have a hard-wired mushroom emergency stop button.

- Each PLC panel shall have Red, Amber, Green and White stacker light and Siren combined.

- Each PLC panel shall have a fluorescent light with door limit switches.

      - Human Machine Interface (HMI)

- The Contractor shall put into operation one HMI for each hydropower turbine.

- The Contractor shall put into operation a panel to house each HMI.

- The Contractor shall develop an application for each HMI to monitor all respective system/site information including but not limited to equipment statuses and alarms and also to enable the operator to change operational modes.

- The HMI software shall be developed by a Certified System Integrator.

      - SCADA

- The Contractor shall develop, configure and supply SCADAs at Central Depot and Esselen Park Control Room to provide an interface and communicate the full plant status including alarms.

- The Contractor shall ensure that information including but not limited to equipment statuses are also configured in the Historian data bases at Central Depot for historical data capture purposes.

- The Contractor shall put into operation at least two reports for each system/site (details to be defines later).

- The SCADA application shall be developed by a Certified System Integrator.

      - Communication network

- The Contractor shall put into operation a full communication network to communicate between instruments, actuators, PLC, HMI and Ethernet switches.

- The supply and installation shall be in accordance with applicable Standard Specifications which may be Profibus or Ethernet.

      - Fibre optic cabling

- The Contractor shall put into operation a fibre optic network.

- The supply and installation shall be in accordance with the Fiber Optic Standard Specification.

      - Ethernet switch

- The Contractor shall put into operation Ethernet switches at each turbine.

- The Ethernet design shall allow for full redundancy topology.

- The Ethernet design shall have minimum bandwidth of 1Gbps to cater for cctv video footage traffic.

- The Contractor shall put into operation the Ethernet network and connect all Ethernet compatible devices onto the Employer’s network.

- The supply and installation shall be in accordance with the Ethernet Standard Specification.

      - Telecommunication

- The Contractor shall put into operation telemetry system linking Hartebeesthoek Hydropwer Plant with Central Depot and Benoni Depot Control Room.

- The wireless modem linking each site to Rand Water Central Depot shall be hybrid type consisting of license free radio, 3G/4G Access Point Name (APN) or 3G/4G Virtual Private Network (VPN) depending on results of each site survey conditions.

- APN telemetry shall utilize Rand Water issued APN.

- The wireless GPRS/GSM modem shall support Modbus TCP/IP communication protocol.

- The wireless GPRS/GSM modem shall have embedded data-logging functionality with expandable memory via SD card.

      - Klipfontein Hydropower Plant

      - Design package

- The design drawings shall be generated according to RW_EES_002.

- The design pack shall be according to SAM AAM 00003 SPEC.

- The Profibus design shall be done by a Certified Profibus Engineer.

- The designs shall be approved by Pr.Eng/Pr.Tech Eng.

- The design pack shall consist of the following drawings:

- Network layout drawing

- PLC rack module wiring drawings

- Termination schedules

- Loop drawings

- Hookup drawings

- Panel General Arrangement Drawings

- Equipment schedules

- Cable schedules

- The Profibus network shall be able to handle minimum 1.5Mb/s baud rate.

- The following is applicable to Profibus design:

| SPECIFICATION | REQUIREMENT |
| --- | --- |
| Baud rate | 12Mb/s – 93.75kb/s; default 1.5Mb/s |
| Maximum segment length | 100m-1000m, default 200m |
| Maximum nodes per segment | 32 |
| Addressing structure | 0,1,2,3,126,127 are reserved for use by slave devies |
| Slave devices per segment | 29; preferred 10% spare capacity per segment |
| Number of segments in series | Maximum 8 segments in series, 9th segment shall be reserved as spare capacity |
| Spurs | No spurs allowed on Profibus DP |
| Termination | Active termination on segment with more than 3 devices. |

      - Instrumentation

- The Contractor shall put into operation the applicable instrumentation to fulfil the functional requirements of the system.

- The supply and installation shall be in accordance with applicable Instrumentation Standard Specifications and manufacture specifications.

      - PLC

- The Contractor shall put into operation PLC system with all modules and ancillary items for each turbine and one Common Services PLC system.

- The PLC shall monitor, control and communicate with applicable instrumentation, actuators, valves, motors, Ethernet switches, UPS, telemetry and any other equipment as required.

- The Functional Design Specification (FDS) shall be developed.

- The PLC software application shall be developed by a Certified System Integrator.

      - PLC Panels

- Each turbine shall have a dedicated PLC panel.

- One PLC panel shall be for the Common Services PLC.

- Each PLC panel shall be manufactures using 3CR12 stainless steel sheet metals or better.

- The thickness of the sheet metal shall be not less than 2mm.

- Each panel shall have heat extraction fan and filtered air inlet

- Each PLC panel shall be IP65 rated.

- Each PLC panel shall be Cornflower blue painted.

- Each PLC panel shall have 70µm paint thickness.

- Each PLC panel shall have a galvanized gland plate.

- Each PLC panel shall have smooth white chassis plate.

- Each PLC panel shall come with miniature circuit breakers.

- The PLC panel shall be manufactured according to RW 00320 AS 491.

- The PLC panel shall have LED type fuse terminals.

- Each PLC panel shall have a hard-wired mushroom emergency stop button.

- Each PLC panel shall have Red, Amber, Green and White stacker light and Siren combined.

- Each PLC panel shall have a fluorescent light with door limit switches.

      - Human Machine Interface (HMI)

- The Contractor shall put into operation one HMI for each hydropower turbine.

- The Contractor shall put into operation a panel to house each HMI.

- The Contractor shall develop an application for each HMI to monitor all respective system/site information including but not limited to equipment statuses and alarms and also to enable the operator to change operational modes.

- The HMI software shall be developed by a Certified System Integrator.

      - SCADA

- The Contractor shall develop, configure and supply SCADAs at Central Depot and Esselen Park Depot Control Room Station to provide an interface and communicate the full plant status including alarms.

- The Contractor shall ensure that information including but not limited to equipment statuses are also configured in the Historian data bases at Central Depot for historical data capture purposes.

- The Contractor shall put into operation at least two reports for each system/site (details to be defines later).

- The SCADA application shall be developed by a Certified System Integrator.

      - Communication network

- The Contractor shall put into operation a full communication network to communicate between instruments, actuators, PLC, HMI and Ethernet switches.

- The supply and installation shall be in accordance with applicable Standard Specifications which may be Profibus or Ethernet.

      - Fibre optic cabling

- The Contractor shall put into operation a fibre optic network.

- The supply and installation shall be in accordance with the Fiber Optic Standard Specification.

      - Ethernet switch

- The Contractor shall put into operation Ethernet switches at each turbine.

- The Ethernet design shall allow for full redundancy topology.

- The Ethernet design shall have minimum bandwidth of 1Gbps to cater for cctv video footage traffic.

- The Contractor shall put into operation the Ethernet network and connect all Ethernet compatible devices onto the Employer’s network.

- The supply and installation shall be in accordance with the Ethernet Standard Specification.

      - Telemetry

- The Contractor shall put into operation telemetry system linking Klipfontein Hydropwer Plant with Central Depot and Benoni Depot Control Room.

- The wireless modem linking each site to Rand Water Central Depot shall be hybrid type consisting of license free radio, 3G/4G Access Point Name (APN) or 3G/4G Virtual Private Network (VPN) depending on results of each site survey conditions.

- APN telemetry shall utilize Rand Water issued APN.

- The wireless GPRS/GSM modem shall support Modbus TCP/IP communication protocol.

- The wireless GPRS/GSM modem shall have embedded data-logging functionality with expandable memory via SD card.

# Logistical sub-systems

      - Scope

This Schedule sets out the design and construction requirements for logistical sub-systems including but not limited to.

- Maintenance Personnel

- Operating Personnel

- Spares

- Tools

      - Operating personnel

Operating personnel shall be supplied by the contractor for two years and thereafter by Rand Water in the event of the BOOT option not being implemented.

      - Maintenance personnel

Maintenance personnel shall be supplied by the contractor for two years and thereafter by Rand Water in the event of the BOOT option not being implemented.

      - Tools

The Tenderer shall detail in the applicable Schedule the special tools required for the maintenance and overhaul of all the equipment to be supplied.

- Tools ordered shall be packed and transported in cases separate from the rest of the equipment and the provisions for spare parts and delivery instructions contained therein shall apply to the tools.

- All slings, shackles, spreads bars, cradles and other equipment necessary for the lifting of components for installation or maintenance shall be provided by the contractor and handed over to the Engineer on completion of the contract.

- Any special tools, special spanners, special cleaning tools, gauges etc, required for the equipment as specified, which, in the opinion of the Engineer, may be necessary for dismantling and re-assembling a set, for checking clearances and for the general maintenance of a set shall be supplied under this contract.

All such appliances shall be handed over to the Engineer on completion of erection.

- The contractor shall supply a set of lifting tackle under this contract.

- The lifting tackle shall be such that the method of lifting each item of plant to be supplied under this contract is the safest practical method that will not damage the item and its finish. The method shall ensure that the load is taken in the designed manner, even if the various ropes are not exactly of the designed length. This requirement may call for positive load balancing devices or articulation.

Provision for attaching slings shall be provided on the pipes. Full details of all lifting tackle shall be forwarded to the Engineer for his approval within six weeks of the contract being awarded and shall include the calculation of loads and stresses by an Engineer qualified to do so. A factor of safety of six shall be used and the tackle shall be supplied with individual load test certificates where applicable.

- All lifting tackle required for this contract shall be delivered to site in advance of relevant items of plant, shall be used for erection of plant to be supplied under this contract and after completion of all work shall be handed to Rand Water in good condition.

- A description of the proposed lifting tackle shall be submitted in the applicable Schedule.

      - Spares

- The Tenderer shall complete the relevant Schedule giving the complete list of spares, which it considers, should be ordered. Rand Water reserves the right to order either the whole or any quantity of the spares offered. Any spares ordered shall be submitted to the Engineer's Representative for examination and checking for interchangeability.

- Spares shall be packed in separate cases from the rest of the equipment and shall not be used by the contractor without the written permission of the Engineer. The spares shall be delivered in liaison with the Engineer or his Representative, directly to the Station Manager for the relevant station and a delivery note bearing the Manager's signature shall be submitted with invoices claiming payment for the spares.

The payments for spares will not be made without the signed delivery note.

- Spares and tools shall be packed and transported in cases separate from the rest of the equipment, cases containing spares and tools shall be clearly and indelibly marked to show the plant for which the spares are supplied.

      - Sequencing of Construction, Supply and Installation of equipment

The works are proposed to be done in the following order;

        - Technical Studies, Services Detection, Regulatory Requirements Protection and or Relocation of existing services, Surge Studies.

        - Positioning of the Hydro Power and electrical sub-station buildings

        - Geotechnical investigations

        - All necessary regulatory requirements to complete the project.

        - Acquisition of Servitude for transmission line between reservoirs and substation.

        - Access road to Bronberg, Brakfontein, Klipfontein & Hartebeesthoek Reservoir sites, storm-water and parking bays

        - Hydropower, Electrical and Automation Buildings at Bronberg, Brakfontein, Klipfontein & Hartebeesthoek Reservoir sites

        - Supply and installation of Mechanical, Electrical and Automation equipment

        - Hot and Cold Commissioning of plant

        - Operation of plant

# VERIFICATION

  - Inspection at works

At any time during manufacture and refurbishment, the whole of the work shall be available for inspection at the manufacturer's, sub-contractor and/or other outside suppliers' works by the Engineer's Representative.

Full information regarding the progress and the necessary facilities to enable the various components to be properly tested and/or inspected shall be given to the Engineer's Representative. The contractor shall make available his expertise, tools and equipment to the Engineer or his Representative for examination of the work. Rand Water reserves the right to reject any item, which has not been presented for such test and/or inspection.

The equipment shall be operated and tested in the presence of the Engineer’s Representative to prove its compliance with the major component requirements.

All work that is to be manufactured or shipped from overseas shall, prior to shipment, be submitted to the Engineer or the Engineer's Representative for final examination on the premises of the contractor or the makers of the same, and shall not on any account be shipped before receiving the Engineer's or Engineer's Representative's approval in writing after such examination, and the contractor shall give at least six days' notice in writing of any of the work being ready for inspection.

Certificates of all tests on materials and components shall be forwarded to the Engineer immediately on completion of the tests.

  - Inspection during installation

The Engineer will inspect the work during the course of installation and every reasonable facility is to be afforded by the contractor for such inspection.

The equipment shall after its installation be operated and tested in the presence of the Engineer’s Representative to prove its compliance with the major component requirements.

The Engineer will notify the contractor in writing of any imperfect or unsound work or of any inferior material which has been supplied and the contractor shall within three working days, proceed to alter, reconstruct or remove such work or supply new material to the standard required by the specification.

  - Validity of inspection and tests

Any inspection, examination or test at makers' works, either of material or of performance, shall not exempt the contractor from any obligation under the contract. The liability of the contractor for defective material or workmanship which may be disclosed after the equipment has been put into service shall be rectified in accordance with the General Conditions of Contract, notwithstanding that the defective item may have been passed previously during manufacture.

  - Quality assurance

Contractor’s Quality Management System.

The contractor’s quality management system shall meet the requirements of ISO 9001

  - Data Requirements

    - Drawings and information

- The sizes of the final drawings to be supplied shall comply with the A series of drawing paper as specified in SANS 822 (3.6.1 A series).  Sizes of paper to be used are A0 to A5 only. Letter height sizes and line thicknesses on these drawings shall be not less than 3 mm respectively.

- Should the makers consider any of the drawings or information to be confidential, the documents shall be marked “CONFIDENTIAL” and they will be treated as such by Rand Water.

- Sufficient information shall be given on the drawings to enable replacement parts to be made locally, if necessary.

- All communication, pamphlets and technical literature shall be in English.

- Three sets of CDs or USB Flash Disc shall be supplied with the approved “CAD” drawings tabled and stored in a format that can be loaded, edited and printed from the windows version of AutoCad 2015 or later.

- All drawings shall utilize the WKS codification system for identification of plant elements.

    - Drawing and information to be supplied

- The following drawings and information shall be submitted.

- A detailed arrangement of the systems and each component.

- Proposed designation plates.

- Details of each component.

- All general, assembly and detail drawings necessary, in the opinion of the Engineer, for the proper maintenance of and/or to effect major repair on site to each component.

- Construction and mounting details of the components etc.

- The Contractor shall also supply, before completion of the contract, any copies of the drawings that the Engineer may require as final drawings, together with data sheet records which shall also be incorporated into the Operating and Maintenance Manuals.

- The Contractor shall supply a complete set of final drawings covering all the equipment supplied and shall submit a list of the final drawings and information that it is proposed to supply. The design pack shall include all the drawings listed above.

- The Contractor shall supply a set of manufacturing drawings to Rand Water for its use in the case of:

- The Contractor going out of business.

- The design supplied being superseded.

- The Contractor not being in a position to supply the equipment concerned.

    - Operating and Maintenance Manuals

Supply three copies of Operating and Maintenance manuals, the manuals shall cover the following aspects in detail, with photographs, isometric assembly drawings, illustrations and drawings. The contents of the manual shall be as follows:

VOLUME 1: OPERATING & MAINTENANCE MANUAL

|  | Description |
| --- | --- |
| PART 1: OPERATIONS |  |
| - GENERAL DESCRIPTION |  |
| - Introduction | A high level introduction of the plant |
| - System Overview | Describe in detail the process with illustrations |
| - Design Parameters and Philosophy | Describe the philosophy of design (incl. properties of the chemical, Flow rates, dosages, number of storage tanks) |
| - CONTROL PHILOSOPHY |  |
| - Description | Description of the control philosophy and algorithms. Discuss the main elements of the control system, purpose and objective of the control, operating regimes, modes of operation (auto, manual, etc.). |
| - PLC configuration | Overview, Programming the PLC, Configuration of PTQ cards, FFBD Configuration (alarms and control). |
| - HMI hardware and software configuration | Homepage, trending |
| - SCADA configuration | Description and configuration of comlink between PLC, HMI and SCADA |
| - Function block diagrams | Drawings of FFB |
| - Alarms, events, trends and interlocks | List of common alarms, list of interlocks. |
| - OPERATING INSTRUCTIONS |  |
| - Performance Specification | List the set points and tuning constants used for all equipment. |
| - Pre Commissioning and commissioning procedure | Procedure for commissioning and performance testing, actual |
| - Pre – Operation checklist and Utility start- up |  |
| - Start-up procedure | Procedures for start-up |
| - Normal operating procedures | Procedures for normal operation |
| - Shutdown procedures | Procedures for shut-down |
| - Disposal Instructions for consumable items | Instructions for disposal of consumable items |
| - Special procedures for abnormal conditions | Description of systematic shutdown under abnormal conditions. |
| - Appendices – Summary of Control Functional Specification | Cause and effect matrix |
| - OPERATION PROCEDURE FROM HMI AND SCADA |  |
| - Operation procedure from the HMI | Description of operation from HMI to the detail of training, with screenshots. |
| - Operation procedure from SCADA | Description of operation from SCADA to the detail of training, with screenshots. |
| - HEALTH, SAFETY & EMERGENCY PROCEDURE AND PRECAUTIONS |  |
| - General |  |
| - Start-up inspections | Critical inspections (visual and otherwise) required prior to start-up and for safe operation, to ensure process operators and maintenance staff safety. |
| - Precautions while working/testing power supplies |  |
| - Emergency Procedures |  |
| - TRAINING MANUAL |  |
| PART 2: MAINTENANCE | Description of the function of the equipment, cleaning thereof, calibration requirements, troubleshooting, element replacement, flow curves, calculations, testing, etc. including pictures. This section must also include periodic maintenance. |
| - PROCESS EQUIPMENT | Process valves, process piping, tanks, vessels, dosing pumps, chlorinators, Evaporators, Vacuum Regulators Catch Pots, Injectors, Drum Frames, Electric/Manual Hoists, pressure relief devices, etc. |
| - AUTOMATION EQUIPMENT | Instrumentation (e.g. pH meters, pressure transmitters, level transmitters, flow meters), PLC, Network, HMI, SCADA, Control panel, etc. |
| - MECHANICAL EQUIPMENT | Cranes, pumpsets, valves, pipework, gravity thickeners, Access steelwork, sand grab, etc. |
| - ELECTRICAL EQUIPMENT | Distribution Lines, switchgear, cabling, transformers, distribution boards, generators, lighting, motors UPS |
| - BUILDING | Exterior, Interior, plumbing, structures, etc. |
| - CIVIL STRUCTURES | Floors, walls, columns, structural steel, etc. |

VOLUME 2: DRAWINGS AND DOCUMENTATION

|  | Description |
| --- | --- |
| - LIST OF DRAWINGS | These should all the final drawings specified in the tender document, as well as any additional drawing required by the engineer as specified in the technical system specification. |
| - LIST OF EQUIPMENT/EQUIPMENT SCHEDULE | List of all equipment with supplier contact details |
| - CABLE SCHEDULES | Schedule of cables |
| - LIST OF INSTRUMENTS/INSTRUMENT SCHEDULE | List of all instruments with supplier contact details |
| - SPARE PARTS LISTS FOR INSTRUMENTTION AND EQUIPMENT |  |
| - PERFORMANCE TESTING DOCUMENTATION (Actual) | The actual document that was used to check performance testing (not a blank template). Also include proof that the problems found were fixed. |
| - COMMISSIONING DOCUMENTATION (Actual) | The actual document that was used to commission the plant (not a blank template). Also include proof that the problems found were fixed. |
| - CALIBRATION, TEST CERTIFICATES, FIBRE CABLE OTDR, ELECTRICAL COC | All certificates for tests and calibrations done on instruments, equipment including fibre cables. |

VOLUME 3: MANUALS

|  | Description |
| --- | --- |
| - OEMs: MANUALS / USERGUIDES/ OPERATING & MAINTENANCE INSTRUCTIONS OF INSTRUMENTATION AND EQUIPMENT | These should be actual manuals which include fault diagnosis and troubleshooting guides. |

GENERAL

- This is a minimum requirement for all O&Ms. Documentation or drawings not listed here but required for different plants, as stated in their individual system specifications and tender documents, must be included in the O&M.

- Each manual must have an electronic version of the manual on a cd/USB flash disk inserted into each manual. The flash disk must also contain the baseline versions at Handover of the PLC programme, Protalk configuration with GSD files (for Profibus), HMI programme and SCADA programme.

- Each page should be inserted into a plastic pocket so that the papers can be kept intact for long periods of time.

- If part of the plant is upgraded, then the contractor shall integrate existing and new manuals.

# PREPARATION FOR DELIVERY

Delivery, packing and marking:

The equipment shall be delivered to the site specified in the applicable tender documents. No railage facilities exist at the site and delivery can be made by road transport only.

The contractor shall make his own arrangements for the acceptance of delivery, offloading and safe storage of material supplied and shall be responsible for the safe arrival of the whole of the plant on site.

All materials supplied shall be securely packed and adequately protected against damage in transit due to rough handling, weather etc.

All delicate items of plant shall be separately and specially packed and marked (in addition to other markings) "FRAGILE".

All cases, packages etc, shall be clearly and indelibly marked with the following: "CONTRACTOR'S NAME"

"RAND WATER"

"THE RELEVANT CONTRACT, SPECIFICATION, ENQUIRY NUMBER" "MASS ..........kg"

"SPARES" (if the case or package contains spares) and the mass shall be stated in the space provided.